## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1030-11_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1030-11_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1030-11_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1030-11_0_4_node_60 | 0.4 | n |  | TRUE
4 | bus_LV_1030-11_0_4_node_61 | 0.4 | n |  | TRUE
5 | bus_LV_1030-11_0_4_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1030-11_0_4_node_54 | 0.4 | n |  | TRUE
7 | bus_LV_1030-11_0_4_node_47 | 0.4 | n |  | TRUE
8 | bus_LV_1030-11_0_4_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_1030-11_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1030-11_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1030-11_0_4_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1030-11_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1030-11_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1030-11_0_4_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_1030-11_0_4_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_1030-11_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1030-11_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1030-11_0_4_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_1030-11_0_4_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1030-11_0_4_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1030-11_0_4_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_1030-11_0_4_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_1030-11_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_1030-11_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_1030-11_0_4_node_59 | 0.4 | n |  | TRUE
26 | bus_LV_1030-11_0_4_node_56 | 0.4 | n |  | TRUE
27 | bus_LV_1030-11_0_4_node_64 | 0.4 | n |  | TRUE
28 | bus_LV_1030-11_0_4_node_69 | 0.4 | n |  | TRUE
29 | bus_LV_1030-11_0_4_node_58 | 0.4 | n |  | TRUE
30 | bus_LV_1030-11_0_4_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_1030-11_0_4_node_55 | 0.4 | n |  | TRUE
32 | bus_LV_1030-11_0_4_node_62 | 0.4 | n |  | TRUE
33 | bus_LV_1030-11_0_4_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_1030-11_0_4_node_17 | 0.4 | n |  | TRUE
35 | bus_LV_1030-11_0_4_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_1030-11_0_4_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_1030-11_0_4_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_1030-11_0_4_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_1030-11_0_4_node_57 | 0.4 | n |  | TRUE
40 | bus_LV_1030-11_0_4_node_39 | 0.4 | n |  | TRUE
41 | bus_LV_1030-11_0_4_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_1030-11_0_4_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_1030-11_0_4_node_42 | 0.4 | n |  | TRUE
44 | bus_LV_1030-11_0_4_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_1030-11_0_4_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_1030-11_0_4_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_1030-11_0_4_node_28 | 0.4 | n |  | TRUE
48 | bus_LV_1030-11_0_4_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_1030-11_0_4_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_1030-11_0_4_node_67 | 0.4 | n |  | TRUE
51 | bus_LV_1030-11_0_4_node_49 | 0.4 | n |  | TRUE
52 | bus_LV_1030-11_0_4_node_50 | 0.4 | n |  | TRUE
53 | bus_LV_1030-11_0_4_node_51 | 0.4 | n |  | TRUE
54 | bus_LV_1030-11_0_4_node_52 | 0.4 | n |  | TRUE
55 | bus_LV_1030-11_0_4_node_53 | 0.4 | n |  | TRUE
56 | bus_LV_1030-11_0_4_node_71 | 0.4 | n |  | TRUE
57 | bus_LV_1030-11_0_4_node_65 | 0.4 | n |  | TRUE
58 | bus_LV_1030-11_0_4_node_66 | 0.4 | n |  | TRUE
59 | bus_LV_1030-11_0_4_node_68 | 0.4 | n |  | TRUE
60 | bus_LV_1030-11_0_4_node_31 | 0.4 | n |  | TRUE
61 | bus_LV_1030-11_0_4_node_32 | 0.4 | n |  | TRUE
62 | bus_LV_1030-11_0_4_node_33 | 0.4 | n |  | TRUE
63 | bus_LV_1030-11_0_4_node_35 | 0.4 | n |  | TRUE
64 | bus_LV_1030-11_0_4_node_40 | 0.4 | n |  | TRUE
65 | bus_LV_1030-11_0_4_node_38 | 0.4 | n |  | TRUE
66 | bus_LV_1030-11_0_4_node_44 | 0.4 | n |  | TRUE
67 | bus_LV_1030-11_0_4_node_45 | 0.4 | n |  | TRUE
68 | bus_LV_1030-11_0_4_node_46 | 0.4 | n |  | TRUE
69 | bus_LV_1030-11_0_4_node_48 | 0.4 | n |  | TRUE
70 | bus_LV_1030-11_0_4_node_145 | 0.4 | n |  | TRUE
71 | bus_LV_1030-11_0_4_node_72 | 0.4 | n |  | TRUE
72 | bus_LV_1030-11_0_4_node_73 | 0.4 | n |  | TRUE
73 | bus_LV_1030-11_0_4_node_74 | 0.4 | n |  | TRUE
74 | bus_LV_1030-11_0_4_node_143 | 0.4 | n |  | TRUE
75 | bus_LV_1030-11_0_4_node_144 | 0.4 | n |  | TRUE
76 | bus_LV_1030-11_0_4_node_76 | 0.4 | n |  | TRUE
77 | bus_LV_1030-11_0_4_node_75 | 0.4 | n |  | TRUE
78 | bus_LV_1030-11_0_4_node_125 | 0.4 | n |  | TRUE
79 | bus_LV_1030-11_0_4_node_146 | 0.4 | n |  | TRUE
80 | bus_LV_1030-11_0_4_node_110 | 0.4 | n |  | TRUE
81 | bus_LV_1030-11_0_4_node_70 | 0.4 | n |  | TRUE
82 | bus_LV_1030-11_0_4_node_80 | 0.4 | n |  | TRUE
83 | bus_LV_1030-11_0_4_node_81 | 0.4 | n |  | TRUE
84 | bus_LV_1030-11_0_4_node_63 | 0.4 | n |  | TRUE
85 | bus_LV_1030-11_0_4_node_108 | 0.4 | n |  | TRUE
86 | bus_LV_1030-11_0_4_node_78 | 0.4 | n |  | TRUE
87 | bus_LV_1030-11_0_4_node_77 | 0.4 | n |  | TRUE
88 | bus_LV_1030-11_0_4_node_79 | 0.4 | n |  | TRUE
89 | bus_LV_1030-11_0_4_node_132 | 0.4 | n |  | TRUE
90 | bus_LV_1030-11_0_4_node_139 | 0.4 | n |  | TRUE
91 | bus_LV_1030-11_0_4_node_82 | 0.4 | n |  | TRUE
92 | bus_LV_1030-11_0_4_node_83 | 0.4 | n |  | TRUE
93 | bus_LV_1030-11_0_4_node_84 | 0.4 | n |  | TRUE
94 | bus_LV_1030-11_0_4_node_85 | 0.4 | n |  | TRUE
95 | bus_LV_1030-11_0_4_node_86 | 0.4 | n |  | TRUE
96 | bus_LV_1030-11_0_4_node_134 | 0.4 | n |  | TRUE
97 | bus_LV_1030-11_0_4_node_138 | 0.4 | n |  | TRUE
98 | bus_LV_1030-11_0_4_node_103 | 0.4 | n |  | TRUE
99 | bus_LV_1030-11_0_4_node_112 | 0.4 | n |  | TRUE
100 | bus_LV_1030-11_0_4_node_133 | 0.4 | n |  | TRUE
101 | bus_LV_1030-11_0_4_node_129 | 0.4 | n |  | TRUE
102 | bus_LV_1030-11_0_4_node_101 | 0.4 | n |  | TRUE
103 | bus_LV_1030-11_0_4_node_115 | 0.4 | n |  | TRUE
104 | bus_LV_1030-11_0_4_node_106 | 0.4 | n |  | TRUE
105 | bus_LV_1030-11_0_4_node_88 | 0.4 | n |  | TRUE
106 | bus_LV_1030-11_0_4_node_89 | 0.4 | n |  | TRUE
107 | bus_LV_1030-11_0_4_node_90 | 0.4 | n |  | TRUE
108 | bus_LV_1030-11_0_4_node_121 | 0.4 | n |  | TRUE
109 | bus_LV_1030-11_0_4_node_91 | 0.4 | n |  | TRUE
110 | bus_LV_1030-11_0_4_node_92 | 0.4 | n |  | TRUE
111 | bus_LV_1030-11_0_4_node_93 | 0.4 | n |  | TRUE
112 | bus_LV_1030-11_0_4_node_119 | 0.4 | n |  | TRUE
113 | bus_LV_1030-11_0_4_node_109 | 0.4 | n |  | TRUE
114 | bus_LV_1030-11_0_4_node_113 | 0.4 | n |  | TRUE
115 | bus_LV_1030-11_0_4_node_120 | 0.4 | n |  | TRUE
116 | bus_LV_1030-11_0_4_node_122 | 0.4 | n |  | TRUE
117 | bus_LV_1030-11_0_4_node_114 | 0.4 | n |  | TRUE
118 | bus_LV_1030-11_0_4_node_94 | 0.4 | n |  | TRUE
119 | bus_LV_1030-11_0_4_node_95 | 0.4 | n |  | TRUE
120 | bus_LV_1030-11_0_4_node_96 | 0.4 | n |  | TRUE
121 | bus_LV_1030-11_0_4_node_97 | 0.4 | n |  | TRUE
122 | bus_LV_1030-11_0_4_node_98 | 0.4 | n |  | TRUE
123 | bus_LV_1030-11_0_4_node_99 | 0.4 | n |  | TRUE
124 | bus_LV_1030-11_0_4_node_105 | 0.4 | n |  | TRUE
125 | bus_LV_1030-11_0_4_node_118 | 0.4 | n |  | TRUE
126 | bus_LV_1030-11_0_4_node_107 | 0.4 | n |  | TRUE
127 | bus_LV_1030-11_0_4_node_100 | 0.4 | n |  | TRUE
128 | bus_LV_1030-11_0_4_node_102 | 0.4 | n |  | TRUE
129 | bus_LV_1030-11_0_4_node_104 | 0.4 | n |  | TRUE
130 | bus_LV_1030-11_0_4_node_117 | 0.4 | n |  | TRUE
131 | bus_LV_1030-11_0_4_node_111 | 0.4 | n |  | TRUE
132 | bus_LV_1030-11_0_4_node_130 | 0.4 | n |  | TRUE
133 | bus_LV_1030-11_0_4_node_123 | 0.4 | n |  | TRUE
134 | bus_LV_1030-11_0_4_node_142 | 0.4 | n |  | TRUE
135 | bus_LV_1030-11_0_4_node_126 | 0.4 | n |  | TRUE
136 | bus_LV_1030-11_0_4_node_127 | 0.4 | n |  | TRUE
137 | bus_LV_1030-11_0_4_node_128 | 0.4 | n |  | TRUE
138 | bus_LV_1030-11_0_4_node_131 | 0.4 | n |  | TRUE
139 | bus_LV_1030-11_0_4_node_136 | 0.4 | n |  | TRUE
140 | bus_LV_1030-11_0_4_node_137 | 0.4 | n |  | TRUE
141 | bus_LV_1030-11_0_4_node_140 | 0.4 | n |  | TRUE
142 | bus_LV_1030-11_0_4_node_141 | 0.4 | n |  | TRUE
143 | bus_MV_470_1_node_34 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1030-11_0_4_load_0 | 0 | 0.00013891 | 3.4814e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1030-11_0_4_load_1 | 1 | 0.0019179 | 0.00048066 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1030-11_0_4_load_2 | 2 | 0.0007391 | 0.00018524 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1030-11_0_4_load_60 | 3 | 0.00013741 | 3.4438e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1030-11_0_4_load_61 | 4 | 0.00044123 | 0.00011058 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1030-11_0_4_load_3 | 5 | 0.0011453 | 0.00028703 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1030-11_0_4_load_54 | 6 | 0.00038023 | 9.5294e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1030-11_0_4_load_47 | 7 | 0.00028497 | 7.142e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1030-11_0_4_load_4 | 8 | 0.0012354 | 0.00030961 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1030-11_0_4_load_9 | 9 | 0.004096 | 0.0010266 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1030-11_0_4_load_7 | 10 | 0.0045589 | 0.0011426 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1030-11_0_4_load_5 | 11 | 0.0010358 | 0.0002596 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1030-11_0_4_load_6 | 12 | 0.0010752 | 0.00026946 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1030-11_0_4_load_8 | 13 | 0.0010364 | 0.00025975 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1030-11_0_4_load_24 | 14 | 0.00084476 | 0.00021172 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1030-11_0_4_load_23 | 15 | 0.00084975 | 0.00021297 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1030-11_0_4_load_10 | 16 | 0.0018307 | 0.00045882 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1030-11_0_4_load_30 | 21 | 0.0041788 | 0.0010473 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1030-11_0_4_load_13 | 23 | 0.0014328 | 0.00035909 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1030-11_0_4_load_59 | 25 | 0.0020602 | 0.00051634 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1030-11_0_4_load_56 | 26 | 0.00095375 | 0.00023903 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1030-11_0_4_load_64 | 27 | 0.0010138 | 0.00025409 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1030-11_0_4_load_69 | 28 | 0.00068096 | 0.00017067 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1030-11_0_4_load_34 | 30 | 0.0020486 | 0.00051342 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1030-11_0_4_load_55 | 31 | 0.0016055 | 0.00040238 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1030-11_0_4_load_62 | 32 | 0.00036025 | 9.0288e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1030-11_0_4_load_19 | 33 | 0.0073235 | 0.0018354 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1030-11_0_4_load_17 | 34 | 0.0088913 | 0.0022284 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1030-11_0_4_load_29 | 35 | 0.0044609 | 0.001118 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1030-11_0_4_load_21 | 37 | 0.0011731 | 0.00029401 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1030-11_0_4_load_22 | 38 | 0.00018118 | 4.5408e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1030-11_0_4_load_57 | 39 | 0.0012005 | 0.00030086 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1030-11_0_4_load_39 | 40 | 0.0048344 | 0.0012116 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1030-11_0_4_load_37 | 41 | 0.0028542 | 0.00071532 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1030-11_0_4_load_36 | 42 | 0.008743 | 0.0021912 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1030-11_0_4_load_25 | 44 | 0.0045783 | 0.0011474 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1030-11_0_4_load_26 | 45 | 0.0031753 | 0.00079581 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1030-11_0_4_load_27 | 46 | 0.0028283 | 0.00070884 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1030-11_0_4_load_28 | 47 | 0.0035268 | 0.0008839 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1030-11_0_4_load_43 | 48 | 0.003002 | 0.00075236 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1030-11_0_4_load_41 | 49 | 0.0025833 | 0.00064743 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1030-11_0_4_load_67 | 50 | 0.0037806 | 0.0009475 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1030-11_0_4_load_49 | 51 | 0.0019972 | 0.00050055 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1030-11_0_4_load_50 | 52 | 0.0038139 | 0.00095586 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1030-11_0_4_load_51 | 53 | 0.00083087 | 0.00020824 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1030-11_0_4_load_52 | 54 | 0.0020269 | 0.00050799 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1030-11_0_4_load_53 | 55 | 0.00051642 | 0.00012943 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1030-11_0_4_load_71 | 56 | 0.0042946 | 0.0010763 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1030-11_0_4_load_65 | 57 | 0.0023503 | 0.00058903 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1030-11_0_4_load_66 | 58 | 0.0037472 | 0.00093915 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1030-11_0_4_load_68 | 59 | 0.0019125 | 0.00047931 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1030-11_0_4_load_31 | 60 | 0.0018115 | 0.000454 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1030-11_0_4_load_32 | 61 | 0.0030941 | 0.00077545 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1030-11_0_4_load_33 | 62 | 0.0016369 | 0.00041025 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1030-11_0_4_load_35 | 63 | 0.0032126 | 0.00080515 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1030-11_0_4_load_40 | 64 | 0.0016316 | 0.00040892 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1030-11_0_4_load_38 | 65 | 0.00070983 | 0.0001779 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1030-11_0_4_load_44 | 66 | 0.0011596 | 0.00029063 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1030-11_0_4_load_45 | 67 | 0.0022136 | 0.00055478 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1030-11_0_4_load_48 | 69 | 0.00040906 | 0.00010252 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1030-11_0_4_load_145 | 70 | 0.00062291 | 0.00015612 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1030-11_0_4_load_72 | 71 | 0.00045847 | 0.0001149 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1030-11_0_4_load_73 | 72 | 7.4038e-05 | 1.8556e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1030-11_0_4_load_74 | 73 | 0.00057812 | 0.00014489 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1030-11_0_4_load_143 | 74 | 0.0010893 | 0.000273 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1030-11_0_4_load_144 | 75 | 0.00064577 | 0.00016184 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1030-11_0_4_load_76 | 76 | 0.0010021 | 0.00025115 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1030-11_0_4_load_75 | 77 | 0.00037997 | 9.523e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1030-11_0_4_load_125 | 78 | 0.00040336 | 0.00010109 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1030-11_0_4_load_146 | 79 | 0.00044826 | 0.00011234 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1030-11_0_4_load_81 | 83 | 0.0030765 | 0.00077104 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1030-11_0_4_load_63 | 84 | 0.00088829 | 0.00022263 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1030-11_0_4_load_78 | 86 | 0.00083453 | 0.00020915 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1030-11_0_4_load_77 | 87 | 0.00030203 | 7.5695e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1030-11_0_4_load_79 | 88 | 0.006298 | 0.0015784 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1030-11_0_4_load_139 | 90 | 0.0002723 | 6.8245e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1030-11_0_4_load_82 | 91 | 0.00021782 | 5.4591e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1030-11_0_4_load_83 | 92 | 0.0004423 | 0.00011085 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1030-11_0_4_load_86 | 95 | 0.001706 | 0.00042757 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1030-11_0_4_load_138 | 97 | 0.00021847 | 5.4753e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1030-11_0_4_load_103 | 98 | 0.0018796 | 0.00047106 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1030-11_0_4_load_112 | 99 | 0.0002125 | 5.3257e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1030-11_0_4_load_133 | 100 | 0.00038328 | 9.606e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1030-11_0_4_load_101 | 102 | 0.0014617 | 0.00036633 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1030-11_0_4_load_115 | 103 | 0.00051502 | 0.00012908 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1030-11_0_4_load_106 | 104 | 0.00016369 | 4.1024e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1030-11_0_4_load_88 | 105 | 0.0059536 | 0.0014921 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1030-11_0_4_load_91 | 109 | 0.0018302 | 0.00045869 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1030-11_0_4_load_92 | 110 | 0.0035244 | 0.00088331 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1030-11_0_4_load_93 | 111 | 0.0056436 | 0.0014144 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1030-11_0_4_load_119 | 112 | 0.0014631 | 0.00036669 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1030-11_0_4_load_113 | 114 | 0.0050259 | 0.0012596 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1030-11_0_4_load_120 | 115 | 0.0031212 | 0.00078226 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1030-11_0_4_load_122 | 116 | 0.0018254 | 0.0004575 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1030-11_0_4_load_94 | 118 | 7.5878e-05 | 1.9017e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1030-11_0_4_load_95 | 119 | 7.8499e-05 | 1.9674e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1030-11_0_4_load_97 | 121 | 0.0006078 | 0.00015233 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1030-11_0_4_load_98 | 122 | 0.00030939 | 7.7541e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1030-11_0_4_load_99 | 123 | 0.00085408 | 0.00021405 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1030-11_0_4_load_118 | 125 | 0.00030057 | 7.533e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1030-11_0_4_load_107 | 126 | 0.00024904 | 6.2414e-05 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1030-11_0_4_load_100 | 127 | 0.0017263 | 0.00043265 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1030-11_0_4_load_102 | 128 | 0.0015449 | 0.0003872 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1030-11_0_4_load_104 | 129 | 0.0016353 | 0.00040985 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1030-11_0_4_load_111 | 131 | 0.0045199 | 0.0011328 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1030-11_0_4_load_130 | 132 | 0.00034111 | 8.549e-05 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1030-11_0_4_load_123 | 133 | 0.00097922 | 0.00024541 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1030-11_0_4_load_142 | 134 | 0.00035876 | 8.9914e-05 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1030-11_0_4_load_126 | 135 | 0.00019883 | 4.9832e-05 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1030-11_0_4_load_127 | 136 | 0.00046628 | 0.00011686 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1030-11_0_4_load_131 | 138 | 0.00020153 | 5.0509e-05 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1030-11_0_4_load_136 | 139 | 0.00018342 | 4.597e-05 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1030-11_0_4_load_137 | 140 | 0.0015835 | 0.00039686 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_1030-11_0_4_load_140 | 141 | 0.00043552 | 0.00010915 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_1030-11_0_4_load_141 | 142 | 0.00032163 | 8.0607e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1030-11_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.042412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1030-11_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.048548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1030-11_0_4_line_2 | NAYY 4x150 SE | 2 | 5 | 0.11152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1030-11_0_4_line_3 | NAYY 4x150 SE | 3 | 4 | 0.027027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1030-11_0_4_line_4 | NAYY 4x150 SE | 4 | 6 | 0.041342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1030-11_0_4_line_5 | NAYY 4x150 SE | 5 | 8 | 0.29758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1030-11_0_4_line_6 | NAYY 4x150 SE | 6 | 7 | 0.022964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1030-11_0_4_line_7 | NAYY 4x150 SE | 7 | 67 | 0.0010313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1030-11_0_4_line_8 | NAYY 4x150 SE | 8 | 9 | 0.10024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1030-11_0_4_line_9 | NAYY 4x150 SE | 9 | 10 | 0.022667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1030-11_0_4_line_10 | NAYY 4x150 SE | 10 | 11 | 0.0071311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1030-11_0_4_line_11 | NAYY 4x150 SE | 11 | 12 | 0.014367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1030-11_0_4_line_12 | NAYY 4x150 SE | 12 | 13 | 0.010969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1030-11_0_4_line_13 | NAYY 4x150 SE | 13 | 14 | 0.015172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1030-11_0_4_line_14 | NAYY 4x150 SE | 14 | 15 | 0.039319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1030-11_0_4_line_15 | NAYY 4x150 SE | 15 | 18 | 0.021671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1030-11_0_4_line_16 | NAYY 4x150 SE | 16 | 17 | 0.037696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1030-11_0_4_line_17 | NAYY 4x150 SE | 17 | 18 | 0.017301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1030-11_0_4_line_18 | NAYY 4x150 SE | 17 | 19 | 0.031569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1030-11_0_4_line_19 | NAYY 4x150 SE | 19 | 20 | 0.036157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1030-11_0_4_line_20 | NAYY 4x150 SE | 19 | 21 | 0.022595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1030-11_0_4_line_21 | NAYY 4x150 SE | 20 | 33 | 0.022543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1030-11_0_4_line_22 | NAYY 4x150 SE | 20 | 34 | 0.040144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1030-11_0_4_line_23 | NAYY 4x150 SE | 21 | 35 | 0.010969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1030-11_0_4_line_24 | NAYY 4x150 SE | 22 | 23 | 0.020757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1030-11_0_4_line_25 | NAYY 4x150 SE | 22 | 24 | 0.039201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1030-11_0_4_line_26 | NAYY 4x150 SE | 23 | 25 | 0.038646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1030-11_0_4_line_27 | NAYY 4x150 SE | 24 | 26 | 0.04235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1030-11_0_4_line_28 | NAYY 4x150 SE | 24 | 27 | 0.04322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1030-11_0_4_line_29 | NAYY 4x150 SE | 25 | 30 | 0.018019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1030-11_0_4_line_30 | NAYY 4x150 SE | 26 | 31 | 0.043671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1030-11_0_4_line_31 | NAYY 4x150 SE | 27 | 32 | 0.029438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1030-11_0_4_line_32 | NAYY 4x150 SE | 28 | 29 | 0.054005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1030-11_0_4_line_33 | NAYY 4x150 SE | 29 | 81 | 0.067857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_1030-11_0_4_line_34 | NAYY 4x150 SE | 29 | 39 | 0.031674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_1030-11_0_4_line_35 | NAYY 4x150 SE | 30 | 61 | 0.0099889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1030-11_0_4_line_36 | NAYY 4x150 SE | 31 | 76 | 0.20069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1030-11_0_4_line_37 | NAYY 4x150 SE | 32 | 84 | 0.016704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1030-11_0_4_line_38 | NAYY 4x150 SE | 35 | 46 | 0.016262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1030-11_0_4_line_39 | NAYY 4x150 SE | 36 | 37 | 0.01189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_1030-11_0_4_line_40 | NAYY 4x150 SE | 36 | 38 | 0.0088156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_1030-11_0_4_line_41 | NAYY 4x150 SE | 37 | 39 | 0.011033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_1030-11_0_4_line_42 | NAYY 4x150 SE | 38 | 40 | 0.20875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_1030-11_0_4_line_43 | NAYY 4x150 SE | 40 | 43 | 0.025277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
44 | LV_1030-11_0_4_line_44 | NAYY 4x150 SE | 40 | 41 | 0.0089007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_1030-11_0_4_line_45 | NAYY 4x150 SE | 41 | 42 | 0.04237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_1030-11_0_4_line_46 | NAYY 4x150 SE | 42 | 65 | 0.0025854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1030-11_0_4_line_47 | NAYY 4x150 SE | 43 | 48 | 0.014098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_1030-11_0_4_line_48 | NAYY 4x150 SE | 43 | 49 | 0.0016308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1030-11_0_4_line_49 | NAYY 4x150 SE | 44 | 45 | 0.010729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1030-11_0_4_line_50 | NAYY 4x150 SE | 44 | 46 | 0.014246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1030-11_0_4_line_51 | NAYY 4x150 SE | 45 | 47 | 0.0094159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1030-11_0_4_line_52 | NAYY 4x150 SE | 47 | 48 | 0.19495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_1030-11_0_4_line_53 | NAYY 4x150 SE | 48 | 50 | 0.025426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1030-11_0_4_line_54 | NAYY 4x150 SE | 50 | 57 | 0.021615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1030-11_0_4_line_55 | NAYY 4x150 SE | 51 | 52 | 0.011426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1030-11_0_4_line_56 | NAYY 4x150 SE | 51 | 53 | 0.026579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1030-11_0_4_line_57 | NAYY 4x150 SE | 52 | 54 | 0.015114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1030-11_0_4_line_58 | NAYY 4x150 SE | 53 | 55 | 0.0013495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1030-11_0_4_line_59 | NAYY 4x150 SE | 54 | 56 | 0.011284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1030-11_0_4_line_60 | NAYY 4x150 SE | 56 | 59 | 0.012688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1030-11_0_4_line_61 | NAYY 4x150 SE | 57 | 58 | 0.0076596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1030-11_0_4_line_62 | NAYY 4x150 SE | 58 | 59 | 0.017338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1030-11_0_4_line_63 | NAYY 4x150 SE | 60 | 61 | 0.013452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1030-11_0_4_line_64 | NAYY 4x150 SE | 60 | 62 | 0.0317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1030-11_0_4_line_65 | NAYY 4x150 SE | 62 | 63 | 0.018482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1030-11_0_4_line_66 | NAYY 4x150 SE | 63 | 64 | 0.00076633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1030-11_0_4_line_67 | NAYY 4x150 SE | 64 | 65 | 0.024441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1030-11_0_4_line_68 | NAYY 4x150 SE | 66 | 67 | 0.0018655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1030-11_0_4_line_69 | NAYY 4x150 SE | 66 | 68 | 0.047405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1030-11_0_4_line_70 | NAYY 4x150 SE | 68 | 69 | 0.088432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1030-11_0_4_line_71 | NAYY 4x150 SE | 68 | 70 | 0.29597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1030-11_0_4_line_72 | NAYY 4x150 SE | 70 | 75 | 0.0061874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1030-11_0_4_line_73 | NAYY 4x150 SE | 71 | 72 | 0.017211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1030-11_0_4_line_74 | NAYY 4x150 SE | 71 | 73 | 0.37092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1030-11_0_4_line_75 | NAYY 4x150 SE | 72 | 74 | 0.018303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1030-11_0_4_line_76 | NAYY 4x150 SE | 73 | 77 | 0.026102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1030-11_0_4_line_77 | NAYY 4x150 SE | 74 | 75 | 0.033692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1030-11_0_4_line_78 | NAYY 4x150 SE | 76 | 77 | 0.015541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1030-11_0_4_line_79 | NAYY 4x150 SE | 78 | 79 | 0.028102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1030-11_0_4_line_80 | NAYY 4x150 SE | 78 | 80 | 0.029763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1030-11_0_4_line_81 | NAYY 4x150 SE | 79 | 134 | 0.017784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1030-11_0_4_line_82 | NAYY 4x150 SE | 80 | 133 | 0.018899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1030-11_0_4_line_83 | NAYY 4x150 SE | 80 | 113 | 0.011875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1030-11_0_4_line_84 | NAYY 4x150 SE | 81 | 82 | 0.064854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
85 | LV_1030-11_0_4_line_85 | NAYY 4x150 SE | 81 | 83 | 0.031964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1030-11_0_4_line_86 | NAYY 4x150 SE | 82 | 85 | 0.002817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
87 | LV_1030-11_0_4_line_87 | NAYY 4x150 SE | 82 | 86 | 0.03023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1030-11_0_4_line_88 | NAYY 4x150 SE | 85 | 89 | 0.03203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
89 | LV_1030-11_0_4_line_89 | NAYY 4x150 SE | 85 | 90 | 0.043884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1030-11_0_4_line_90 | NAYY 4x150 SE | 86 | 87 | 0.00035516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1030-11_0_4_line_91 | NAYY 4x150 SE | 87 | 88 | 0.063022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1030-11_0_4_line_92 | NAYY 4x150 SE | 89 | 132 | 0.032573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
93 | LV_1030-11_0_4_line_93 | NAYY 4x150 SE | 91 | 92 | 0.024234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1030-11_0_4_line_94 | NAYY 4x150 SE | 91 | 93 | 0.028856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1030-11_0_4_line_95 | NAYY 4x150 SE | 93 | 94 | 0.042959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_1030-11_0_4_line_96 | NAYY 4x150 SE | 93 | 95 | 0.082454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_1030-11_0_4_line_97 | NAYY 4x150 SE | 94 | 96 | 0.003157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
98 | LV_1030-11_0_4_line_98 | NAYY 4x150 SE | 94 | 97 | 0.018062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1030-11_0_4_line_99 | NAYY 4x150 SE | 95 | 98 | 0.020161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_1030-11_0_4_line_100 | NAYY 4x150 SE | 96 | 99 | 0.013769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1030-11_0_4_line_101 | NAYY 4x150 SE | 96 | 100 | 0.008751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
102 | LV_1030-11_0_4_line_102 | NAYY 4x150 SE | 97 | 101 | 0.01345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1030-11_0_4_line_103 | NAYY 4x150 SE | 98 | 102 | 0.024664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
104 | LV_1030-11_0_4_line_104 | NAYY 4x150 SE | 99 | 121 | 0.0107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1030-11_0_4_line_105 | NAYY 4x150 SE | 100 | 138 | 0.014721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
106 | LV_1030-11_0_4_line_106 | NAYY 4x150 SE | 101 | 139 | 0.010636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1030-11_0_4_line_107 | NAYY 4x150 SE | 101 | 136 | 0.022348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1030-11_0_4_line_108 | NAYY 4x150 SE | 102 | 127 | 0.010948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
109 | LV_1030-11_0_4_line_109 | NAYY 4x150 SE | 103 | 104 | 0.020093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1030-11_0_4_line_110 | NAYY 4x150 SE | 104 | 124 | 0.0063661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1030-11_0_4_line_111 | NAYY 4x150 SE | 105 | 106 | 0.030263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1030-11_0_4_line_112 | NAYY 4x150 SE | 105 | 107 | 0.054131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
113 | LV_1030-11_0_4_line_113 | NAYY 4x150 SE | 105 | 108 | 0.17355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
114 | LV_1030-11_0_4_line_114 | NAYY 4x150 SE | 106 | 109 | 0.015762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1030-11_0_4_line_115 | NAYY 4x150 SE | 107 | 110 | 0.057575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
116 | LV_1030-11_0_4_line_116 | NAYY 4x150 SE | 107 | 111 | 0.03976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1030-11_0_4_line_117 | NAYY 4x150 SE | 108 | 112 | 0.10693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
118 | LV_1030-11_0_4_line_118 | NAYY 4x150 SE | 109 | 113 | 0.018217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1030-11_0_4_line_119 | NAYY 4x150 SE | 110 | 114 | 0.033851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
120 | LV_1030-11_0_4_line_120 | NAYY 4x150 SE | 112 | 115 | 0.030111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1030-11_0_4_line_121 | NAYY 4x150 SE | 114 | 117 | 0.047388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
122 | LV_1030-11_0_4_line_122 | NAYY 4x150 SE | 115 | 116 | 0.04205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_1030-11_0_4_line_123 | NAYY 4x150 SE | 117 | 130 | 0.014522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
124 | LV_1030-11_0_4_line_124 | NAYY 4x150 SE | 118 | 119 | 0.014172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_1030-11_0_4_line_125 | NAYY 4x150 SE | 118 | 120 | 0.041562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_1030-11_0_4_line_126 | NAYY 4x150 SE | 119 | 121 | 0.012039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_1030-11_0_4_line_127 | NAYY 4x150 SE | 120 | 122 | 0.013285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_1030-11_0_4_line_128 | NAYY 4x150 SE | 120 | 123 | 0.077105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_1030-11_0_4_line_129 | NAYY 4x150 SE | 122 | 124 | 0.014592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_1030-11_0_4_line_130 | NAYY 4x150 SE | 123 | 125 | 0.0034171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_1030-11_0_4_line_131 | NAYY 4x150 SE | 124 | 126 | 0.018577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_1030-11_0_4_line_132 | NAYY 4x150 SE | 127 | 128 | 0.020853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
133 | LV_1030-11_0_4_line_133 | NAYY 4x150 SE | 128 | 129 | 0.012679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
134 | LV_1030-11_0_4_line_134 | NAYY 4x150 SE | 129 | 130 | 0.011807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
135 | LV_1030-11_0_4_line_135 | NAYY 4x150 SE | 130 | 131 | 0.012403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_1030-11_0_4_line_136 | NAYY 4x150 SE | 132 | 137 | 0.010362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
137 | LV_1030-11_0_4_line_137 | NAYY 4x150 SE | 134 | 142 | 0.018091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_1030-11_0_4_line_138 | NAYY 4x150 SE | 135 | 136 | 0.013625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_1030-11_0_4_line_139 | NAYY 4x150 SE | 137 | 138 | 0.032574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
140 | LV_1030-11_0_4_line_140 | NAYY 4x150 SE | 139 | 140 | 0.0063791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_1030-11_0_4_line_141 | NAYY 4x150 SE | 141 | 142 | 0.017703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1030-11_0_4_trafo_36 | 0.25 MVA 20/0.4 kV | 143 | 42 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2664017.0887 | 1232919.4791 | 2664033.0854 | 1232880.1996
1 | 2664033.0854 | 1232880.1996 | 2664051.3964 | 1232835.2375
2 | 2664051.3964 | 1232835.2375 | 2664096.9018 | 1232733.428
3 | 2663778.8012 | 1233236.5941 | 2663776.1266 | 1233235.6943 | 2663767.8919 | 1233232.6261 | 2663752.6994 | 1233230.0037
4 | 2663752.6994 | 1233230.0037 | 2663749.2108 | 1233229.4015 | 2663737.438 | 1233226.5512 | 2663737.9561 | 1233210.0125 | 2663736.6829 | 1233200.9595 | 2663736.6829 | 1233200.9595
5 | 2664259.8848 | 1232484.4448 | 2664096.9018 | 1232733.428
6 | 2663716.1683 | 1233191.154 | 2663721.2118 | 1233192.0879 | 2663736.6829 | 1233200.9595
7 | 2663715.1542 | 1233190.9662 | 2663716.1683 | 1233191.154
8 | 2664193.3218 | 1232409.4948 | 2664259.8848 | 1232484.4448
9 | 2664193.3218 | 1232409.4948 | 2664204.0555 | 1232389.5303
10 | 2664204.0555 | 1232389.5303 | 2664207.4324 | 1232383.2494
11 | 2664207.4324 | 1232383.2494 | 2664214.2359 | 1232370.595
12 | 2664219.4301 | 1232360.9339 | 2664214.2359 | 1232370.595
13 | 2664219.4301 | 1232360.9339 | 2664220.7852 | 1232358.4133 | 2664226.0664 | 1232353.2002 | 2664228.441 | 1232348.9256
14 | 2664228.441 | 1232348.9256 | 2664232.7463 | 1232341.1756 | 2664233.8931 | 1232338.7641 | 2664234.3791 | 1232335.8341 | 2664233.6948 | 1232333.2917 | 2664221.1026 | 1232315.0326
15 | 2664210.6903 | 1232296.1411 | 2664218.6285 | 1232308.5349 | 2664221.1026 | 1232315.0326 | 2664221.1026 | 1232315.0326
16 | 2664196.573 | 1232306.1953 | 2664179.3009 | 1232318.7949 | 2664175.8498 | 1232321.4261 | 2664166.33 | 1232328.6938
17 | 2664210.6903 | 1232296.1411 | 2664203.7526 | 1232301.1917 | 2664196.573 | 1232306.1953
18 | 2664179.2351 | 1232280.0131 | 2664180.0124 | 1232283.0569 | 2664196.573 | 1232306.1953
19 | 2664193.264 | 1232250.1004 | 2664193.8545 | 1232261.3364 | 2664192.1665 | 1232266.8885 | 2664190.3154 | 1232269.3035 | 2664181.3167 | 1232275.1769 | 2664179.9774 | 1232277.186 | 2664179.2351 | 1232280.0131
20 | 2664179.2351 | 1232280.0131 | 2664160.2747 | 1232292.3023
21 | 2664193.264 | 1232250.1004 | 2664170.8376 | 1232252.3854
22 | 2664193.264 | 1232250.1004 | 2664187.3495 | 1232244.5441 | 2664160.8729 | 1232226.5204
23 | 2664151.0699 | 1232298.2684 | 2664160.2747 | 1232292.3023
24 | 2663726.8253 | 1232386.8737 | 2663734.0228 | 1232382.27 | 2663738.9473 | 1232379.9101 | 2663745.2064 | 1232377.3756
25 | 2663697.2083 | 1232361.6509 | 2663705.0959 | 1232366.1384 | 2663711.4163 | 1232370.5979 | 2663715.4508 | 1232374.2658 | 2663719.1988 | 1232377.8194 | 2663726.8253 | 1232386.8737
26 | 2663783.6576 | 1232380.4099 | 2663777.7992 | 1232380.705 | 2663769.9808 | 1232380.3654 | 2663745.2064 | 1232377.3756 | 2663745.2064 | 1232377.3756
27 | 2663697.2083 | 1232361.6509 | 2663683.0882 | 1232355.1065 | 2663658.4699 | 1232344.5477
28 | 2663697.2083 | 1232361.6509 | 2663694.8051 | 1232373.2217 | 2663696.4 | 1232404.5834
29 | 2663783.6576 | 1232380.4099 | 2663788.1711 | 1232380.1826 | 2663800.8754 | 1232375.6184
30 | 2663618.3103 | 1232327.3912 | 2663622.1242 | 1232328.959 | 2663658.4699 | 1232344.5477
31 | 2663697.6119 | 1232433.9916 | 2663697.5506 | 1232427.2088 | 2663696.4 | 1232404.5834
32 | 2663861.9736 | 1232028.855 | 2663830.8544 | 1232072.9922
33 | 2663821.9413 | 1231978.4032 | 2663823.2799 | 1231987.7348 | 2663826.7589 | 1231998.0234 | 2663832.5593 | 1232007.2139 | 2663838.5901 | 1232013.983 | 2663861.9736 | 1232028.855
34 | 2663861.9736 | 1232028.855 | 2663888.6949 | 1232045.8614
35 | 2663800.8754 | 1232375.6184 | 2663801.0024 | 1232375.5727 | 2663808.9551 | 1232369.7542
36 | 2663618.3103 | 1232327.3912 | 2663473.3364 | 1232466.1669
37 | 2663697.6119 | 1232433.9916 | 2663697.703 | 1232444.0771 | 2663694.7498 | 1232450
38 | 2664137.4236 | 1232307.1132 | 2664137.4236 | 1232307.1132 | 2664151.0699 | 1232298.2684
39 | 2663908.0332 | 1232058.169 | 2663898.0024 | 1232051.785
40 | 2663908.0332 | 1232058.169 | 2663903.141 | 1232065.5027
41 | 2663898.0024 | 1232051.785 | 2663888.6949 | 1232045.8614
42 | 2663903.141 | 1232065.5027 | 2663910.6099 | 1232274.1199
43 | 2663935.3301 | 1232268.8452 | 2663921.2441 | 1232271.7958 | 2663910.6099 | 1232274.1199
44 | 2663901.9144 | 1232276.0204 | 2663910.6099 | 1232274.1199
45 | 2663868.8949 | 1232300.7592 | 2663883.517 | 1232284.6432 | 2663889.3507 | 1232280.1363 | 2663899.3769 | 1232276.575 | 2663901.9144 | 1232276.0204
46 | 2663868.8949 | 1232300.7592 | 2663867.1577 | 1232302.6739
47 | 2663935.3301 | 1232268.8452 | 2663935.7972 | 1232272.586 | 2663935.4982 | 1232277.1525 | 2663934.2942 | 1232282.7766 | 2663934.2942 | 1232282.7766
48 | 2663935.3301 | 1232268.8452 | 2663936.9262 | 1232268.5108
49 | 2664130.7821 | 1232319.7164 | 2664125.7802 | 1232329.2081
50 | 2664130.7821 | 1232319.7164 | 2664137.4236 | 1232307.1132
51 | 2664121.3905 | 1232337.5381 | 2664125.7802 | 1232329.2081
52 | 2664121.3905 | 1232337.5381 | 2663934.2942 | 1232282.7766
53 | 2663934.2942 | 1232282.7766 | 2663923.6481 | 1232305.8669
54 | 2663914.512 | 1232325.4557 | 2663920.0982 | 1232313.5664 | 2663923.6481 | 1232305.8669
55 | 2663882.2501 | 1232393.7255 | 2663887.1902 | 1232383.4228
56 | 2663882.2501 | 1232393.7255 | 2663870.7581 | 1232417.6921
57 | 2663887.1902 | 1232383.4228 | 2663891.448 | 1232374.5431 | 2663893.6873 | 1232369.7772
58 | 2663870.1747 | 1232418.9089 | 2663870.7581 | 1232417.6921
59 | 2663898.4859 | 1232359.5642 | 2663893.6873 | 1232369.7772
60 | 2663903.8816 | 1232348.0804 | 2663898.4859 | 1232359.5642
61 | 2663914.512 | 1232325.4557 | 2663911.2547 | 1232332.3882
62 | 2663911.2547 | 1232332.3882 | 2663903.8816 | 1232348.0804
63 | 2663817.9261 | 1232359.7354 | 2663816.4793 | 1232361.5296 | 2663808.9551 | 1232369.7542 | 2663808.9551 | 1232369.7542
64 | 2663817.9261 | 1232359.7354 | 2663835.6884 | 1232337.709 | 2663837.9581 | 1232335.172
65 | 2663850.281 | 1232321.3983 | 2663837.9581 | 1232335.172
66 | 2663850.792 | 1232320.8272 | 2663850.281 | 1232321.3983
67 | 2663850.792 | 1232320.8272 | 2663858.2213 | 1232312.5232 | 2663867.1577 | 1232302.6739
68 | 2663713.3199 | 1233190.6265 | 2663715.1542 | 1233190.9662
69 | 2663670.1115 | 1233192.3406 | 2663680.0057 | 1233197.4055 | 2663686.0034 | 1233195.1571 | 2663692.5801 | 1233189.0458 | 2663703.6211 | 1233188.8306 | 2663713.3199 | 1233190.6265
70 | 2663670.1115 | 1233192.3406 | 2663675.7024 | 1233199.0827 | 2663682.2619 | 1233212.2394 | 2663688.8412 | 1233223.5396 | 2663694.3371 | 1233235.6175 | 2663697.9555 | 1233247.6753 | 2663700.7933 | 1233258.3906 | 2663702.0387 | 1233267.2208 | 2663701.5252 | 1233273.2345
71 | 2663670.1115 | 1233192.3406 | 2663531.7606 | 1232930.6967
72 | 2663533.7247 | 1232924.8293 | 2663531.7606 | 1232930.6967
73 | 2663550.2303 | 1232875.5232 | 2663551.7828 | 1232870.8853 | 2663555.3305 | 1232859.0872
74 | 2663555.3305 | 1232859.0872 | 2663453.6044 | 1232502.3879
75 | 2663550.2303 | 1232875.5232 | 2663544.42 | 1232892.88
76 | 2663453.6044 | 1232502.3879 | 2663453.8849 | 1232501.9529 | 2663467.0632 | 1232480.0235
77 | 2663533.7247 | 1232924.8293 | 2663544.42 | 1232892.88
78 | 2663467.0632 | 1232480.0235 | 2663473.1112 | 1232469.9593 | 2663473.3364 | 1232466.1669
79 | 2663558.4426 | 1232062.4001 | 2663553.5148 | 1232068.1209 | 2663545.4663 | 1232075.8066 | 2663540.3513 | 1232078.2647 | 2663536.6072 | 1232078.4407
80 | 2663509.2657 | 1232067.659 | 2663518.1905 | 1232072.9244 | 2663528.708 | 1232077.2507 | 2663534.9569 | 1232078.5183 | 2663536.6072 | 1232078.4407
81 | 2663570.0493 | 1232048.9254 | 2663558.4426 | 1232062.4001
82 | 2663509.2657 | 1232067.659 | 2663496.8353 | 1232081.8946
83 | 2663517.0854 | 1232058.7033 | 2663515.2072 | 1232060.8513 | 2663509.2657 | 1232067.659
84 | 2663809.941 | 1231914.6993 | 2663811.6944 | 1231922.779 | 2663819.1864 | 1231959.2166 | 2663821.9413 | 1231978.4032
85 | 2663821.9413 | 1231978.4032 | 2663814.2261 | 1231979.6879 | 2663810.4455 | 1231981.9711 | 2663795.5011 | 1231994.8465
86 | 2663809.941 | 1231914.6993 | 2663809.342 | 1231911.9466
87 | 2663809.941 | 1231914.6993 | 2663792.9034 | 1231922.3549 | 2663783.8572 | 1231929.5381
88 | 2663794.5838 | 1231883.6253 | 2663799.8051 | 1231891.0417 | 2663809.342 | 1231911.9466
89 | 2663809.342 | 1231911.9466 | 2663817.6309 | 1231910.846 | 2663826.6014 | 1231909.0299 | 2663835.4538 | 1231904.1106 | 2663843.1652 | 1231896.1437 | 2663846.0319 | 1231891.8598
90 | 2663783.5791 | 1231929.7589 | 2663783.8572 | 1231929.5381
91 | 2663752.1082 | 1231976.086 | 2663757.5667 | 1231969.1511 | 2663770.0802 | 1231957.5443 | 2663771.943 | 1231954.7291 | 2663772.1627 | 1231952.6079 | 2663768.0753 | 1231946.082 | 2663767.5853 | 1231943.753 | 2663768.1187 | 1231942.0353 | 2663783.5791 | 1231929.7589
92 | 2663794.5838 | 1231883.6253 | 2663791.9134 | 1231879.8386 | 2663788.7133 | 1231875.3013 | 2663785.5358 | 1231870.7865 | 2663780.8967 | 1231866.2671 | 2663772.0104 | 1231860.8835
93 | 2663645.6694 | 1231797.7573 | 2663624.9958 | 1231785.1124
94 | 2663671.1665 | 1231811.1218 | 2663658.5182 | 1231805.6162 | 2663645.6694 | 1231797.7573
95 | 2663710.486 | 1231828.6878 | 2663671.1665 | 1231811.1218
96 | 2663671.1665 | 1231811.1218 | 2663655.8962 | 1231857.3998 | 2663642.9705 | 1231887.7036 | 2663642.6434 | 1231888.4073
97 | 2663713.3725 | 1231829.9862 | 2663710.486 | 1231828.6878
98 | 2663710.486 | 1231828.6878 | 2663700.8505 | 1231843.9644
99 | 2663642.6434 | 1231888.4073 | 2663634.1458 | 1231906.6902
100 | 2663713.3725 | 1231829.9862 | 2663720.966 | 1231818.5001
101 | 2663713.3725 | 1231829.9862 | 2663721.3628 | 1231833.555
102 | 2663693.09 | 1231854.9409 | 2663698.8533 | 1231847.1308 | 2663700.8505 | 1231843.9644
103 | 2663634.1458 | 1231906.6902 | 2663630.4753 | 1231914.5875 | 2663628.9715 | 1231917.8291 | 2663622.7145 | 1231928.5139
104 | 2663720.966 | 1231818.5001 | 2663726.8669 | 1231809.5743
105 | 2663721.3628 | 1231833.555 | 2663734.8044 | 1231839.5585
106 | 2663693.09 | 1231854.9409 | 2663686.7734 | 1231863.4982
107 | 2663693.09 | 1231854.9409 | 2663711.702 | 1231867.3118
108 | 2663617.182 | 1231937.9617 | 2663622.7145 | 1231928.5139
109 | 2663733.685 | 1231738.7941 | 2663725.8271 | 1231737.0142 | 2663714.509 | 1231732.918
110 | 2663739.8938 | 1231740.2004 | 2663733.685 | 1231738.7941
111 | 2663491.935 | 1232036.1977 | 2663491.1962 | 1232029.5077 | 2663489.9729 | 1232024.9361 | 2663488.0087 | 1232021.6574 | 2663485.4649 | 1232019.4733 | 2663474.9245 | 1232014.5693
112 | 2663472.679 | 1231972.9841 | 2663458.9517 | 1232003.3019 | 2663459.1502 | 1232005.9836 | 2663461.0057 | 1232008.0936 | 2663474.9245 | 1232014.5693
113 | 2663474.9245 | 1232014.5693 | 2663301.4384 | 1232019.167
114 | 2663491.935 | 1232036.1977 | 2663495.9405 | 1232041.9109 | 2663502.8194 | 1232047.3739
115 | 2663472.679 | 1231972.9841 | 2663489.3463 | 1231936.1378 | 2663491.8126 | 1231933.5291 | 2663494.8684 | 1231933.1615 | 2663504.5838 | 1231937.0543
116 | 2663472.679 | 1231972.9841 | 2663509.6596 | 1231987.5878
117 | 2663301.4384 | 1232019.167 | 2663297.8093 | 1231995.1571 | 2663296.458 | 1231971.3049 | 2663300.3141 | 1231912.6702
118 | 2663517.0854 | 1232058.7033 | 2663502.8194 | 1232047.3739
119 | 2663504.5838 | 1231937.0543 | 2663536.0063 | 1231949.6445
120 | 2663300.3141 | 1231912.6702 | 2663302.2901 | 1231882.6238
121 | 2663577.6847 | 1231966.3458 | 2663550.7249 | 1231952.2817 | 2663548.8654 | 1231954.7969 | 2663536.0063 | 1231949.6445
122 | 2663305.0496 | 1231840.6641 | 2663302.2901 | 1231882.6238
123 | 2663577.6847 | 1231966.3458 | 2663589.9751 | 1231974.1379
124 | 2663741.3223 | 1231787.7088 | 2663733.5064 | 1231799.5313
125 | 2663764.0516 | 1231752.9121 | 2663745.0488 | 1231782.072 | 2663741.3223 | 1231787.7088
126 | 2663733.5064 | 1231799.5313 | 2663726.8669 | 1231809.5743
127 | 2663764.0516 | 1231752.9121 | 2663761.5464 | 1231749.95 | 2663756.7091 | 1231746.2513 | 2663753.6285 | 1231745.0236
128 | 2663764.0516 | 1231752.9121 | 2663776.0458 | 1231751.6288 | 2663786.0422 | 1231748.0892 | 2663795.855 | 1231741.9126 | 2663814.7233 | 1231725.3153 | 2663820.0532 | 1231720.5138 | 2663825.0596 | 1231711.2394
129 | 2663739.8938 | 1231740.2004 | 2663743.6636 | 1231741.0525 | 2663753.6285 | 1231745.0236
130 | 2663826.6828 | 1231708.2324 | 2663825.0596 | 1231711.2394
131 | 2663739.8938 | 1231740.2004 | 2663741.6282 | 1231731.7134 | 2663741.6856 | 1231726.355 | 2663740.1109 | 1231722.0797
132 | 2663617.182 | 1231937.9617 | 2663612.7958 | 1231945.452 | 2663605.2606 | 1231955.0121
133 | 2663597.4122 | 1231964.9697 | 2663605.2606 | 1231955.0121
134 | 2663589.9751 | 1231974.1379 | 2663592.8434 | 1231970.7663 | 2663597.4122 | 1231964.9697
135 | 2663589.9751 | 1231974.1379 | 2663581.9435 | 1231983.5888
136 | 2663763.1477 | 1231855.5142 | 2663772.0104 | 1231860.8835
137 | 2663581.8563 | 1232035.2182 | 2663570.0493 | 1232048.9254
138 | 2663723.0495 | 1231874.8542 | 2663711.702 | 1231867.3118
139 | 2663763.1477 | 1231855.5142 | 2663742.4494 | 1231842.973 | 2663734.8044 | 1231839.5585
140 | 2663682.985 | 1231868.6305 | 2663686.7734 | 1231863.4982
141 | 2663581.8563 | 1232035.2182 | 2663593.4102 | 1232021.8048

## bus_geodata
| x | y | coords
0 | 2664017.0887 | 1232919.4791
1 | 2664033.0854 | 1232880.1996
2 | 2664051.3964 | 1232835.2375
3 | 2663778.8012 | 1233236.5941
4 | 2663752.6994 | 1233230.0037
5 | 2664096.9018 | 1232733.428
6 | 2663736.6829 | 1233200.9595
7 | 2663716.1683 | 1233191.154
8 | 2664259.8848 | 1232484.4448
9 | 2664193.3218 | 1232409.4948
10 | 2664204.0555 | 1232389.5303
11 | 2664207.4324 | 1232383.2494
12 | 2664214.2359 | 1232370.595
13 | 2664219.4301 | 1232360.9339
14 | 2664228.441 | 1232348.9256
15 | 2664221.1026 | 1232315.0326
16 | 2664166.33 | 1232328.6938
17 | 2664196.573 | 1232306.1953
18 | 2664210.6904 | 1232296.1411
19 | 2664179.2351 | 1232280.0131
20 | 2664193.264 | 1232250.1004
21 | 2664160.2747 | 1232292.3023
22 | 2663726.8253 | 1232386.8737
23 | 2663745.2064 | 1232377.3756
24 | 2663697.2083 | 1232361.6509
25 | 2663783.6576 | 1232380.4099
26 | 2663658.4699 | 1232344.5477
27 | 2663696.4 | 1232404.5834
28 | 2663830.8544 | 1232072.9922
29 | 2663861.9736 | 1232028.855
30 | 2663800.8754 | 1232375.6184
31 | 2663618.3103 | 1232327.3912
32 | 2663697.6119 | 1232433.9916
33 | 2664170.8376 | 1232252.3854
34 | 2664160.8729 | 1232226.5204
35 | 2664151.0699 | 1232298.2684
36 | 2663908.0332 | 1232058.169
37 | 2663898.0024 | 1232051.785
38 | 2663903.141 | 1232065.5027
39 | 2663888.6949 | 1232045.8614
40 | 2663910.6099 | 1232274.1199
41 | 2663901.9144 | 1232276.0204
42 | 2663868.8949 | 1232300.7592
43 | 2663935.3301 | 1232268.8452
44 | 2664130.7821 | 1232319.7164
45 | 2664125.7802 | 1232329.2081
46 | 2664137.4236 | 1232307.1132
47 | 2664121.3905 | 1232337.5381
48 | 2663934.2942 | 1232282.7766
49 | 2663936.9262 | 1232268.5108
50 | 2663923.6481 | 1232305.8669
51 | 2663882.2501 | 1232393.7255
52 | 2663887.1902 | 1232383.4228
53 | 2663870.7581 | 1232417.6921
54 | 2663893.6873 | 1232369.7772
55 | 2663870.1747 | 1232418.9089
56 | 2663898.4859 | 1232359.5642
57 | 2663914.512 | 1232325.4557
58 | 2663911.2547 | 1232332.3882
59 | 2663903.8816 | 1232348.0804
60 | 2663817.9261 | 1232359.7354
61 | 2663808.9551 | 1232369.7542
62 | 2663837.9581 | 1232335.172
63 | 2663850.281 | 1232321.3983
64 | 2663850.792 | 1232320.8272
65 | 2663867.1577 | 1232302.6739
66 | 2663713.3199 | 1233190.6265
67 | 2663715.1542 | 1233190.9662
68 | 2663670.1115 | 1233192.3406
69 | 2663701.5252 | 1233273.2345
70 | 2663531.7606 | 1232930.6967
71 | 2663555.3305 | 1232859.0872
72 | 2663550.2303 | 1232875.5232
73 | 2663453.6044 | 1232502.3879
74 | 2663544.42 | 1232892.88
75 | 2663533.7247 | 1232924.8293
76 | 2663473.3364 | 1232466.1669
77 | 2663467.0632 | 1232480.0235
78 | 2663536.6072 | 1232078.4407
79 | 2663558.4426 | 1232062.4001
80 | 2663509.2657 | 1232067.659
81 | 2663821.9413 | 1231978.4032
82 | 2663809.941 | 1231914.6993
83 | 2663795.5011 | 1231994.8465
84 | 2663694.7498 | 1232450
85 | 2663809.342 | 1231911.9466
86 | 2663783.8572 | 1231929.5381
87 | 2663783.5791 | 1231929.7589
88 | 2663752.1082 | 1231976.086
89 | 2663794.5838 | 1231883.6253
90 | 2663846.0319 | 1231891.8598
91 | 2663645.6694 | 1231797.7573
92 | 2663624.9958 | 1231785.1124
93 | 2663671.1665 | 1231811.1218
94 | 2663710.486 | 1231828.6878
95 | 2663642.6434 | 1231888.4073
96 | 2663713.3725 | 1231829.9862
97 | 2663700.8505 | 1231843.9644
98 | 2663634.1458 | 1231906.6902
99 | 2663720.966 | 1231818.5001
100 | 2663721.3628 | 1231833.555
101 | 2663693.09 | 1231854.9409
102 | 2663622.7145 | 1231928.5139
103 | 2663714.509 | 1231732.918
104 | 2663733.685 | 1231738.7941
105 | 2663474.9245 | 1232014.5693
106 | 2663491.935 | 1232036.1977
107 | 2663472.679 | 1231972.9841
108 | 2663301.4384 | 1232019.167
109 | 2663502.8194 | 1232047.3739
110 | 2663504.5838 | 1231937.0543
111 | 2663509.6596 | 1231987.5878
112 | 2663300.3141 | 1231912.6702
113 | 2663517.0854 | 1232058.7033
114 | 2663536.0063 | 1231949.6445
115 | 2663302.2901 | 1231882.6238
116 | 2663305.0496 | 1231840.6641
117 | 2663577.6847 | 1231966.3458
118 | 2663741.3223 | 1231787.7088
119 | 2663733.5064 | 1231799.5313
120 | 2663764.0516 | 1231752.9121
121 | 2663726.8669 | 1231809.5743
122 | 2663753.6285 | 1231745.0236
123 | 2663825.0596 | 1231711.2394
124 | 2663739.8938 | 1231740.2004
125 | 2663826.6828 | 1231708.2324
126 | 2663740.1109 | 1231722.0797
127 | 2663617.182 | 1231937.9617
128 | 2663605.2606 | 1231955.0121
129 | 2663597.4122 | 1231964.9697
130 | 2663589.9751 | 1231974.1379
131 | 2663581.9435 | 1231983.5888
132 | 2663772.0104 | 1231860.8835
133 | 2663496.8353 | 1232081.8946
134 | 2663570.0493 | 1232048.9254
135 | 2663723.0495 | 1231874.8542
136 | 2663711.702 | 1231867.3118
137 | 2663763.1477 | 1231855.5142
138 | 2663734.8044 | 1231839.5585
139 | 2663686.7734 | 1231863.4982
140 | 2663682.985 | 1231868.6305
141 | 2663593.4102 | 1232021.8048
142 | 2663581.8563 | 1232035.2182
143 | 2663935.3301 | 1232268.8452

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97272 | -0.19271 | 0.00013891 | 3.4814e-05
1 | 0.97273 | -0.19265 | 0.0019179 | 0.00048066
2 | 0.97288 | -0.19159 | 0.0007391 | 0.00018524
3 | 0.98105 | -0.13439 | 0.00013741 | 3.4438e-05
4 | 0.98105 | -0.13435 | 0.00044123 | 0.00011058
5 | 0.97334 | -0.18829 | 0.0011453 | 0.00028703
6 | 0.98109 | -0.1341 | 0.00038023 | 9.5294e-05
7 | 0.98112 | -0.13387 | 0.00028497 | 7.142e-05
8 | 0.97505 | -0.17585 | 0.0012354 | 0.00030961
9 | 0.97581 | -0.17036 | 0.004096 | 0.0010266
10 | 0.97612 | -0.16814 | 0.0045589 | 0.0011426
11 | 0.97626 | -0.1671 | 0.0010358 | 0.0002596
12 | 0.97658 | -0.16486 | 0.0010752 | 0.00026946
13 | 0.97683 | -0.16302 | 0.0010364 | 0.00025975
14 | 0.97721 | -0.16032 | 0.00084476 | 0.00021172
15 | 0.97823 | -0.15298 | 0.00084975 | 0.00021297
16 | 0.9792 | -0.14609 | 0.0018307 | 0.00045882
17 | 0.9793 | -0.14537 | 0 | 0
18 | 0.97882 | -0.14874 | 0 | 0
19 | 0.98024 | -0.13861 | 0 | 0
20 | 0.97939 | -0.14471 | 0 | 0
21 | 0.98145 | -0.12999 | 0.0041788 | 0.0010473
22 | 0.99432 | -0.039847 | 0 | 0
23 | 0.99476 | -0.03674 | 0.0014328 | 0.00035909
24 | 0.99349 | -0.045722 | 0 | 0
25 | 0.99566 | -0.030404 | 0.0020602 | 0.00051634
26 | 0.99273 | -0.051104 | 0.00095375 | 0.00023903
27 | 0.99335 | -0.046714 | 0.0010138 | 0.00025409
28 | 0.98697 | -0.090864 | 0.00068096 | 0.00017067
29 | 0.98702 | -0.090486 | 0 | 0
30 | 0.99613 | -0.02708 | 0.0020486 | 0.00051342
31 | 0.992 | -0.056237 | 0.0016055 | 0.00040238
32 | 0.9933 | -0.047086 | 0.00036025 | 9.0288e-05
33 | 0.97915 | -0.14643 | 0.0073235 | 0.0018354
34 | 0.97887 | -0.14843 | 0.0088913 | 0.0022284
35 | 0.98211 | -0.12533 | 0.0044609 | 0.001118
36 | 0.98877 | -0.078204 | 0 | 0
37 | 0.98838 | -0.080941 | 0.0011731 | 0.00029401
38 | 0.98905 | -0.076176 | 0.00018118 | 4.5408e-05
39 | 0.98802 | -0.083438 | 0.0012005 | 0.00030086
40 | 0.99591 | -0.028352 | 0.0048344 | 0.0012116
41 | 0.99661 | -0.023484 | 0.0028542 | 0.00071532
42 | 1 | 0 | -0.20187 | -0.050734
43 | 0.9948 | -0.036031 | 0 | 0
44 | 0.98418 | -0.1106 | 0.0045783 | 0.0011474
45 | 0.985 | -0.10476 | 0.0031753 | 0.00079581
46 | 0.98318 | -0.11769 | 0.0028283 | 0.00070884
47 | 0.98577 | -0.099337 | 0.0035268 | 0.0008839
48 | 0.99421 | -0.040199 | 0.003002 | 0.00075236
49 | 0.9948 | -0.036074 | 0.0025833 | 0.00064743
50 | 0.99328 | -0.046696 | 0.0037806 | 0.0009475
51 | 0.99142 | -0.059869 | 0.0019972 | 0.00050055
52 | 0.99147 | -0.059481 | 0.0038139 | 0.00095586
53 | 0.99136 | -0.060233 | 0.00083087 | 0.00020824
54 | 0.99163 | -0.058382 | 0.0020269 | 0.00050799
55 | 0.99136 | -0.06024 | 0.00051642 | 0.00012943
56 | 0.99177 | -0.057329 | 0.0042946 | 0.0010763
57 | 0.99261 | -0.0514 | 0.0023503 | 0.00058903
58 | 0.9924 | -0.052886 | 0.0037472 | 0.00093915
59 | 0.99202 | -0.055593 | 0.0019125 | 0.00047931
60 | 0.99688 | -0.021859 | 0.0018115 | 0.000454
61 | 0.99643 | -0.025032 | 0.0030941 | 0.00077545
62 | 0.99802 | -0.013816 | 0.0016369 | 0.00041025
63 | 0.99874 | -0.008832 | 0.0032126 | 0.00080515
64 | 0.99877 | -0.0086008 | 0.0016316 | 0.00040892
65 | 0.99988 | -0.00083844 | 0.00070983 | 0.0001779
66 | 0.98113 | -0.13379 | 0.0011596 | 0.00029063
67 | 0.98112 | -0.13386 | 0.0022136 | 0.00055478
68 | 0.98145 | -0.13152 | 0 | 0
69 | 0.9814 | -0.13189 | 0.00040906 | 0.00010252
70 | 0.98361 | -0.11603 | 0.00062291 | 0.00015612
71 | 0.98435 | -0.11072 | 0.00045847 | 0.0001149
72 | 0.98416 | -0.11206 | 7.4038e-05 | 1.8556e-05
73 | 0.98861 | -0.080325 | 0.00057812 | 0.00014489
74 | 0.98397 | -0.11346 | 0.0010893 | 0.000273
75 | 0.98366 | -0.11566 | 0.00064577 | 0.00016184
76 | 0.98913 | -0.076615 | 0.0010021 | 0.00025115
77 | 0.98893 | -0.078037 | 0.00037997 | 9.523e-05
78 | 0.97159 | -0.20074 | 0.00040336 | 0.00010109
79 | 0.97153 | -0.2012 | 0.00044826 | 0.00011234
80 | 0.97168 | -0.20011 | 0 | 0
81 | 0.9849 | -0.10547 | 0 | 0
82 | 0.98297 | -0.11916 | 0 | 0
83 | 0.98476 | -0.10648 | 0.0030765 | 0.00077104
84 | 0.99327 | -0.047237 | 0.00088829 | 0.00022263
85 | 0.98289 | -0.11969 | 0 | 0
86 | 0.98264 | -0.12149 | 0.00083453 | 0.00020915
87 | 0.98264 | -0.12151 | 0.00030203 | 7.5695e-05
88 | 0.98206 | -0.12562 | 0.006298 | 0.0015784
89 | 0.98206 | -0.12561 | 0 | 0
90 | 0.98288 | -0.11981 | 0.0002723 | 6.8245e-05
91 | 0.97842 | -0.15159 | 0.00021782 | 5.4591e-05
92 | 0.9784 | -0.1517 | 0.0004423 | 0.00011085
93 | 0.97845 | -0.15139 | 0 | 0
94 | 0.97942 | -0.14443 | 0 | 0
95 | 0.9766 | -0.16459 | 0.001706 | 0.00042757
96 | 0.9795 | -0.14389 | 0 | 0
97 | 0.97935 | -0.14492 | 0.00021847 | 5.4753e-05
98 | 0.97617 | -0.16771 | 0.0018796 | 0.00047106
99 | 0.97943 | -0.14437 | 0.0002125 | 5.3257e-05
100 | 0.97972 | -0.14228 | 0.00038328 | 9.606e-05
101 | 0.9793 | -0.14527 | 0 | 0
102 | 0.97566 | -0.17136 | 0.0014617 | 0.00036633
103 | 0.97908 | -0.14692 | 0.00051502 | 0.00012908
104 | 0.97909 | -0.14681 | 0.00016369 | 4.1024e-05
105 | 0.97213 | -0.19684 | 0.0059536 | 0.0014921
106 | 0.97192 | -0.19837 | 0 | 0
107 | 0.97258 | -0.19356 | 0 | 0
108 | 0.97158 | -0.20079 | 0 | 0
109 | 0.97181 | -0.19917 | 0.0018302 | 0.00045869
110 | 0.97322 | -0.18892 | 0.0035244 | 0.00088331
111 | 0.97225 | -0.19593 | 0.0056436 | 0.0014144
112 | 0.97108 | -0.20443 | 0.0014631 | 0.00036669
113 | 0.97173 | -0.19974 | 0 | 0
114 | 0.97366 | -0.18578 | 0.0050259 | 0.0012596
115 | 0.97086 | -0.206 | 0.0031212 | 0.00078226
116 | 0.97075 | -0.20682 | 0.0018254 | 0.0004575
117 | 0.97438 | -0.18055 | 0 | 0
118 | 0.97928 | -0.14541 | 7.5878e-05 | 1.9017e-05
119 | 0.97934 | -0.14505 | 7.8499e-05 | 1.9674e-05
120 | 0.97914 | -0.14645 | 0 | 0
121 | 0.97938 | -0.14472 | 0.0006078 | 0.00015233
122 | 0.97912 | -0.14663 | 0.00030939 | 7.7541e-05
123 | 0.97901 | -0.14738 | 0.00085408 | 0.00021405
124 | 0.9791 | -0.14677 | 0 | 0
125 | 0.97901 | -0.14739 | 0.00030057 | 7.533e-05
126 | 0.97909 | -0.14682 | 0.00024904 | 6.2414e-05
127 | 0.97544 | -0.17293 | 0.0017263 | 0.00043265
128 | 0.97505 | -0.17579 | 0.0015449 | 0.0003872
129 | 0.97481 | -0.17746 | 0.0016353 | 0.00040985
130 | 0.97461 | -0.17895 | 0 | 0
131 | 0.97452 | -0.17954 | 0.0045199 | 0.0011328
132 | 0.98121 | -0.13165 | 0.00034111 | 8.549e-05
133 | 0.97165 | -0.20031 | 0.00097922 | 0.00024541
134 | 0.9715 | -0.20141 | 0.00035876 | 8.9914e-05
135 | 0.97928 | -0.14545 | 0.00019883 | 4.9832e-05
136 | 0.97928 | -0.14542 | 0.00046628 | 0.00011686
137 | 0.98094 | -0.13356 | 0 | 0
138 | 0.9801 | -0.13958 | 0.00020153 | 5.0509e-05
139 | 0.97928 | -0.14546 | 0.00018342 | 4.597e-05
140 | 0.97926 | -0.14557 | 0.0015835 | 0.00039686
141 | 0.97146 | -0.20164 | 0.00043552 | 0.00010915
142 | 0.97148 | -0.20156 | 0.00032163 | 8.0607e-05
143 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00013891 | -3.4814e-05 | 0.00013891 | 3.4288e-05 | 1.194e-09 | -5.2602e-07 | 0.0002125 | 0.00021231 | 0.0002125 | 0.97272 | -0.19271 | 0.97273 | -0.19265 | 0.078703
1 | -0.0020568 | -0.00051495 | 0.0020571 | 0.00051447 | 2.9983e-07 | -4.8742e-07 | 0.0031461 | 0.0031459 | 0.0031461 | 0.97273 | -0.19265 | 0.97288 | -0.19159 | 1.1652
2 | -0.0027962 | -0.0006997 | 0.0027975 | 0.00069881 | 1.2724e-06 | -8.96e-07 | 0.0042764 | 0.0042759 | 0.0042764 | 0.97288 | -0.19159 | 0.97334 | -0.18829 | 1.5838
3 | -0.00013741 | -3.4438e-05 | 0.00013741 | 3.4097e-05 | 7.3214e-10 | -3.4098e-07 | 0.00020842 | 0.0002083 | 0.00020842 | 0.98105 | -0.13439 | 0.98105 | -0.13435 | 0.077192
4 | -0.00057864 | -0.00014468 | 0.00057866 | 0.00014416 | 1.9861e-08 | -5.144e-07 | 0.00087753 | 0.00087734 | 0.00087753 | 0.98105 | -0.13435 | 0.98109 | -0.1341 | 0.32501
5 | -0.0039427 | -0.00098583 | 0.0039495 | 0.00098472 | 6.7431e-06 | -1.1117e-06 | 0.0060267 | 0.0060254 | 0.0060267 | 0.97334 | -0.18829 | 0.97505 | -0.17585 | 2.2321
6 | -0.00095888 | -0.00023946 | 0.00095891 | 0.00023918 | 3.0293e-08 | -2.7834e-07 | 0.001454 | 0.0014539 | 0.001454 | 0.98109 | -0.1341 | 0.98112 | -0.13387 | 0.53853
7 | -0.0012439 | -0.0003106 | 0.0012439 | 0.00031059 | 2.2894e-09 | -1.2144e-08 | 0.0018861 | 0.0018861 | 0.0018861 | 0.98112 | -0.13387 | 0.98112 | -0.13386 | 0.69856
8 | -0.0051848 | -0.0012943 | 0.0051887 | 0.0012946 | 3.9141e-06 | 2.5415e-07 | 0.0079107 | 0.0079102 | 0.0079107 | 0.97505 | -0.17585 | 0.97581 | -0.17036 | 2.9299
9 | -0.0092848 | -0.0023212 | 0.0092876 | 0.002322 | 2.8345e-06 | 8.0693e-07 | 0.014156 | 0.014156 | 0.014156 | 0.97581 | -0.17036 | 0.97612 | -0.16814 | 5.2431
10 | -0.013847 | -0.0034645 | 0.013849 | 0.0034652 | 1.9822e-06 | 6.7323e-07 | 0.021106 | 0.021106 | 0.021106 | 0.97612 | -0.16814 | 0.97626 | -0.1671 | 7.817
11 | -0.014884 | -0.0037248 | 0.014889 | 0.0037264 | 4.6134e-06 | 1.5947e-06 | 0.022685 | 0.022685 | 0.022685 | 0.97626 | -0.1671 | 0.97658 | -0.16486 | 8.4017
12 | -0.015964 | -0.0039959 | 0.015968 | 0.0039973 | 4.0493e-06 | 1.4201e-06 | 0.024323 | 0.024323 | 0.024323 | 0.97658 | -0.16486 | 0.97683 | -0.16302 | 9.0085
13 | -0.017005 | -0.004257 | 0.017011 | 0.0042593 | 6.3517e-06 | 2.2529e-06 | 0.025902 | 0.025901 | 0.025902 | 0.97683 | -0.16302 | 0.97721 | -0.16032 | 9.5932
14 | -0.017856 | -0.004471 | 0.017874 | 0.0044775 | 1.8136e-05 | 6.4821e-06 | 0.027188 | 0.027188 | 0.027188 | 0.97721 | -0.16032 | 0.97823 | -0.15298 | 10.0696
15 | -0.018724 | -0.0046905 | 0.018735 | 0.0046944 | 1.0968e-05 | 3.9464e-06 | 0.02848 | 0.02848 | 0.02848 | 0.97823 | -0.15298 | 0.97882 | -0.14874 | 10.5482
16 | -0.0018307 | -0.00045882 | 0.0018309 | 0.00045842 | 1.8204e-07 | -4.0421e-07 | 0.002782 | 0.0027819 | 0.002782 | 0.9792 | -0.14609 | 0.9793 | -0.14537 | 1.0304
17 | 0.018743 | 0.0046976 | -0.018735 | -0.0046944 | 8.7567e-06 | 3.1504e-06 | 0.02848 | 0.02848 | 0.02848 | 0.9793 | -0.14537 | 0.97882 | -0.14874 | 10.5482
18 | -0.020574 | -0.005156 | 0.020593 | 0.005163 | 1.9252e-05 | 7.007e-06 | 0.031262 | 0.031262 | 0.031262 | 0.9793 | -0.14537 | 0.98024 | -0.13861 | 11.5785
19 | 0.016235 | 0.0040703 | -0.016221 | -0.0040654 | 1.3704e-05 | 4.8153e-06 | 0.024645 | 0.024645 | 0.024645 | 0.98024 | -0.13861 | 0.97939 | -0.14471 | 9.1279
20 | -0.036828 | -0.0092332 | 0.036872 | 0.0092499 | 4.4068e-05 | 1.6664e-05 | 0.055907 | 0.055907 | 0.055907 | 0.98024 | -0.13861 | 0.98145 | -0.12999 | 20.7062
21 | 0.0073253 | 0.0018358 | -0.0073235 | -0.0018354 | 1.7424e-06 | 3.8654e-07 | 0.011129 | 0.01113 | 0.01113 | 0.97939 | -0.14471 | 0.97915 | -0.14643 | 4.1221
22 | 0.0088958 | 0.0022296 | -0.0088913 | -0.0022284 | 4.5761e-06 | 1.2551e-06 | 0.013516 | 0.013516 | 0.013516 | 0.97939 | -0.14471 | 0.97887 | -0.14843 | 5.0059
23 | -0.041051 | -0.010297 | 0.041078 | 0.010307 | 2.6517e-05 | 1.006e-05 | 0.062242 | 0.062242 | 0.062242 | 0.98145 | -0.12999 | 0.98211 | -0.12533 | 23.0527
24 | -0.014811 | -0.0037089 | 0.014818 | 0.0037111 | 6.3629e-06 | 2.1779e-06 | 0.022164 | 0.022164 | 0.022164 | 0.99432 | -0.039847 | 0.99476 | -0.03674 | 8.2089
25 | 0.014811 | 0.0037089 | -0.014799 | -0.0037048 | 1.2017e-05 | 4.1138e-06 | 0.022164 | 0.022164 | 0.022164 | 0.99432 | -0.039847 | 0.99349 | -0.045722 | 8.209
26 | -0.01625 | -0.0040702 | 0.016265 | 0.0040752 | 1.4248e-05 | 4.9779e-06 | 0.024307 | 0.024307 | 0.024307 | 0.99476 | -0.03674 | 0.99566 | -0.030404 | 9.0027
27 | 0.012536 | 0.0031388 | -0.012527 | -0.0031358 | 9.3161e-06 | 3.0351e-06 | 0.018776 | 0.018776 | 0.018776 | 0.99349 | -0.045722 | 0.99273 | -0.051104 | 6.954
28 | 0.0022628 | 0.000566 | -0.0022624 | -0.00056644 | 3.0971e-07 | -4.4046e-07 | 0.0033887 | 0.0033889 | 0.0033889 | 0.99349 | -0.045722 | 0.99335 | -0.046714 | 1.2551
29 | -0.018325 | -0.0045915 | 0.018333 | 0.0045945 | 8.4326e-06 | 3.0089e-06 | 0.027386 | 0.027386 | 0.027386 | 0.99566 | -0.030404 | 0.99613 | -0.02708 | 10.143
30 | 0.011573 | 0.0028968 | -0.011565 | -0.0028942 | 8.1997e-06 | 2.5895e-06 | 0.017346 | 0.017346 | 0.017346 | 0.99273 | -0.051104 | 0.992 | -0.056237 | 6.4246
31 | 0.0012486 | 0.00031235 | -0.0012486 | -0.0003127 | 6.4254e-08 | -3.5635e-07 | 0.0018702 | 0.0018703 | 0.0018703 | 0.99335 | -0.046714 | 0.9933 | -0.047086 | 0.69272
32 | -0.00068096 | -0.00017067 | 0.000681 | 0.00016999 | 3.5511e-08 | -6.7654e-07 | 0.0010267 | 0.0010264 | 0.0010267 | 0.98697 | -0.090864 | 0.98702 | -0.090486 | 0.38025
33 | 0.064928 | 0.016324 | -0.064793 | -0.016275 | 0.00013529 | 4.9437e-05 | 0.097903 | 0.097904 | 0.097904 | 0.98702 | -0.090486 | 0.9849 | -0.10547 | 12.0869
34 | -0.065609 | -0.016494 | 0.065674 | 0.016518 | 6.4479e-05 | 2.3584e-05 | 0.09893 | 0.098929 | 0.09893 | 0.98702 | -0.090486 | 0.98802 | -0.083438 | 12.2135
35 | -0.020382 | -0.0051079 | 0.020388 | 0.00511 | 5.7779e-06 | 2.0922e-06 | 0.030446 | 0.030446 | 0.030446 | 0.99613 | -0.02708 | 0.99643 | -0.025032 | 11.2764
36 | 0.0099597 | 0.0024918 | -0.0099318 | -0.0024836 | 2.7947e-05 | 8.1652e-06 | 0.014938 | 0.014939 | 0.014939 | 0.992 | -0.056237 | 0.98913 | -0.076615 | 5.533
37 | 0.00088831 | 0.00022242 | -0.00088829 | -0.00022263 | 1.8457e-08 | -2.0911e-07 | 0.0013307 | 0.0013307 | 0.0013307 | 0.9933 | -0.047086 | 0.99327 | -0.047237 | 0.49286
38 | -0.045539 | -0.011425 | 0.045587 | 0.011444 | 4.8314e-05 | 1.8376e-05 | 0.069001 | 0.069001 | 0.069001 | 0.98211 | -0.12533 | 0.98318 | -0.11769 | 25.556
39 | 0.068097 | 0.017131 | -0.068071 | -0.017121 | 2.5985e-05 | 9.5367e-06 | 0.1025 | 0.1025 | 0.1025 | 0.98877 | -0.078204 | 0.98838 | -0.080941 | 12.6547
40 | -0.068097 | -0.017131 | 0.068116 | 0.017138 | 1.9266e-05 | 7.0706e-06 | 0.1025 | 0.1025 | 0.1025 | 0.98877 | -0.078204 | 0.98905 | -0.076176 | 12.6547
41 | 0.066897 | 0.016827 | -0.066874 | -0.016819 | 2.3287e-05 | 8.5326e-06 | 0.10074 | 0.10074 | 0.10074 | 0.98838 | -0.080941 | 0.98802 | -0.083438 | 12.4367
42 | -0.068297 | -0.017183 | 0.068756 | 0.017352 | 0.00045862 | 0.0001683 | 0.10278 | 0.10277 | 0.10278 | 0.98905 | -0.076176 | 0.99591 | -0.028352 | 12.6883
43 | 0.091383 | 0.023024 | -0.091285 | -0.022987 | 9.8077e-05 | 3.6736e-05 | 0.13658 | 0.13658 | 0.13658 | 0.99591 | -0.028352 | 0.9948 | -0.036031 | 16.8619
44 | -0.16497 | -0.041587 | 0.16509 | 0.04163 | 0.00011256 | 4.2946e-05 | 0.24658 | 0.24658 | 0.24658 | 0.99591 | -0.028352 | 0.99661 | -0.023484 | 30.4416
45 | -0.16794 | -0.042345 | 0.16849 | 0.042557 | 0.00055451 | 0.00021161 | 0.25084 | 0.25084 | 0.25084 | 0.99661 | -0.023484 | 1 | 0 | 30.9677
46 | 0.03258 | 0.0081775 | -0.032577 | -0.0081761 | 3.7924e-06 | 1.4247e-06 | 0.048484 | 0.048485 | 0.048485 | 1 | 0 | 0.99988 | -0.00083844 | 17.9572
47 | 0.088702 | 0.02234 | -0.08865 | -0.02232 | 5.1649e-05 | 1.9316e-05 | 0.13272 | 0.13272 | 0.13272 | 0.9948 | -0.036031 | 0.99421 | -0.040199 | 16.3849
48 | 0.0025833 | 0.00064742 | -0.0025833 | -0.00064743 | 1.5194e-08 | -1.5329e-08 | 0.0038641 | 0.0038641 | 0.0038641 | 0.9948 | -0.036031 | 0.9948 | -0.036074 | 1.4311
49 | -0.053041 | -0.013318 | 0.053084 | 0.013335 | 4.3066e-05 | 1.6427e-05 | 0.080204 | 0.080204 | 0.080204 | 0.98418 | -0.1106 | 0.985 | -0.10476 | 29.7051
50 | 0.048463 | 0.012171 | -0.048415 | -0.012153 | 4.7739e-05 | 1.818e-05 | 0.073282 | 0.073282 | 0.073282 | 0.98418 | -0.1106 | 0.98318 | -0.11769 | 27.1414
51 | -0.05626 | -0.01413 | 0.056302 | 0.014147 | 4.2451e-05 | 1.6207e-05 | 0.085 | 0.085 | 0.085 | 0.985 | -0.10476 | 0.98577 | -0.099337 | 31.4817
52 | -0.059829 | -0.01503 | 0.060325 | 0.015216 | 0.00049621 | 0.00018584 | 0.090324 | 0.090322 | 0.090324 | 0.98577 | -0.099337 | 0.99421 | -0.040199 | 16.7267
53 | 0.025323 | 0.0063516 | -0.0253 | -0.0063432 | 2.2793e-05 | 8.4371e-06 | 0.037902 | 0.037902 | 0.037902 | 0.99421 | -0.040199 | 0.99328 | -0.046696 | 14.0379
54 | 0.021519 | 0.0053957 | -0.021505 | -0.0053905 | 1.4018e-05 | 5.112e-06 | 0.032239 | 0.032239 | 0.032239 | 0.99328 | -0.046696 | 0.99261 | -0.0514 | 11.9403
55 | -0.0033446 | -0.00083788 | 0.0033448 | 0.0008378 | 1.7965e-07 | -7.8247e-08 | 0.0050198 | 0.0050197 | 0.0050198 | 0.99142 | -0.059869 | 0.99147 | -0.059481 | 1.8592
56 | 0.0013474 | 0.00033733 | -0.0013473 | -0.00033765 | 6.7823e-08 | -3.1664e-07 | 0.0020221 | 0.0020223 | 0.0020223 | 0.99142 | -0.059869 | 0.99136 | -0.060233 | 0.74898
57 | -0.0071587 | -0.0017937 | 0.0071598 | 0.0017939 | 1.0886e-06 | 2.2374e-07 | 0.010744 | 0.010744 | 0.010744 | 0.99147 | -0.059481 | 0.99163 | -0.058382 | 3.9791
58 | 0.00051642 | 0.00012941 | -0.00051642 | -0.00012943 | 5.0592e-10 | -1.7205e-08 | 0.00077513 | 0.00077514 | 0.00077514 | 0.99136 | -0.060233 | 0.99136 | -0.06024 | 0.28709
59 | -0.0091867 | -0.0023019 | 0.009188 | 0.0023022 | 1.3381e-06 | 3.6904e-07 | 0.013785 | 0.013785 | 0.013785 | 0.99163 | -0.058382 | 0.99177 | -0.057329 | 5.1056
60 | -0.013483 | -0.0033786 | 0.013486 | 0.0033796 | 3.2398e-06 | 1.0823e-06 | 0.020228 | 0.020228 | 0.020228 | 0.99177 | -0.057329 | 0.99202 | -0.055593 | 7.492
61 | 0.019155 | 0.0048015 | -0.019151 | -0.0048001 | 3.9412e-06 | 1.4168e-06 | 0.028716 | 0.028716 | 0.028716 | 0.99261 | -0.0514 | 0.9924 | -0.052886 | 10.6354
62 | 0.015404 | 0.0038609 | -0.015398 | -0.0038589 | 5.7716e-06 | 1.9959e-06 | 0.023097 | 0.023097 | 0.023097 | 0.9924 | -0.052886 | 0.99202 | -0.055593 | 8.5545
63 | 0.023492 | 0.0058893 | -0.023482 | -0.0058855 | 1.0322e-05 | 3.7947e-06 | 0.035067 | 0.035067 | 0.035067 | 0.99688 | -0.021859 | 0.99643 | -0.025032 | 12.9877
64 | -0.025304 | -0.0063433 | 0.025332 | 0.0063537 | 2.822e-05 | 1.044e-05 | 0.037771 | 0.03777 | 0.037771 | 0.99688 | -0.021859 | 0.99802 | -0.013816 | 13.9891
65 | -0.026969 | -0.006764 | 0.026987 | 0.0067709 | 1.8647e-05 | 6.9303e-06 | 0.040211 | 0.040211 | 0.040211 | 0.99802 | -0.013816 | 0.99874 | -0.008832 | 14.893
66 | -0.0302 | -0.0075761 | 0.030201 | 0.0075764 | 9.6823e-07 | 3.6237e-07 | 0.044997 | 0.044997 | 0.044997 | 0.99874 | -0.008832 | 0.99877 | -0.0086008 | 16.6657
67 | -0.031833 | -0.0079853 | 0.031867 | 0.0079982 | 3.4307e-05 | 1.2875e-05 | 0.047428 | 0.047428 | 0.047428 | 0.99877 | -0.0086008 | 0.99988 | -0.00083844 | 17.566
68 | 0.0034575 | 0.00086535 | -0.0034575 | -0.00086536 | 3.2003e-08 | -1.125e-08 | 0.0052433 | 0.0052433 | 0.0052433 | 0.98113 | -0.13379 | 0.98112 | -0.13386 | 1.942
69 | -0.0046171 | -0.001156 | 0.0046186 | 0.0011559 | 1.4503e-06 | -4.1068e-08 | 0.0070021 | 0.0070019 | 0.0070021 | 0.98113 | -0.13379 | 0.98145 | -0.13152 | 2.5934
70 | 0.00040908 | 0.00010141 | -0.00040906 | -0.00010252 | 2.1214e-08 | -1.1093e-06 | 0.00061983 | 0.00062023 | 0.00062023 | 0.98145 | -0.13152 | 0.9814 | -0.13189 | 0.22971
71 | -0.0050277 | -0.0012574 | 0.0050384 | 0.0012577 | 1.0727e-05 | 3.7716e-07 | 0.0076217 | 0.0076204 | 0.0076217 | 0.98145 | -0.13152 | 0.98361 | -0.11603 | 2.8228
72 | -0.0056613 | -0.0014138 | 0.0056616 | 0.0014139 | 2.8308e-07 | 3.0339e-08 | 0.0085627 | 0.0085627 | 0.0085627 | 0.98361 | -0.11603 | 0.98366 | -0.11566 | 3.1714
73 | 0.0074754 | 0.0018682 | -0.007474 | -0.0018679 | 1.371e-06 | 3.0855e-07 | 0.011298 | 0.011299 | 0.011299 | 0.98435 | -0.11072 | 0.98416 | -0.11206 | 4.1846
74 | -0.0079338 | -0.0019831 | 0.0079671 | 0.0019912 | 3.3278e-05 | 8.0636e-06 | 0.011992 | 0.01199 | 0.011992 | 0.98435 | -0.11072 | 0.98861 | -0.080325 | 4.4413
75 | 0.0074 | 0.0018493 | -0.0073985 | -0.001849 | 1.4293e-06 | 3.1718e-07 | 0.011187 | 0.011187 | 0.011187 | 0.98416 | -0.11206 | 0.98397 | -0.11346 | 4.1432
76 | -0.0085452 | -0.0021361 | 0.0085479 | 0.0021368 | 2.6936e-06 | 7.0121e-07 | 0.01286 | 0.01286 | 0.01286 | 0.98861 | -0.080325 | 0.98893 | -0.078037 | 4.763
77 | 0.0063093 | 0.001576 | -0.0063073 | -0.0015757 | 1.9132e-06 | 3.0802e-07 | 0.0095394 | 0.0095395 | 0.0095395 | 0.98397 | -0.11346 | 0.98366 | -0.11566 | 3.5332
78 | 0.0089296 | 0.0022325 | -0.0089279 | -0.002232 | 1.7495e-06 | 4.7344e-07 | 0.013432 | 0.013432 | 0.013432 | 0.98913 | -0.076615 | 0.98893 | -0.078037 | 4.9747
79 | 0.0015643 | 0.00039106 | -0.0015642 | -0.00039137 | 1.0063e-07 | -3.0931e-07 | 0.0023954 | 0.0023956 | 0.0023956 | 0.97159 | -0.20074 | 0.97153 | -0.2012 | 0.88725
80 | -0.0019677 | -0.00049216 | 0.0019678 | 0.00049185 | 1.6862e-07 | -3.0378e-07 | 0.0030132 | 0.0030131 | 0.0030132 | 0.97159 | -0.20074 | 0.97168 | -0.20011 | 1.116
81 | 0.001116 | 0.00027903 | -0.0011159 | -0.00027924 | 3.2414e-08 | -2.0775e-07 | 0.001709 | 0.0017091 | 0.0017091 | 0.97153 | -0.2012 | 0.9715 | -0.20141 | 0.63299
82 | 0.00097924 | 0.00024519 | -0.00097922 | -0.00024541 | 2.6519e-08 | -2.2389e-07 | 0.0014995 | 0.0014996 | 0.0014996 | 0.97168 | -0.20011 | 0.97165 | -0.20031 | 0.55541
83 | -0.0029471 | -0.00073704 | 0.0029472 | 0.00073695 | 1.5089e-07 | -8.9064e-08 | 0.0045126 | 0.0045125 | 0.0045126 | 0.97168 | -0.20011 | 0.97173 | -0.19974 | 1.6713
84 | 0.061716 | 0.015504 | -0.061599 | -0.015461 | 0.00011731 | 4.265e-05 | 0.093255 | 0.093256 | 0.093256 | 0.9849 | -0.10547 | 0.98297 | -0.11916 | 11.5131
85 | 0.0030769 | 0.0007708 | -0.0030765 | -0.00077104 | 4.3102e-07 | -2.4094e-07 | 0.0046486 | 0.0046487 | 0.0046487 | 0.9849 | -0.10547 | 0.98476 | -0.10648 | 1.7217
86 | 0.054158 | 0.013597 | -0.054154 | -0.013596 | 3.9392e-06 | 1.4079e-06 | 0.081993 | 0.081993 | 0.081993 | 0.98297 | -0.11916 | 0.98289 | -0.11969 | 10.1226
87 | 0.0074405 | 0.0018644 | -0.0074381 | -0.0018638 | 2.3931e-06 | 5.3734e-07 | 0.011263 | 0.011263 | 0.011263 | 0.98297 | -0.11916 | 0.98264 | -0.12149 | 4.1716
88 | 0.053882 | 0.013528 | -0.053838 | -0.013512 | 4.4341e-05 | 1.5837e-05 | 0.081581 | 0.081581 | 0.081581 | 0.98289 | -0.11969 | 0.98206 | -0.12561 | 10.0718
89 | 0.0002723 | 6.769e-05 | -0.0002723 | -6.8245e-05 | 4.6515e-09 | -5.544e-07 | 0.00041205 | 0.00041225 | 0.00041225 | 0.98289 | -0.11969 | 0.98288 | -0.11981 | 0.15268
90 | 0.0066036 | 0.0016547 | -0.0066036 | -0.0016547 | 2.2161e-08 | 4.0241e-09 | 0.0099997 | 0.0099997 | 0.0099997 | 0.98264 | -0.12149 | 0.98264 | -0.12151 | 3.7036
91 | 0.0063015 | 0.001579 | -0.006298 | -0.0015784 | 3.581e-06 | 5.7942e-07 | 0.0095424 | 0.0095426 | 0.0095426 | 0.98264 | -0.12151 | 0.98206 | -0.12562 | 3.5343
92 | 0.053838 | 0.013512 | -0.053793 | -0.013496 | 4.5093e-05 | 1.6108e-05 | 0.081581 | 0.081582 | 0.081582 | 0.98206 | -0.12561 | 0.98121 | -0.13165 | 10.0718
93 | 0.0004423 | 0.00011055 | -0.0004423 | -0.00011085 | 6.8415e-09 | -3.0172e-07 | 0.00067256 | 0.00067267 | 0.00067267 | 0.97842 | -0.15159 | 0.9784 | -0.1517 | 0.24914
94 | -0.00066012 | -0.00016514 | 0.00066014 | 0.00016478 | 1.8142e-08 | -3.5544e-07 | 0.0010038 | 0.0010037 | 0.0010038 | 0.97842 | -0.15159 | 0.97845 | -0.15139 | 0.37179
95 | -0.046709 | -0.01171 | 0.046754 | 0.011726 | 4.5089e-05 | 1.5722e-05 | 0.071036 | 0.071035 | 0.071036 | 0.97845 | -0.15139 | 0.97942 | -0.14443 | 8.7699
96 | 0.046049 | 0.011545 | -0.045965 | -0.011516 | 8.4116e-05 | 2.9251e-05 | 0.070032 | 0.070033 | 0.070033 | 0.97845 | -0.15139 | 0.9766 | -0.16459 | 8.6461
97 | -0.049405 | -0.012389 | 0.049409 | 0.012391 | 3.6998e-06 | 1.3038e-06 | 0.075063 | 0.075062 | 0.075063 | 0.97942 | -0.14443 | 0.9795 | -0.14389 | 9.267
98 | 0.0026509 | 0.00066336 | -0.0026507 | -0.00066352 | 1.8278e-07 | -1.5699e-07 | 0.0040271 | 0.0040272 | 0.0040272 | 0.97942 | -0.14443 | 0.97935 | -0.14492 | 1.4915
99 | 0.044259 | 0.011089 | -0.04424 | -0.011082 | 1.9069e-05 | 6.5779e-06 | 0.067434 | 0.067434 | 0.067434 | 0.9766 | -0.16459 | 0.97617 | -0.16771 | 8.3252
100 | 0.0033676 | 0.00084107 | -0.0033674 | -0.00084116 | 2.2479e-07 | -8.6841e-08 | 0.0051149 | 0.005115 | 0.005115 | 0.9795 | -0.14389 | 0.97943 | -0.14437 | 1.8944
101 | -0.052776 | -0.013232 | 0.052788 | 0.013236 | 1.1701e-05 | 4.1699e-06 | 0.080177 | 0.080177 | 0.080177 | 0.9795 | -0.14389 | 0.97972 | -0.14228 | 9.8984
102 | 0.0024322 | 0.00060877 | -0.0024321 | -0.00060889 | 1.146e-07 | -1.2516e-07 | 0.0036952 | 0.0036953 | 0.0036953 | 0.97935 | -0.14492 | 0.9793 | -0.14527 | 1.3686
103 | 0.04236 | 0.010611 | -0.042339 | -0.010604 | 2.1389e-05 | 7.3019e-06 | 0.064569 | 0.06457 | 0.06457 | 0.97617 | -0.16771 | 0.97566 | -0.17136 | 7.9715
104 | 0.0031549 | 0.0007879 | -0.0031548 | -0.00078798 | 1.5333e-07 | -7.568e-08 | 0.0047922 | 0.0047922 | 0.0047922 | 0.97943 | -0.14437 | 0.97938 | -0.14472 | 1.7749
105 | -0.053171 | -0.013332 | 0.053191 | 0.013339 | 1.9971e-05 | 7.1248e-06 | 0.080759 | 0.080759 | 0.080759 | 0.97972 | -0.14228 | 0.9801 | -0.13958 | 9.9703
106 | 0.001767 | 0.00044265 | -0.0017669 | -0.00044276 | 4.7841e-08 | -1.1542e-07 | 0.0026848 | 0.0026849 | 0.0026849 | 0.9793 | -0.14527 | 0.97928 | -0.14546 | 0.99439
107 | 0.00066512 | 0.00016625 | -0.00066511 | -0.00016652 | 1.424e-08 | -2.757e-07 | 0.0010105 | 0.0010106 | 0.0010106 | 0.9793 | -0.14527 | 0.97928 | -0.14542 | 0.37429
108 | 0.040877 | 0.010237 | -0.040868 | -0.010234 | 8.8502e-06 | 2.9938e-06 | 0.06234 | 0.06234 | 0.06234 | 0.97566 | -0.17136 | 0.97544 | -0.17293 | 7.6963
109 | -0.00051502 | -0.00012908 | 0.00051503 | 0.00012883 | 7.6811e-09 | -2.4975e-07 | 0.00078274 | 0.00078265 | 0.00078274 | 0.97908 | -0.14692 | 0.97909 | -0.14681 | 0.2899
110 | -0.00067872 | -0.00016985 | 0.00067872 | 0.00016977 | 4.2259e-09 | -7.8438e-08 | 0.0010314 | 0.0010314 | 0.0010314 | 0.97909 | -0.14681 | 0.9791 | -0.14677 | 0.38201
111 | 0.0047792 | 0.0011955 | -0.0047782 | -0.0011955 | 1.0104e-06 | 1.3484e-08 | 0.0073146 | 0.0073147 | 0.0073147 | 0.97213 | -0.19684 | 0.97192 | -0.19837 | 2.7092
112 | -0.017151 | -0.0042872 | 0.017158 | 0.0042881 | 7.7569e-06 | 9.6911e-07 | 0.026248 | 0.026247 | 0.026248 | 0.97213 | -0.19684 | 0.97258 | -0.19356 | 3.2405
113 | 0.0064178 | 0.0015995 | -0.0064143 | -0.0016046 | 3.4821e-06 | -5.1121e-06 | 0.0098204 | 0.0098227 | 0.0098227 | 0.97213 | -0.19684 | 0.97158 | -0.20079 | 1.2127
114 | 0.0047782 | 0.0011955 | -0.0047776 | -0.0011955 | 5.2624e-07 | 7.093e-09 | 0.0073147 | 0.0073148 | 0.0073148 | 0.97192 | -0.19837 | 0.97181 | -0.19917 | 2.7092
115 | -0.022804 | -0.0057028 | 0.022818 | 0.0057062 | 1.4573e-05 | 3.4601e-06 | 0.034884 | 0.034884 | 0.034884 | 0.97258 | -0.19356 | 0.97322 | -0.18892 | 4.3067
116 | 0.0056454 | 0.0014146 | -0.0056436 | -0.0014144 | 1.8509e-06 | 2.1865e-07 | 0.0086372 | 0.0086374 | 0.0086374 | 0.97258 | -0.19356 | 0.97225 | -0.19593 | 3.199
117 | 0.0064143 | 0.0016046 | -0.0064111 | -0.001606 | 3.2194e-06 | -1.409e-06 | 0.0098227 | 0.0098236 | 0.0098236 | 0.97158 | -0.20079 | 0.97108 | -0.20443 | 1.8192
118 | 0.0029475 | 0.00073682 | -0.0029472 | -0.00073695 | 2.3148e-07 | -1.3667e-07 | 0.0045125 | 0.0045125 | 0.0045125 | 0.97181 | -0.19917 | 0.97173 | -0.19974 | 1.6713
119 | -0.026343 | -0.0065895 | 0.026354 | 0.0065927 | 1.1419e-05 | 3.1296e-06 | 0.040272 | 0.040272 | 0.040272 | 0.97322 | -0.18892 | 0.97366 | -0.18578 | 4.9719
120 | 0.004948 | 0.0012394 | -0.0049469 | -0.0012393 | 1.0801e-06 | 4.2971e-08 | 0.0075816 | 0.0075818 | 0.0075818 | 0.97108 | -0.20443 | 0.97086 | -0.206 | 2.8081
121 | -0.03138 | -0.0078523 | 0.031403 | 0.0078592 | 2.2665e-05 | 6.948e-06 | 0.047953 | 0.047952 | 0.047953 | 0.97366 | -0.18578 | 0.97438 | -0.18055 | 5.9201
122 | 0.0018256 | 0.00045706 | -0.0018254 | -0.0004575 | 2.0543e-07 | -4.4092e-07 | 0.0027979 | 0.0027981 | 0.0027981 | 0.97086 | -0.206 | 0.97075 | -0.20682 | 1.0363
123 | -0.031403 | -0.0078592 | 0.03141 | 0.0078614 | 6.9456e-06 | 2.1286e-06 | 0.047952 | 0.047952 | 0.047952 | 0.97438 | -0.18055 | 0.97461 | -0.17895 | 5.92
124 | -0.0024682 | -0.00061622 | 0.0024683 | 0.00061609 | 1.2433e-07 | -1.305e-07 | 0.0037496 | 0.0037495 | 0.0037496 | 0.97928 | -0.14541 | 0.97934 | -0.14505 | 1.3887
125 | 0.0023923 | 0.0005972 | -0.002392 | -0.00059759 | 3.4257e-07 | -3.9108e-07 | 0.0036343 | 0.0036345 | 0.0036345 | 0.97928 | -0.14541 | 0.97914 | -0.14645 | 1.3461
126 | -0.0025468 | -0.00063576 | 0.002547 | 0.00063565 | 1.1244e-07 | -1.0825e-07 | 0.0038688 | 0.0038687 | 0.0038688 | 0.97934 | -0.14505 | 0.97938 | -0.14472 | 1.4329
127 | 0.0012372 | 0.00030916 | -0.0012372 | -0.00030932 | 2.9296e-08 | -1.5582e-07 | 0.0018799 | 0.0018799 | 0.0018799 | 0.97914 | -0.14645 | 0.97912 | -0.14663 | 0.69627
128 | 0.0011548 | 0.00028843 | -0.0011547 | -0.00028934 | 1.4816e-07 | -9.1268e-07 | 0.0017546 | 0.001755 | 0.001755 | 0.97914 | -0.14645 | 0.97901 | -0.14738 | 0.64999
129 | 0.00092778 | 0.00023178 | -0.00092776 | -0.00023195 | 1.8096e-08 | -1.7656e-07 | 0.0014097 | 0.0014098 | 0.0014098 | 0.97912 | -0.14663 | 0.9791 | -0.14677 | 0.52214
130 | 0.00030057 | 7.5287e-05 | -0.00030057 | -7.533e-05 | 4.4499e-10 | -4.2797e-08 | 0.00045683 | 0.00045684 | 0.00045684 | 0.97901 | -0.14738 | 0.97901 | -0.14739 | 0.1692
131 | 0.00024904 | 6.2181e-05 | -0.00024904 | -6.2414e-05 | 1.6602e-09 | -2.33e-07 | 0.0003784 | 0.00037848 | 0.00037848 | 0.9791 | -0.14677 | 0.97909 | -0.14682 | 0.14018
132 | 0.039142 | 0.0098016 | -0.039126 | -0.0097964 | 1.5463e-05 | 5.1665e-06 | 0.059707 | 0.059707 | 0.059707 | 0.97544 | -0.17293 | 0.97505 | -0.17579 | 7.3713
133 | 0.037581 | 0.0094092 | -0.037573 | -0.0094064 | 8.6736e-06 | 2.8617e-06 | 0.05735 | 0.05735 | 0.05735 | 0.97505 | -0.17579 | 0.97481 | -0.17746 | 7.0802
134 | 0.035937 | 0.0089965 | -0.03593 | -0.0089941 | 7.3896e-06 | 2.4007e-06 | 0.054853 | 0.054854 | 0.054854 | 0.97481 | -0.17746 | 0.97461 | -0.17895 | 6.772
135 | 0.0045202 | 0.0011328 | -0.0045199 | -0.0011328 | 3.6862e-07 | -1.2765e-08 | 0.0069014 | 0.0069015 | 0.0069015 | 0.97461 | -0.17895 | 0.97452 | -0.17954 | 2.5561
136 | 0.053451 | 0.01341 | -0.053437 | -0.013405 | 1.4164e-05 | 5.0551e-06 | 0.081065 | 0.081065 | 0.081065 | 0.98121 | -0.13165 | 0.98094 | -0.13356 | 10.008
137 | 0.00075717 | 0.00018932 | -0.00075715 | -0.00018954 | 1.518e-08 | -2.1816e-07 | 0.0011596 | 0.0011597 | 0.0011597 | 0.9715 | -0.20141 | 0.97148 | -0.20156 | 0.4295
138 | -0.00019883 | -4.9832e-05 | 0.00019883 | 4.9661e-05 | 7.7592e-10 | -1.7113e-07 | 0.00030212 | 0.00030206 | 0.00030212 | 0.97928 | -0.14545 | 0.97928 | -0.14542 | 0.1119
139 | 0.053437 | 0.013405 | -0.053393 | -0.013389 | 4.4525e-05 | 1.5892e-05 | 0.081065 | 0.081065 | 0.081065 | 0.98094 | -0.13356 | 0.9801 | -0.13958 | 10.008
140 | 0.0015835 | 0.00039679 | -0.0015835 | -0.00039686 | 2.3046e-08 | -7.1391e-08 | 0.0024062 | 0.0024062 | 0.0024062 | 0.97928 | -0.14546 | 0.97926 | -0.14557 | 0.89118
141 | -0.00043552 | -0.00010915 | 0.00043552 | 0.00010893 | 4.9155e-09 | -2.173e-07 | 0.0006671 | 0.00066702 | 0.0006671 | 0.97146 | -0.20164 | 0.97148 | -0.20156 | 0.24707

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21062 | 0.052926

## res_load
| p_mw | q_mvar
0 | 0.00013891 | 3.4814e-05
1 | 0.0019179 | 0.00048066
2 | 0.0007391 | 0.00018524
3 | 0.00013741 | 3.4438e-05
4 | 0.00044123 | 0.00011058
5 | 0.0011453 | 0.00028703
6 | 0.00038023 | 9.5294e-05
7 | 0.00028497 | 7.142e-05
8 | 0.0012354 | 0.00030961
9 | 0.004096 | 0.0010266
10 | 0.0045589 | 0.0011426
11 | 0.0010358 | 0.0002596
12 | 0.0010752 | 0.00026946
13 | 0.0010364 | 0.00025975
14 | 0.00084476 | 0.00021172
15 | 0.00084975 | 0.00021297
16 | 0.0018307 | 0.00045882
17 | 0.0041788 | 0.0010473
18 | 0.0014328 | 0.00035909
19 | 0.0020602 | 0.00051634
20 | 0.00095375 | 0.00023903
21 | 0.0010138 | 0.00025409
22 | 0.00068096 | 0.00017067
23 | 0.0020486 | 0.00051342
24 | 0.0016055 | 0.00040238
25 | 0.00036025 | 9.0288e-05
26 | 0.0073235 | 0.0018354
27 | 0.0088913 | 0.0022284
28 | 0.0044609 | 0.001118
29 | 0.0011731 | 0.00029401
30 | 0.00018118 | 4.5408e-05
31 | 0.0012005 | 0.00030086
32 | 0.0048344 | 0.0012116
33 | 0.0028542 | 0.00071532
34 | 0.008743 | 0.0021912
35 | 0.0045783 | 0.0011474
36 | 0.0031753 | 0.00079581
37 | 0.0028283 | 0.00070884
38 | 0.0035268 | 0.0008839
39 | 0.003002 | 0.00075236
40 | 0.0025833 | 0.00064743
41 | 0.0037806 | 0.0009475
42 | 0.0019972 | 0.00050055
43 | 0.0038139 | 0.00095586
44 | 0.00083087 | 0.00020824
45 | 0.0020269 | 0.00050799
46 | 0.00051642 | 0.00012943
47 | 0.0042946 | 0.0010763
48 | 0.0023503 | 0.00058903
49 | 0.0037472 | 0.00093915
50 | 0.0019125 | 0.00047931
51 | 0.0018115 | 0.000454
52 | 0.0030941 | 0.00077545
53 | 0.0016369 | 0.00041025
54 | 0.0032126 | 0.00080515
55 | 0.0016316 | 0.00040892
56 | 0.00070983 | 0.0001779
57 | 0.0011596 | 0.00029063
58 | 0.0022136 | 0.00055478
59 | 0.00040906 | 0.00010252
60 | 0.00062291 | 0.00015612
61 | 0.00045847 | 0.0001149
62 | 7.4038e-05 | 1.8556e-05
63 | 0.00057812 | 0.00014489
64 | 0.0010893 | 0.000273
65 | 0.00064577 | 0.00016184
66 | 0.0010021 | 0.00025115
67 | 0.00037997 | 9.523e-05
68 | 0.00040336 | 0.00010109
69 | 0.00044826 | 0.00011234
70 | 0.0030765 | 0.00077104
71 | 0.00088829 | 0.00022263
72 | 0.00083453 | 0.00020915
73 | 0.00030203 | 7.5695e-05
74 | 0.006298 | 0.0015784
75 | 0.0002723 | 6.8245e-05
76 | 0.00021782 | 5.4591e-05
77 | 0.0004423 | 0.00011085
78 | 0.001706 | 0.00042757
79 | 0.00021847 | 5.4753e-05
80 | 0.0018796 | 0.00047106
81 | 0.0002125 | 5.3257e-05
82 | 0.00038328 | 9.606e-05
83 | 0.0014617 | 0.00036633
84 | 0.00051502 | 0.00012908
85 | 0.00016369 | 4.1024e-05
86 | 0.0059536 | 0.0014921
87 | 0.0018302 | 0.00045869
88 | 0.0035244 | 0.00088331
89 | 0.0056436 | 0.0014144
90 | 0.0014631 | 0.00036669
91 | 0.0050259 | 0.0012596
92 | 0.0031212 | 0.00078226
93 | 0.0018254 | 0.0004575
94 | 7.5878e-05 | 1.9017e-05
95 | 7.8499e-05 | 1.9674e-05
96 | 0.0006078 | 0.00015233
97 | 0.00030939 | 7.7541e-05
98 | 0.00085408 | 0.00021405
99 | 0.00030057 | 7.533e-05
100 | 0.00024904 | 6.2414e-05
101 | 0.0017263 | 0.00043265
102 | 0.0015449 | 0.0003872
103 | 0.0016353 | 0.00040985
104 | 0.0045199 | 0.0011328
105 | 0.00034111 | 8.549e-05
106 | 0.00097922 | 0.00024541
107 | 0.00035876 | 8.9914e-05
108 | 0.00019883 | 4.9832e-05
109 | 0.00046628 | 0.00011686
110 | 0.00020153 | 5.0509e-05
111 | 0.00018342 | 4.597e-05
112 | 0.0015835 | 0.00039686
113 | 0.00043552 | 0.00010915
114 | 0.00032163 | 8.0607e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1