## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1030-14_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1030-14_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1030-14_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1030-14_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1030-14_0_4_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_1030-14_0_4_node_114 | 0.4 | n |  | TRUE
6 | bus_LV_1030-14_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1030-14_0_4_node_115 | 0.4 | n |  | TRUE
8 | bus_LV_1030-14_0_4_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_1030-14_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1030-14_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1030-14_0_4_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_1030-14_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1030-14_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1030-14_0_4_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_1030-14_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1030-14_0_4_node_68 | 0.4 | n |  | TRUE
17 | bus_LV_1030-14_0_4_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_1030-14_0_4_node_65 | 0.4 | n |  | TRUE
19 | bus_LV_1030-14_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1030-14_0_4_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_1030-14_0_4_node_70 | 0.4 | n |  | TRUE
22 | bus_LV_1030-14_0_4_node_69 | 0.4 | n |  | TRUE
23 | bus_LV_1030-14_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1030-14_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1030-14_0_4_node_73 | 0.4 | n |  | TRUE
26 | bus_LV_1030-14_0_4_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1030-14_0_4_node_67 | 0.4 | n |  | TRUE
28 | bus_LV_1030-14_0_4_node_86 | 0.4 | n |  | TRUE
29 | bus_LV_1030-14_0_4_node_104 | 0.4 | n |  | TRUE
30 | bus_LV_1030-14_0_4_node_101 | 0.4 | n |  | TRUE
31 | bus_LV_1030-14_0_4_node_66 | 0.4 | n |  | TRUE
32 | bus_LV_1030-14_0_4_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_1030-14_0_4_node_100 | 0.4 | n |  | TRUE
34 | bus_LV_1030-14_0_4_node_61 | 0.4 | n |  | TRUE
35 | bus_LV_1030-14_0_4_node_60 | 0.4 | n |  | TRUE
36 | bus_LV_1030-14_0_4_node_72 | 0.4 | n |  | TRUE
37 | bus_LV_1030-14_0_4_node_84 | 0.4 | n |  | TRUE
38 | bus_LV_1030-14_0_4_node_89 | 0.4 | n |  | TRUE
39 | bus_LV_1030-14_0_4_node_81 | 0.4 | n |  | TRUE
40 | bus_LV_1030-14_0_4_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_1030-14_0_4_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_1030-14_0_4_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_1030-14_0_4_node_45 | 0.4 | n |  | TRUE
44 | bus_LV_1030-14_0_4_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_1030-14_0_4_node_24 | 0.4 | n |  | TRUE
46 | bus_LV_1030-14_0_4_node_25 | 0.4 | n |  | TRUE
47 | bus_LV_1030-14_0_4_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_1030-14_0_4_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_1030-14_0_4_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_1030-14_0_4_node_50 | 0.4 | n |  | TRUE
51 | bus_LV_1030-14_0_4_node_53 | 0.4 | n |  | TRUE
52 | bus_LV_1030-14_0_4_node_51 | 0.4 | n |  | TRUE
53 | bus_LV_1030-14_0_4_node_54 | 0.4 | n |  | TRUE
54 | bus_LV_1030-14_0_4_node_29 | 0.4 | n |  | TRUE
55 | bus_LV_1030-14_0_4_node_30 | 0.4 | n |  | TRUE
56 | bus_LV_1030-14_0_4_node_31 | 0.4 | n |  | TRUE
57 | bus_LV_1030-14_0_4_node_33 | 0.4 | n |  | TRUE
58 | bus_LV_1030-14_0_4_node_32 | 0.4 | n |  | TRUE
59 | bus_LV_1030-14_0_4_node_36 | 0.4 | n |  | TRUE
60 | bus_LV_1030-14_0_4_node_110 | 0.4 | n |  | TRUE
61 | bus_LV_1030-14_0_4_node_48 | 0.4 | n |  | TRUE
62 | bus_LV_1030-14_0_4_node_34 | 0.4 | n |  | TRUE
63 | bus_LV_1030-14_0_4_node_111 | 0.4 | n |  | TRUE
64 | bus_LV_1030-14_0_4_node_109 | 0.4 | n |  | TRUE
65 | bus_LV_1030-14_0_4_node_46 | 0.4 | n |  | TRUE
66 | bus_LV_1030-14_0_4_node_62 | 0.4 | n |  | TRUE
67 | bus_LV_1030-14_0_4_node_63 | 0.4 | n |  | TRUE
68 | bus_LV_1030-14_0_4_node_35 | 0.4 | n |  | TRUE
69 | bus_LV_1030-14_0_4_node_37 | 0.4 | n |  | TRUE
70 | bus_LV_1030-14_0_4_node_38 | 0.4 | n |  | TRUE
71 | bus_LV_1030-14_0_4_node_39 | 0.4 | n |  | TRUE
72 | bus_LV_1030-14_0_4_node_40 | 0.4 | n |  | TRUE
73 | bus_LV_1030-14_0_4_node_42 | 0.4 | n |  | TRUE
74 | bus_LV_1030-14_0_4_node_116 | 0.4 | n |  | TRUE
75 | bus_LV_1030-14_0_4_node_44 | 0.4 | n |  | TRUE
76 | bus_LV_1030-14_0_4_node_117 | 0.4 | n |  | TRUE
77 | bus_LV_1030-14_0_4_node_118 | 0.4 | n |  | TRUE
78 | bus_LV_1030-14_0_4_node_47 | 0.4 | n |  | TRUE
79 | bus_LV_1030-14_0_4_node_49 | 0.4 | n |  | TRUE
80 | bus_LV_1030-14_0_4_node_52 | 0.4 | n |  | TRUE
81 | bus_LV_1030-14_0_4_node_55 | 0.4 | n |  | TRUE
82 | bus_LV_1030-14_0_4_node_56 | 0.4 | n |  | TRUE
83 | bus_LV_1030-14_0_4_node_57 | 0.4 | n |  | TRUE
84 | bus_LV_1030-14_0_4_node_58 | 0.4 | n |  | TRUE
85 | bus_LV_1030-14_0_4_node_59 | 0.4 | n |  | TRUE
86 | bus_LV_1030-14_0_4_node_120 | 0.4 | n |  | TRUE
87 | bus_LV_1030-14_0_4_node_74 | 0.4 | n |  | TRUE
88 | bus_LV_1030-14_0_4_node_71 | 0.4 | n |  | TRUE
89 | bus_LV_1030-14_0_4_node_64 | 0.4 | n |  | TRUE
90 | bus_LV_1030-14_0_4_node_75 | 0.4 | n |  | TRUE
91 | bus_LV_1030-14_0_4_node_77 | 0.4 | n |  | TRUE
92 | bus_LV_1030-14_0_4_node_76 | 0.4 | n |  | TRUE
93 | bus_LV_1030-14_0_4_node_102 | 0.4 | n |  | TRUE
94 | bus_LV_1030-14_0_4_node_82 | 0.4 | n |  | TRUE
95 | bus_LV_1030-14_0_4_node_88 | 0.4 | n |  | TRUE
96 | bus_LV_1030-14_0_4_node_91 | 0.4 | n |  | TRUE
97 | bus_LV_1030-14_0_4_node_90 | 0.4 | n |  | TRUE
98 | bus_LV_1030-14_0_4_node_96 | 0.4 | n |  | TRUE
99 | bus_LV_1030-14_0_4_node_78 | 0.4 | n |  | TRUE
100 | bus_LV_1030-14_0_4_node_79 | 0.4 | n |  | TRUE
101 | bus_LV_1030-14_0_4_node_80 | 0.4 | n |  | TRUE
102 | bus_LV_1030-14_0_4_node_97 | 0.4 | n |  | TRUE
103 | bus_LV_1030-14_0_4_node_99 | 0.4 | n |  | TRUE
104 | bus_LV_1030-14_0_4_node_95 | 0.4 | n |  | TRUE
105 | bus_LV_1030-14_0_4_node_85 | 0.4 | n |  | TRUE
106 | bus_LV_1030-14_0_4_node_87 | 0.4 | n |  | TRUE
107 | bus_LV_1030-14_0_4_node_98 | 0.4 | n |  | TRUE
108 | bus_LV_1030-14_0_4_node_94 | 0.4 | n |  | TRUE
109 | bus_LV_1030-14_0_4_node_93 | 0.4 | n |  | TRUE
110 | bus_LV_1030-14_0_4_node_107 | 0.4 | n |  | TRUE
111 | bus_LV_1030-14_0_4_node_105 | 0.4 | n |  | TRUE
112 | bus_LV_1030-14_0_4_node_103 | 0.4 | n |  | TRUE
113 | bus_LV_1030-14_0_4_node_112 | 0.4 | n |  | TRUE
114 | bus_LV_1030-14_0_4_node_106 | 0.4 | n |  | TRUE
115 | bus_LV_1030-14_0_4_node_119 | 0.4 | n |  | TRUE
116 | bus_LV_1030-14_0_4_node_121 | 0.4 | n |  | TRUE
117 | bus_MV_470_1_node_39 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1030-14_0_4_load_0 | 0 | 0.00083468 | 0.00020919 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1030-14_0_4_load_1 | 1 | 0.0010587 | 0.00026534 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1030-14_0_4_load_8 | 4 | 0.0094954 | 0.0023798 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1030-14_0_4_load_114 | 5 | 0.0019448 | 0.00048741 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1030-14_0_4_load_115 | 7 | 0.0031955 | 0.00080086 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1030-14_0_4_load_4 | 8 | 0.012593 | 0.0031561 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1030-14_0_4_load_5 | 9 | 0.0044988 | 0.0011275 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1030-14_0_4_load_7 | 10 | 0.011807 | 0.0029591 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1030-14_0_4_load_68 | 16 | 0.0022725 | 0.00056954 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1030-14_0_4_load_21 | 17 | 0.0049891 | 0.0012504 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1030-14_0_4_load_65 | 18 | 0.0015777 | 0.00039541 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1030-14_0_4_load_70 | 21 | 0.0022226 | 0.00055704 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1030-14_0_4_load_69 | 22 | 0.0037337 | 0.00093575 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1030-14_0_4_load_73 | 25 | 0.0013371 | 0.0003351 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1030-14_0_4_load_86 | 28 | 0.0010289 | 0.00025786 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1030-14_0_4_load_104 | 29 | 0.00085758 | 0.00021493 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1030-14_0_4_load_101 | 30 | 0.0011101 | 0.00027823 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1030-14_0_4_load_66 | 31 | 0.0043392 | 0.0010875 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1030-14_0_4_load_20 | 32 | 0.0055244 | 0.0013845 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1030-14_0_4_load_100 | 33 | 0.0019963 | 0.00050031 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1030-14_0_4_load_61 | 34 | 0.0016166 | 0.00040516 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1030-14_0_4_load_60 | 35 | 0.0014509 | 0.00036363 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1030-14_0_4_load_72 | 36 | 0.0019833 | 0.00049705 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1030-14_0_4_load_84 | 37 | 0.00097439 | 0.0002442 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1030-14_0_4_load_89 | 38 | 0.0021824 | 0.00054697 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1030-14_0_4_load_81 | 39 | 0.00058802 | 0.00014737 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1030-14_0_4_load_23 | 41 | 0.00055875 | 0.00014004 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1030-14_0_4_load_45 | 43 | 0.00055875 | 0.00014004 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1030-14_0_4_load_24 | 45 | 0.0016093 | 0.00040332 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1030-14_0_4_load_25 | 46 | 0.0016063 | 0.00040258 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1030-14_0_4_load_26 | 47 | 0.0015606 | 0.00039112 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1030-14_0_4_load_27 | 48 | 0.0016072 | 0.00040281 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1030-14_0_4_load_28 | 49 | 0.0042695 | 0.00107 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1030-14_0_4_load_50 | 50 | 0.0015922 | 0.00039904 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1030-14_0_4_load_53 | 51 | 0.00050315 | 0.0001261 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1030-14_0_4_load_51 | 52 | 0.0015925 | 0.00039913 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1030-14_0_4_load_54 | 53 | 0.00050371 | 0.00012624 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1030-14_0_4_load_29 | 54 | 0.0017052 | 0.00042736 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1030-14_0_4_load_30 | 55 | 0.006373 | 0.0015972 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1030-14_0_4_load_31 | 56 | 0.0017022 | 0.0004266 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1030-14_0_4_load_36 | 59 | 0.001711 | 0.00042881 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1030-14_0_4_load_48 | 61 | 0.002108 | 0.00052831 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1030-14_0_4_load_34 | 62 | 0.0017081 | 0.00042809 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1030-14_0_4_load_109 | 64 | 0.0053866 | 0.00135 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1030-14_0_4_load_46 | 65 | 0.0020612 | 0.00051658 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1030-14_0_4_load_35 | 68 | 0.0057605 | 0.0014437 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1030-14_0_4_load_37 | 69 | 0.00054807 | 0.00013736 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1030-14_0_4_load_38 | 70 | 0.00054773 | 0.00013727 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1030-14_0_4_load_39 | 71 | 0.00050371 | 0.00012624 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1030-14_0_4_load_40 | 72 | 0.0014335 | 0.00035926 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1030-14_0_4_load_42 | 73 | 0.0009861 | 0.00024714 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1030-14_0_4_load_117 | 76 | 0.0030769 | 0.00077115 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1030-14_0_4_load_118 | 77 | 0.0016355 | 0.00040989 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1030-14_0_4_load_47 | 78 | 0.0016168 | 0.0004052 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1030-14_0_4_load_49 | 79 | 0.0015738 | 0.00039442 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1030-14_0_4_load_52 | 80 | 0.0015764 | 0.00039508 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1030-14_0_4_load_55 | 81 | 0.0017179 | 0.00043054 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1030-14_0_4_load_57 | 83 | 0.0015003 | 0.00037601 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1030-14_0_4_load_58 | 84 | 0.0024196 | 0.00060642 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1030-14_0_4_load_59 | 85 | 0.0017996 | 0.00045103 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1030-14_0_4_load_120 | 86 | 0.0016583 | 0.0004156 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1030-14_0_4_load_74 | 87 | 0.0015339 | 0.00038443 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1030-14_0_4_load_71 | 88 | 0.0029903 | 0.00074944 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1030-14_0_4_load_64 | 89 | 0.0033867 | 0.00084879 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1030-14_0_4_load_102 | 93 | 0.00401 | 0.001005 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1030-14_0_4_load_88 | 95 | 0.0015352 | 0.00038476 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1030-14_0_4_load_91 | 96 | 0.00089175 | 0.00022349 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1030-14_0_4_load_90 | 97 | 0.0046209 | 0.0011581 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1030-14_0_4_load_96 | 98 | 0.0029323 | 0.00073491 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1030-14_0_4_load_78 | 99 | 0.00052808 | 0.00013235 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1030-14_0_4_load_79 | 100 | 0.0010888 | 0.00027288 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1030-14_0_4_load_99 | 103 | 0.001938 | 0.00048572 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1030-14_0_4_load_95 | 104 | 0.002622 | 0.00065715 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1030-14_0_4_load_85 | 105 | 0.00091318 | 0.00022886 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1030-14_0_4_load_87 | 106 | 0.0011808 | 0.00029594 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1030-14_0_4_load_98 | 107 | 0.0039053 | 0.00097875 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1030-14_0_4_load_94 | 108 | 0.0016001 | 0.00040103 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1030-14_0_4_load_107 | 110 | 0.0029188 | 0.00073152 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1030-14_0_4_load_105 | 111 | 0.0033685 | 0.00084421 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1030-14_0_4_load_103 | 112 | 0.0051443 | 0.0012893 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1030-14_0_4_load_112 | 113 | 0.0018139 | 0.0004546 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1030-14_0_4_load_106 | 114 | 0.0035608 | 0.00089243 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1030-14_0_4_load_121 | 116 | 0.0018063 | 0.0004527 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 80 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1030-14_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.017647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1030-14_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.025228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1030-14_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.016596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1030-14_0_4_line_3 | NAYY 4x150 SE | 3 | 4 | 0.024034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1030-14_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.009605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1030-14_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.01788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1030-14_0_4_line_6 | NAYY 4x150 SE | 5 | 7 | 0.013697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1030-14_0_4_line_7 | NAYY 4x150 SE | 6 | 11 | 0.019525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_1030-14_0_4_line_8 | NAYY 4x150 SE | 6 | 8 | 0.019399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_1030-14_0_4_line_9 | NAYY 4x150 SE | 8 | 9 | 0.03466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_1030-14_0_4_line_10 | NAYY 4x150 SE | 9 | 10 | 0.042871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_1030-14_0_4_line_11 | NAYY 4x150 SE | 10 | 12 | 0.0025158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_1030-14_0_4_line_12 | NAYY 4x150 SE | 11 | 17 | 0.021884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_1030-14_0_4_line_13 | NAYY 4x150 SE | 11 | 18 | 0.039141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1030-14_0_4_line_14 | NAYY 4x150 SE | 11 | 15 | 0.004724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1030-14_0_4_line_15 | NAYY 4x150 SE | 12 | 13 | 0.021683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_1030-14_0_4_line_16 | NAYY 4x150 SE | 13 | 14 | 0.0208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_1030-14_0_4_line_17 | NAYY 4x150 SE | 14 | 23 | 0.01017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1030-14_0_4_line_18 | NAYY 4x150 SE | 15 | 16 | 0.031754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1030-14_0_4_line_19 | NAYY 4x150 SE | 17 | 32 | 0.0093287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_1030-14_0_4_line_20 | NAYY 4x150 SE | 18 | 31 | 0.0025477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1030-14_0_4_line_21 | NAYY 4x150 SE | 19 | 20 | 0.006689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1030-14_0_4_line_22 | NAYY 4x150 SE | 19 | 21 | 0.037834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1030-14_0_4_line_23 | NAYY 4x150 SE | 19 | 22 | 0.0070206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1030-14_0_4_line_24 | NAYY 4x150 SE | 20 | 26 | 0.043479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1030-14_0_4_line_25 | NAYY 4x150 SE | 21 | 33 | 0.022439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1030-14_0_4_line_26 | NAYY 4x150 SE | 22 | 23 | 0.023225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1030-14_0_4_line_27 | NAYY 4x150 SE | 23 | 24 | 0.014816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1030-14_0_4_line_28 | NAYY 4x150 SE | 24 | 25 | 0.02881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1030-14_0_4_line_29 | NAYY 4x150 SE | 25 | 36 | 0.012436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1030-14_0_4_line_30 | NAYY 4x150 SE | 26 | 27 | 0.1702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1030-14_0_4_line_31 | NAYY 4x150 SE | 26 | 28 | 0.022566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1030-14_0_4_line_32 | NAYY 4x150 SE | 27 | 29 | 0.079936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1030-14_0_4_line_33 | NAYY 4x150 SE | 27 | 30 | 0.012584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1030-14_0_4_line_34 | NAYY 4x150 SE | 28 | 37 | 0.023356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1030-14_0_4_line_35 | NAYY 4x150 SE | 30 | 93 | 0.034258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1030-14_0_4_line_36 | NAYY 4x150 SE | 32 | 40 | 0.014071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_1030-14_0_4_line_37 | NAYY 4x150 SE | 33 | 94 | 0.050146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1030-14_0_4_line_38 | NAYY 4x150 SE | 34 | 35 | 0.031976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1030-14_0_4_line_39 | NAYY 4x150 SE | 35 | 66 | 0.018162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1030-14_0_4_line_40 | NAYY 4x150 SE | 36 | 88 | 0.015563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1030-14_0_4_line_41 | NAYY 4x150 SE | 37 | 105 | 0.050148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1030-14_0_4_line_42 | NAYY 4x150 SE | 38 | 39 | 0.036018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1030-14_0_4_line_43 | NAYY 4x150 SE | 39 | 101 | 0.018701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1030-14_0_4_line_44 | NAYY 4x150 SE | 40 | 41 | 0.014184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_1030-14_0_4_line_45 | NAYY 4x150 SE | 41 | 42 | 0.020104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_1030-14_0_4_line_46 | NAYY 4x150 SE | 42 | 43 | 0.020524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_1030-14_0_4_line_47 | NAYY 4x150 SE | 42 | 44 | 0.004567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1030-14_0_4_line_48 | NAYY 4x150 SE | 43 | 53 | 0.0030375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_1030-14_0_4_line_49 | NAYY 4x150 SE | 44 | 71 | 0.024128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1030-14_0_4_line_50 | NAYY 4x150 SE | 45 | 46 | 0.0056496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_1030-14_0_4_line_51 | NAYY 4x150 SE | 45 | 47 | 0.0056801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_1030-14_0_4_line_52 | NAYY 4x150 SE | 46 | 48 | 0.0056452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
53 | LV_1030-14_0_4_line_53 | NAYY 4x150 SE | 47 | 49 | 0.0086018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
54 | LV_1030-14_0_4_line_54 | NAYY 4x150 SE | 48 | 50 | 0.009603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_1030-14_0_4_line_55 | NAYY 4x150 SE | 49 | 51 | 0.009612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
56 | LV_1030-14_0_4_line_56 | NAYY 4x150 SE | 50 | 52 | 0.0072177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
57 | LV_1030-14_0_4_line_57 | NAYY 4x150 SE | 51 | 53 | 0.004372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
58 | LV_1030-14_0_4_line_58 | NAYY 4x150 SE | 52 | 80 | 0.019063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
59 | LV_1030-14_0_4_line_59 | NAYY 4x150 SE | 54 | 55 | 0.003167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1030-14_0_4_line_60 | NAYY 4x150 SE | 54 | 56 | 0.0041901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1030-14_0_4_line_61 | NAYY 4x150 SE | 56 | 57 | 0.031024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1030-14_0_4_line_62 | NAYY 4x150 SE | 57 | 61 | 0.014152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1030-14_0_4_line_63 | NAYY 4x150 SE | 58 | 59 | 0.012122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1030-14_0_4_line_64 | NAYY 4x150 SE | 58 | 60 | 0.022388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1030-14_0_4_line_65 | NAYY 4x150 SE | 59 | 62 | 0.0063247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1030-14_0_4_line_66 | NAYY 4x150 SE | 60 | 63 | 0.028837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1030-14_0_4_line_67 | NAYY 4x150 SE | 60 | 64 | 0.028208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1030-14_0_4_line_68 | NAYY 4x150 SE | 61 | 65 | 0.0002741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1030-14_0_4_line_69 | NAYY 4x150 SE | 62 | 68 | 0.010793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1030-14_0_4_line_70 | NAYY 4x150 SE | 63 | 74 | 0.023296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1030-14_0_4_line_71 | NAYY 4x150 SE | 63 | 84 | 0.020545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1030-14_0_4_line_72 | NAYY 4x150 SE | 64 | 109 | 0.020309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1030-14_0_4_line_73 | NAYY 4x150 SE | 65 | 78 | 0.012624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1030-14_0_4_line_74 | NAYY 4x150 SE | 66 | 67 | 0.004013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1030-14_0_4_line_75 | NAYY 4x150 SE | 67 | 87 | 0.0044646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1030-14_0_4_line_76 | NAYY 4x150 SE | 67 | 88 | 0.020512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1030-14_0_4_line_77 | NAYY 4x150 SE | 68 | 69 | 0.0082442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1030-14_0_4_line_78 | NAYY 4x150 SE | 69 | 70 | 0.0065987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1030-14_0_4_line_79 | NAYY 4x150 SE | 71 | 72 | 0.015543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1030-14_0_4_line_80 | NAYY 4x150 SE | 72 | 73 | 0.018983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1030-14_0_4_line_81 | NAYY 4x150 SE | 73 | 74 | 0.01868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1030-14_0_4_line_82 | NAYY 4x150 SE | 74 | 75 | 0.019639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1030-14_0_4_line_83 | NAYY 4x150 SE | 75 | 76 | 0.02248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1030-14_0_4_line_84 | NAYY 4x150 SE | 76 | 77 | 0.031329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1030-14_0_4_line_85 | NAYY 4x150 SE | 77 | 115 | 0.0085048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1030-14_0_4_line_86 | NAYY 4x150 SE | 78 | 79 | 0.015171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1030-14_0_4_line_87 | NAYY 4x150 SE | 79 | 80 | 0.007137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1030-14_0_4_line_88 | NAYY 4x150 SE | 81 | 82 | 0.015083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1030-14_0_4_line_89 | NAYY 4x150 SE | 81 | 83 | 0.025374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1030-14_0_4_line_90 | NAYY 4x150 SE | 82 | 84 | 0.010205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1030-14_0_4_line_91 | NAYY 4x150 SE | 82 | 85 | 0.0082944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1030-14_0_4_line_92 | NAYY 4x150 SE | 85 | 86 | 0.0081043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1030-14_0_4_line_93 | NAYY 4x150 SE | 87 | 91 | 0.012786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1030-14_0_4_line_94 | NAYY 4x150 SE | 89 | 90 | 0.0012087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1030-14_0_4_line_95 | NAYY 4x150 SE | 90 | 92 | 0.012781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1030-14_0_4_line_96 | NAYY 4x150 SE | 90 | 91 | 0.010506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1030-14_0_4_line_97 | NAYY 4x150 SE | 91 | 95 | 0.027819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1030-14_0_4_line_98 | NAYY 4x150 SE | 92 | 96 | 0.022811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1030-14_0_4_line_99 | NAYY 4x150 SE | 93 | 112 | 0.013721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1030-14_0_4_line_100 | NAYY 4x150 SE | 94 | 101 | 0.023134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1030-14_0_4_line_101 | NAYY 4x150 SE | 95 | 98 | 0.013831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1030-14_0_4_line_102 | NAYY 4x150 SE | 96 | 97 | 0.02077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1030-14_0_4_line_103 | NAYY 4x150 SE | 98 | 108 | 0.00082258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1030-14_0_4_line_104 | NAYY 4x150 SE | 99 | 100 | 0.011639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1030-14_0_4_line_105 | NAYY 4x150 SE | 99 | 101 | 0.038639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1030-14_0_4_line_106 | NAYY 4x150 SE | 102 | 103 | 0.0016812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1030-14_0_4_line_107 | NAYY 4x150 SE | 102 | 104 | 0.03144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1030-14_0_4_line_108 | NAYY 4x150 SE | 104 | 108 | 0.022832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1030-14_0_4_line_109 | NAYY 4x150 SE | 105 | 106 | 0.03055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1030-14_0_4_line_110 | NAYY 4x150 SE | 106 | 107 | 0.033952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1030-14_0_4_line_111 | NAYY 4x150 SE | 109 | 110 | 0.014274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1030-14_0_4_line_112 | NAYY 4x150 SE | 110 | 111 | 0.03603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1030-14_0_4_line_113 | NAYY 4x150 SE | 111 | 114 | 0.0103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1030-14_0_4_line_114 | NAYY 4x150 SE | 112 | 113 | 0.026507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1030-14_0_4_line_115 | NAYY 4x150 SE | 115 | 116 | 0.013544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1030-14_0_4_trafo_52 | 0.25 MVA 20/0.4 kV | 117 | 80 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2662567.5894 | 1229465.0488 | 2662582.7467 | 1229474.0864
1 | 2662604.4154 | 1229487.0064 | 2662582.7467 | 1229474.0864
2 | 2662615.918 | 1229499.0019 | 2662610.1254 | 1229492.9704 | 2662608.6641 | 1229491.454 | 2662607.8698 | 1229490.6229 | 2662604.4154 | 1229487.0064
3 | 2662615.918 | 1229499.0019 | 2662631.9832 | 1229516.8775
4 | 2662615.918 | 1229499.0019 | 2662608.8484 | 1229505.504
5 | 2662645.1843 | 1229528.3957 | 2662642.1641 | 1229527.4299 | 2662640.1792 | 1229525.997 | 2662631.9832 | 1229516.8775
6 | 2662598.7669 | 1229514.7761 | 2662608.8484 | 1229505.504
7 | 2662645.1843 | 1229528.3957 | 2662650.0393 | 1229529.9367 | 2662653.2705 | 1229530.2821 | 2662660.1088 | 1229527.6524 | 2662663.4677 | 1229529.5445
8 | 2662645.1843 | 1229528.3957 | 2662641.7184 | 1229536.6646 | 2662637.9694 | 1229546.4008
9 | 2662637.9694 | 1229546.4008 | 2662628.9525 | 1229569.8184 | 2662626.4229 | 1229577.6635 | 2662626.1389 | 1229578.9558
10 | 2662613.7653 | 1229619.8103 | 2662615.4238 | 1229617.1511 | 2662617.4293 | 1229612.3024 | 2662620.2737 | 1229603.3376 | 2662622.8819 | 1229593.7811 | 2662626.1389 | 1229578.9558
11 | 2662612.4339 | 1229621.945 | 2662613.7653 | 1229619.8103
12 | 2662663.4677 | 1229529.5445 | 2662670.2673 | 1229534.8974 | 2662682.948 | 1229538.6693
13 | 2662663.4677 | 1229529.5445 | 2662654.3201 | 1229536.3526 | 2662650.1329 | 1229541.1783 | 2662647.5143 | 1229545.965 | 2662641.6229 | 1229560.7254
14 | 2662663.4677 | 1229529.5445 | 2662667.3821 | 1229526.884
15 | 2662612.4339 | 1229621.945 | 2662619.4182 | 1229623.4305 | 2662633.6199 | 1229626.5598
16 | 2662633.6199 | 1229626.5598 | 2662636.7579 | 1229641.5026 | 2662639.0913 | 1229646.5193
17 | 2662632.8929 | 1229654.5815 | 2662636.3185 | 1229650.1258 | 2662639.0913 | 1229646.5193
18 | 2662667.3821 | 1229526.884 | 2662693.0347 | 1229508.1686
19 | 2662682.948 | 1229538.6693 | 2662691.8895 | 1229541.3289
20 | 2662641.6229 | 1229560.7254 | 2662640.6784 | 1229563.0915
21 | 2662611.2566 | 1229664.6825 | 2662606.2159 | 1229664.2403 | 2662604.5736 | 1229664.0896
22 | 2662611.2566 | 1229664.6825 | 2662612.2054 | 1229687.5296 | 2662610.2701 | 1229702.3708
23 | 2662611.2566 | 1229664.6825 | 2662616.9936 | 1229665.1877 | 2662618.25 | 1229665.301
24 | 2662572.5479 | 1229668.7557 | 2662585.257 | 1229658.2159 | 2662592.7915 | 1229654.2037 | 2662594.2853 | 1229654.0748 | 2662597.9099 | 1229653.7461 | 2662601.3483 | 1229655.2722 | 2662602.5808 | 1229656.9306 | 2662604.1559 | 1229661.3056 | 2662604.5736 | 1229664.0896
25 | 2662610.2701 | 1229702.3708 | 2662608.5134 | 1229715.8424 | 2662607.4682 | 1229724.6341
26 | 2662632.8929 | 1229654.5815 | 2662631.3085 | 1229656.844 | 2662629.176 | 1229655.7542 | 2662625.5776 | 1229655.0381 | 2662622.6327 | 1229655.563 | 2662620.4754 | 1229656.8411 | 2662618.9545 | 1229659.5491 | 2662618.25 | 1229665.301
27 | 2662632.8929 | 1229654.5815 | 2662637.6585 | 1229658.1228 | 2662643.9787 | 1229664.3934
28 | 2662643.9787 | 1229664.3934 | 2662660.4486 | 1229688.0319
29 | 2662667.5577 | 1229698.2352 | 2662660.4486 | 1229688.0319
30 | 2662455.258 | 1229747.0741 | 2662458.9031 | 1229754.1614 | 2662463.3091 | 1229751.5616 | 2662474.4886 | 1229746.698 | 2662484.0428 | 1229739.338 | 2662527.1136 | 1229700.7766 | 2662575.2341 | 1229658.2549 | 2662573.3774 | 1229665.5179 | 2662572.5479 | 1229668.7557
31 | 2662572.5479 | 1229668.7557 | 2662563.6598 | 1229681.893 | 2662559.435 | 1229687.0985
32 | 2662455.258 | 1229747.0741 | 2662460.9171 | 1229743.4534 | 2662472.7105 | 1229731.3472 | 2662483.9725 | 1229714.3099 | 2662486.5774 | 1229704.3308 | 2662484.0827 | 1229696.6218 | 2662475.4416 | 1229689.1596 | 2662470.4445 | 1229685.7301
33 | 2662455.258 | 1229747.0741 | 2662447.4025 | 1229752.0949 | 2662445.0203 | 1229754.3216
34 | 2662544.5887 | 1229705.1263 | 2662548.7088 | 1229700.3144 | 2662559.435 | 1229687.0985
35 | 2662445.0203 | 1229754.3216 | 2662419.9932 | 1229777.7151
36 | 2662705.3769 | 1229545.3408 | 2662691.8895 | 1229541.3289
37 | 2662601.5482 | 1229774.4294 | 2662607.4682 | 1229724.6341
38 | 2662681.2628 | 1229710.7768 | 2662663.0696 | 1229684.4809
39 | 2662691.5963 | 1229725.7126 | 2662681.2628 | 1229710.7768
40 | 2662676.4543 | 1229711.0041 | 2662667.5577 | 1229698.2352
41 | 2662544.5887 | 1229705.1263 | 2662544.199 | 1229705.5815 | 2662510.7366 | 1229738.8403 | 2662509.2726 | 1229740.7033
42 | 2662597.5829 | 1229774.3225 | 2662601.7297 | 1229738.5439
43 | 2662595.4298 | 1229792.8992 | 2662597.5829 | 1229774.3225
44 | 2662705.3769 | 1229545.3408 | 2662718.258 | 1229551.2781
45 | 2662737.1954 | 1229557.5174 | 2662730.5544 | 1229556.5245 | 2662727.8661 | 1229555.7068 | 2662718.258 | 1229551.2781
46 | 2662737.1954 | 1229557.5174 | 2662730.6334 | 1229572.0132 | 2662728.6047 | 1229576.1549
47 | 2662741.7262 | 1229558.1879 | 2662737.1954 | 1229557.5174
48 | 2662728.6047 | 1229576.1549 | 2662727.2685 | 1229578.8826
49 | 2662741.7262 | 1229558.1879 | 2662750.6729 | 1229558.9271 | 2662753.552 | 1229569.6645 | 2662755.6673 | 1229573.1001
50 | 2662713.0254 | 1229602.2419 | 2662711.1288 | 1229607.5636
51 | 2662714.9324 | 1229596.8915 | 2662713.0254 | 1229602.2419
52 | 2662709.2335 | 1229612.8812 | 2662711.1288 | 1229607.5636
53 | 2662717.8202 | 1229588.789 | 2662717.8202 | 1229588.789 | 2662714.9324 | 1229596.8915
54 | 2662706.0096 | 1229621.9269 | 2662709.2335 | 1229612.8812
55 | 2662717.8202 | 1229588.789 | 2662725.3453 | 1229582.8089
56 | 2662706.0096 | 1229621.9269 | 2662703.5865 | 1229628.7257
57 | 2662725.3453 | 1229582.8089 | 2662725.3453 | 1229582.8089 | 2662727.2685 | 1229578.8826
58 | 2662697.1865 | 1229646.6826 | 2662703.5865 | 1229628.7257
59 | 2662732.1494 | 1229648.2476 | 2662734.3046 | 1229645.927
60 | 2662732.1494 | 1229648.2476 | 2662730.0247 | 1229650.5355 | 2662729.4678 | 1229651.4465
61 | 2662717.8718 | 1229680.1266 | 2662726.6483 | 1229656.059 | 2662729.4678 | 1229651.4465
62 | 2662717.8718 | 1229680.1266 | 2662704.7652 | 1229674.7892
63 | 2662764.5098 | 1229634.6667 | 2662768.2591 | 1229623.1391
64 | 2662764.5098 | 1229634.6667 | 2662773.7197 | 1229634.1413 | 2662779.9966 | 1229633.0179 | 2662786.3493 | 1229630.4611
65 | 2662770.2154 | 1229617.1246 | 2662768.2591 | 1229623.1391
66 | 2662786.3493 | 1229630.4611 | 2662794.5031 | 1229623.0645 | 2662801.1774 | 1229611.572 | 2662801.8917 | 1229607.0655
67 | 2662786.3493 | 1229630.4611 | 2662791.5994 | 1229639.7669 | 2662792.6315 | 1229646.7713 | 2662791.8061 | 1229657.182
68 | 2662704.5113 | 1229674.6858 | 2662704.7652 | 1229674.7892
69 | 2662770.2154 | 1229617.1246 | 2662773.5537 | 1229606.8607
70 | 2662807.3581 | 1229584.4196 | 2662801.8917 | 1229607.0655
71 | 2662801.8917 | 1229607.0655 | 2662821.402 | 1229613.5042
72 | 2662788.7339 | 1229677.2499 | 2662789.5461 | 1229672.0774 | 2662791.6177 | 1229659.5578 | 2662791.8061 | 1229657.182
73 | 2662704.5113 | 1229674.6858 | 2662698.4481 | 1229672.2167 | 2662693.7387 | 1229668.3757 | 2662693.7387 | 1229668.3757
74 | 2662688.1801 | 1229727.8335 | 2662691.5963 | 1229725.7126
75 | 2662688.1801 | 1229727.8335 | 2662690.5912 | 1229731.591
76 | 2662688.1801 | 1229727.8335 | 2662676.4543 | 1229711.0041
77 | 2662773.5537 | 1229606.8607 | 2662776.1036 | 1229599.0207
78 | 2662778.1446 | 1229592.7456 | 2662776.1036 | 1229599.0207
79 | 2662770.2906 | 1229577.7439 | 2662767.4191 | 1229577.2268 | 2662761.952 | 1229576.2685 | 2662758.8205 | 1229575.0902 | 2662755.6673 | 1229573.1001 | 2662755.6673 | 1229573.1001
80 | 2662770.2906 | 1229577.7439 | 2662788.9734 | 1229581.1086
81 | 2662807.3581 | 1229584.4196 | 2662788.9734 | 1229581.1086
82 | 2662815.6639 | 1229566.9404 | 2662810.9792 | 1229572.9504 | 2662807.3581 | 1229584.4196
83 | 2662815.6639 | 1229566.9404 | 2662822.0681 | 1229573.8569 | 2662825.4148 | 1229576.8942 | 2662832.5815 | 1229581.5279
84 | 2662832.5815 | 1229581.5279 | 2662834.2257 | 1229582.591 | 2662853.6512 | 1229588.9114 | 2662861.9849 | 1229592.1566
85 | 2662869.9099 | 1229595.2428 | 2662861.9849 | 1229592.1566
86 | 2662693.7387 | 1229668.3757 | 2662693.0766 | 1229662.9208 | 2662694.6031 | 1229653.931 | 2662694.7905 | 1229653.4054
87 | 2662697.1865 | 1229646.6826 | 2662694.7905 | 1229653.4054
88 | 2662831.0926 | 1229616.7022 | 2662833.1687 | 1229617.3802 | 2662834.8366 | 1229619.4102 | 2662841.3837 | 1229627.3244
89 | 2662856.0311 | 1229623.9259 | 2662857.4864 | 1229625.9982 | 2662847.4929 | 1229634.7094 | 2662841.3837 | 1229627.3244
90 | 2662831.0926 | 1229616.7022 | 2662821.402 | 1229613.5042
91 | 2662831.0926 | 1229616.7022 | 2662828.7884 | 1229624.6702
92 | 2662825.2391 | 1229630.0824 | 2662827.0667 | 1229630.6243 | 2662828.7884 | 1229624.6702
93 | 2662697.4964 | 1229742.3522 | 2662690.5912 | 1229731.591
94 | 2662704.1 | 1229746.1576 | 2662703.5348 | 1229745.0892
95 | 2662704.1 | 1229746.1576 | 2662710.0791 | 1229757.4613
96 | 2662697.4964 | 1229742.3522 | 2662700.4818 | 1229748.0429 | 2662704.1 | 1229746.1576
97 | 2662697.4964 | 1229742.3522 | 2662682.1034 | 1229752.3743 | 2662674.1993 | 1229757.555
98 | 2662710.0791 | 1229757.4613 | 2662731.965 | 1229751.0323
99 | 2662409.6919 | 1229786.7645 | 2662414.1379 | 1229783.1883 | 2662419.9932 | 1229777.7151
100 | 2662601.5482 | 1229774.4294 | 2662600.8664 | 1229780.1926 | 2662599.279 | 1229793.529 | 2662595.4298 | 1229792.8992
101 | 2662674.1993 | 1229757.555 | 2662668.7312 | 1229761.1391 | 2662664.1137 | 1229766.7841
102 | 2662751.8932 | 1229745.1784 | 2662731.965 | 1229751.0323
103 | 2662663.5929 | 1229767.4208 | 2662664.1137 | 1229766.7841
104 | 2662557.3396 | 1229774.2642 | 2662556.2458 | 1229782.4581 | 2662557.7291 | 1229785.4867
105 | 2662595.4298 | 1229792.8992 | 2662560.567 | 1229787.1955 | 2662557.7291 | 1229785.4867
106 | 2662630.5105 | 1229810.2685 | 2662629.5885 | 1229811.6744
107 | 2662630.5105 | 1229810.2685 | 2662634.8992 | 1229804.9891 | 2662644.3347 | 1229794.5372 | 2662650.762 | 1229786.2426
108 | 2662663.5929 | 1229767.4208 | 2662661.8242 | 1229769.583 | 2662656.0849 | 1229779.3733 | 2662650.762 | 1229786.2426
109 | 2662509.2726 | 1229740.7033 | 2662492.2014 | 1229762.4276 | 2662490.6661 | 1229764.9125
110 | 2662490.6661 | 1229764.9125 | 2662477.8826 | 1229785.6033 | 2662473.8808 | 1229794.363
111 | 2662788.7339 | 1229677.2499 | 2662802.9152 | 1229675.6211
112 | 2662838.1388 | 1229668.515 | 2662826.9185 | 1229671.894 | 2662815.4806 | 1229673.2074 | 2662804.0704 | 1229675.4884 | 2662802.9152 | 1229675.6211
113 | 2662838.1388 | 1229668.515 | 2662840.2941 | 1229667.866 | 2662847.7499 | 1229664.8328
114 | 2662409.6919 | 1229786.7645 | 2662389.0374 | 1229803.3782
115 | 2662869.9099 | 1229595.2428 | 2662867.4581 | 1229606.4464 | 2662865.425 | 1229606.0024

## bus_geodata
| x | y | coords
0 | 2662567.5894 | 1229465.0488
1 | 2662582.7467 | 1229474.0864
2 | 2662604.4154 | 1229487.0064
3 | 2662615.918 | 1229499.0019
4 | 2662631.9832 | 1229516.8775
5 | 2662608.8483 | 1229505.504
6 | 2662645.1843 | 1229528.3957
7 | 2662598.7669 | 1229514.7761
8 | 2662637.9694 | 1229546.4008
9 | 2662626.1389 | 1229578.9558
10 | 2662613.7653 | 1229619.8103
11 | 2662663.4677 | 1229529.5445
12 | 2662612.4339 | 1229621.945
13 | 2662633.6199 | 1229626.5598
14 | 2662639.0913 | 1229646.5193
15 | 2662667.3821 | 1229526.884
16 | 2662693.0347 | 1229508.1686
17 | 2662682.948 | 1229538.6693
18 | 2662641.6229 | 1229560.7254
19 | 2662611.2566 | 1229664.6825
20 | 2662604.5736 | 1229664.0896
21 | 2662610.2701 | 1229702.3708
22 | 2662618.25 | 1229665.301
23 | 2662632.8929 | 1229654.5815
24 | 2662643.9787 | 1229664.3934
25 | 2662660.4486 | 1229688.0319
26 | 2662572.5479 | 1229668.7557
27 | 2662455.258 | 1229747.0741
28 | 2662559.435 | 1229687.0985
29 | 2662470.4445 | 1229685.7301
30 | 2662445.0203 | 1229754.3216
31 | 2662640.6784 | 1229563.0915
32 | 2662691.8895 | 1229541.3289
33 | 2662607.4682 | 1229724.6341
34 | 2662663.0696 | 1229684.4809
35 | 2662681.2628 | 1229710.7768
36 | 2662667.5577 | 1229698.2352
37 | 2662544.5887 | 1229705.1263
38 | 2662601.7297 | 1229738.5439
39 | 2662597.5829 | 1229774.3225
40 | 2662705.3769 | 1229545.3408
41 | 2662718.258 | 1229551.2781
42 | 2662737.1954 | 1229557.5174
43 | 2662728.6047 | 1229576.1549
44 | 2662741.7262 | 1229558.1879
45 | 2662713.0254 | 1229602.2419
46 | 2662711.1288 | 1229607.5636
47 | 2662714.9324 | 1229596.8915
48 | 2662709.2335 | 1229612.8812
49 | 2662717.8202 | 1229588.789
50 | 2662706.0096 | 1229621.9269
51 | 2662725.3453 | 1229582.8089
52 | 2662703.5865 | 1229628.7257
53 | 2662727.2685 | 1229578.8826
54 | 2662732.1494 | 1229648.2476
55 | 2662734.3046 | 1229645.927
56 | 2662729.4678 | 1229651.4465
57 | 2662717.8718 | 1229680.1266
58 | 2662764.5098 | 1229634.6667
59 | 2662768.2591 | 1229623.1391
60 | 2662786.3493 | 1229630.461
61 | 2662704.7652 | 1229674.7892
62 | 2662770.2154 | 1229617.1246
63 | 2662801.8917 | 1229607.0655
64 | 2662791.8061 | 1229657.182
65 | 2662704.5113 | 1229674.6858
66 | 2662691.5963 | 1229725.7126
67 | 2662688.1801 | 1229727.8335
68 | 2662773.5537 | 1229606.8607
69 | 2662776.1036 | 1229599.0207
70 | 2662778.1446 | 1229592.7456
71 | 2662755.6673 | 1229573.1001
72 | 2662770.2906 | 1229577.7439
73 | 2662788.9734 | 1229581.1086
74 | 2662807.3581 | 1229584.4196
75 | 2662815.6639 | 1229566.9404
76 | 2662832.5815 | 1229581.5279
77 | 2662861.9849 | 1229592.1566
78 | 2662693.7387 | 1229668.3757
79 | 2662694.7905 | 1229653.4054
80 | 2662697.1865 | 1229646.6826
81 | 2662841.3837 | 1229627.3244
82 | 2662831.0926 | 1229616.7022
83 | 2662856.0311 | 1229623.9259
84 | 2662821.402 | 1229613.5042
85 | 2662828.7884 | 1229624.6702
86 | 2662825.2391 | 1229630.0824
87 | 2662690.5912 | 1229731.591
88 | 2662676.4543 | 1229711.0041
89 | 2662703.5348 | 1229745.0892
90 | 2662704.1 | 1229746.1576
91 | 2662697.4964 | 1229742.3522
92 | 2662710.0791 | 1229757.4613
93 | 2662419.9932 | 1229777.7151
94 | 2662601.5482 | 1229774.4294
95 | 2662674.1993 | 1229757.555
96 | 2662731.965 | 1229751.0323
97 | 2662751.8932 | 1229745.1784
98 | 2662664.1137 | 1229766.7841
99 | 2662557.7291 | 1229785.4867
100 | 2662557.3396 | 1229774.2642
101 | 2662595.4298 | 1229792.8992
102 | 2662630.5105 | 1229810.2685
103 | 2662629.5885 | 1229811.6744
104 | 2662650.762 | 1229786.2426
105 | 2662509.2726 | 1229740.7033
106 | 2662490.6661 | 1229764.9125
107 | 2662473.8808 | 1229794.363
108 | 2662663.5929 | 1229767.4208
109 | 2662788.7339 | 1229677.2499
110 | 2662802.9152 | 1229675.6211
111 | 2662838.1388 | 1229668.515
112 | 2662409.6919 | 1229786.7645
113 | 2662389.0374 | 1229803.3782
114 | 2662847.7499 | 1229664.8328
115 | 2662869.9099 | 1229595.2428
116 | 2662865.425 | 1229606.0024
117 | 2662717.8718 | 1229680.1266

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98473 | -0.10663 | 0.00083468 | 0.00020919
1 | 0.98475 | -0.10648 | 0.0010587 | 0.00026534
2 | 0.98482 | -0.10599 | 0 | 0
3 | 0.98487 | -0.10566 | 0 | 0
4 | 0.98511 | -0.10392 | 0.0094954 | 0.0023798
5 | 0.9848 | -0.10617 | 0.0019448 | 0.00048741
6 | 0.98554 | -0.10088 | 0 | 0
7 | 0.98473 | -0.10662 | 0.0031955 | 0.00080086
8 | 0.98467 | -0.10705 | 0.012593 | 0.0031561
9 | 0.98332 | -0.1166 | 0.0044988 | 0.0011275
10 | 0.98174 | -0.12777 | 0.011807 | 0.0029591
11 | 0.98658 | -0.093578 | 0 | 0
12 | 0.98166 | -0.12833 | 0 | 0
13 | 0.98099 | -0.13311 | 0 | 0
14 | 0.98002 | -0.14 | 0 | 0
15 | 0.98656 | -0.093689 | 0 | 0
16 | 0.98646 | -0.094429 | 0.0022725 | 0.00056954
17 | 0.98782 | -0.0848 | 0.0049891 | 0.0012504
18 | 0.98624 | -0.095955 | 0.0015777 | 0.00039541
19 | 0.97764 | -0.15699 | 0 | 0
20 | 0.97743 | -0.15846 | 0 | 0
21 | 0.97716 | -0.1604 | 0.0022226 | 0.00055704
22 | 0.97794 | -0.15482 | 0.0037337 | 0.00093575
23 | 0.97907 | -0.14675 | 0 | 0
24 | 0.97841 | -0.15145 | 0 | 0
25 | 0.97713 | -0.16062 | 0.0013371 | 0.0003351
26 | 0.9761 | -0.16801 | 0 | 0
27 | 0.97287 | -0.19119 | 0 | 0
28 | 0.97584 | -0.1699 | 0.0010289 | 0.00025786
29 | 0.97277 | -0.19191 | 0.00085758 | 0.00021493
30 | 0.97265 | -0.19279 | 0.0011101 | 0.00027823
31 | 0.98622 | -0.096068 | 0.0043392 | 0.0010875
32 | 0.98837 | -0.080906 | 0.0055244 | 0.0013845
33 | 0.97695 | -0.16191 | 0.0019963 | 0.00050031
34 | 0.97509 | -0.17528 | 0.0016166 | 0.00040516
35 | 0.97516 | -0.17474 | 0.0014509 | 0.00036363
36 | 0.9766 | -0.1644 | 0.0019833 | 0.00049705
37 | 0.9756 | -0.17161 | 0.00097439 | 0.0002442
38 | 0.9763 | -0.16665 | 0.0021824 | 0.00054697
39 | 0.97641 | -0.16582 | 0.00058802 | 0.00014737
40 | 0.98925 | -0.074777 | 0 | 0
41 | 0.99013 | -0.068609 | 0.00055875 | 0.00014004
42 | 0.99138 | -0.059846 | 0 | 0
43 | 0.99309 | -0.04787 | 0.00055875 | 0.00014004
44 | 0.99109 | -0.061892 | 0 | 0
45 | 0.99576 | -0.0293 | 0.0016093 | 0.00040332
46 | 0.99626 | -0.025857 | 0.0016063 | 0.00040258
47 | 0.99527 | -0.032734 | 0.0015606 | 0.00039112
48 | 0.99676 | -0.02239 | 0.0016072 | 0.00040281
49 | 0.99452 | -0.037896 | 0.0042695 | 0.00107
50 | 0.99762 | -0.016449 | 0.0015922 | 0.00039904
51 | 0.99371 | -0.043535 | 0.00050315 | 0.0001261
52 | 0.99827 | -0.011951 | 0.0015925 | 0.00039913
53 | 0.99335 | -0.046095 | 0.00050371 | 0.00012624
54 | 0.99855 | -0.010134 | 0.0017052 | 0.00042736
55 | 0.99852 | -0.010336 | 0.006373 | 0.0015972
56 | 0.9986 | -0.009795 | 0.0017022 | 0.0004266
57 | 0.99903 | -0.0067588 | 0 | 0
58 | 0.98373 | -0.11393 | 0 | 0
59 | 0.98355 | -0.11522 | 0.001711 | 0.00042881
60 | 0.98406 | -0.11156 | 0 | 0
61 | 0.99923 | -0.0053744 | 0.002108 | 0.00052831
62 | 0.98347 | -0.11578 | 0.0017081 | 0.00042809
63 | 0.98513 | -0.10398 | 0 | 0
64 | 0.98344 | -0.11599 | 0.0053866 | 0.00135
65 | 0.99924 | -0.0053418 | 0.0020612 | 0.00051658
66 | 0.97524 | -0.17415 | 0 | 0
67 | 0.97526 | -0.17402 | 0 | 0
68 | 0.98336 | -0.11654 | 0.0057605 | 0.0014437
69 | 0.98335 | -0.11663 | 0.00054807 | 0.00013736
70 | 0.98334 | -0.11667 | 0.00054773 | 0.00013727
71 | 0.98955 | -0.072718 | 0.00050371 | 0.00012624
72 | 0.98857 | -0.07963 | 0.0014335 | 0.00035926
73 | 0.98741 | -0.087812 | 0.0009861 | 0.00024714
74 | 0.9863 | -0.095692 | 0 | 0
75 | 0.98611 | -0.097007 | 0 | 0
76 | 0.9859 | -0.098513 | 0.0030769 | 0.00077115
77 | 0.98574 | -0.099622 | 0.0016355 | 0.00040989
78 | 0.99949 | -0.0035814 | 0.0016168 | 0.0004052
79 | 0.99983 | -0.0012217 | 0.0015738 | 0.00039442
80 | 1 | 0 | -0.20913 | -0.05262
81 | 0.98469 | -0.10711 | 0.0017179 | 0.00043054
82 | 0.98476 | -0.10661 | 0 | 0
83 | 0.98463 | -0.1075 | 0.0015003 | 0.00037601
84 | 0.98486 | -0.1059 | 0.0024196 | 0.00060642
85 | 0.98472 | -0.1069 | 0.0017996 | 0.00045103
86 | 0.9847 | -0.10704 | 0.0016583 | 0.0004156
87 | 0.97512 | -0.17501 | 0.0015339 | 0.00038443
88 | 0.97598 | -0.16883 | 0.0029903 | 0.00074944
89 | 0.97461 | -0.17866 | 0.0033867 | 0.00084879
90 | 0.97462 | -0.17862 | 0 | 0
91 | 0.97476 | -0.17763 | 0 | 0
92 | 0.97452 | -0.17936 | 0 | 0
93 | 0.9721 | -0.19676 | 0.00401 | 0.001005
94 | 0.97663 | -0.16422 | 0 | 0
95 | 0.97433 | -0.18074 | 0.0015352 | 0.00038476
96 | 0.97433 | -0.18068 | 0.00089175 | 0.00022349
97 | 0.97419 | -0.18169 | 0.0046209 | 0.0011581
98 | 0.97414 | -0.18207 | 0.0029323 | 0.00073491
99 | 0.97639 | -0.16593 | 0.00052808 | 0.00013235
100 | 0.97638 | -0.16607 | 0.0010888 | 0.00027288
101 | 0.97649 | -0.16528 | 0 | 0
102 | 0.97389 | -0.18386 | 0 | 0
103 | 0.97389 | -0.18389 | 0.001938 | 0.00048572
104 | 0.97398 | -0.18322 | 0.002622 | 0.00065715
105 | 0.97516 | -0.17477 | 0.00091318 | 0.00022886
106 | 0.97493 | -0.17641 | 0.0011808 | 0.00029594
107 | 0.97474 | -0.1778 | 0.0039053 | 0.00097875
108 | 0.97413 | -0.18212 | 0.0016001 | 0.00040103
109 | 0.98315 | -0.11806 | 0 | 0
110 | 0.98294 | -0.11951 | 0.0029188 | 0.00073152
111 | 0.98258 | -0.12209 | 0.0033685 | 0.00084421
112 | 0.97196 | -0.19777 | 0.0051443 | 0.0012893
113 | 0.97189 | -0.19828 | 0.0018139 | 0.0004546
114 | 0.98253 | -0.12247 | 0.0035608 | 0.00089243
115 | 0.98572 | -0.09978 | 0 | 0
116 | 0.98569 | -0.10003 | 0.0018063 | 0.0004527
117 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00083468 | -0.00020919 | 0.0008347 | 0.00020897 | 1.7517e-08 | -2.1777e-07 | 0.0012613 | 0.0012612 | 0.0012613 | 0.98473 | -0.10663 | 0.98475 | -0.10648 | 0.46714
1 | -0.0018934 | -0.00047431 | 0.0018935 | 0.00047404 | 1.2885e-07 | -2.7143e-07 | 0.002861 | 0.0028608 | 0.002861 | 0.98475 | -0.10648 | 0.98482 | -0.10599 | 1.0596
2 | -0.0018935 | -0.00047404 | 0.0018936 | 0.00047386 | 8.4755e-08 | -1.7858e-07 | 0.0028608 | 0.0028608 | 0.0028608 | 0.98482 | -0.10599 | 0.98487 | -0.10566 | 1.0596
3 | -0.0070344 | -0.0017621 | 0.0070361 | 0.0017624 | 1.6939e-06 | 3.456e-07 | 0.010628 | 0.010628 | 0.010628 | 0.98487 | -0.10566 | 0.98511 | -0.10392 | 3.9362
4 | 0.0051408 | 0.0012882 | -0.0051405 | -0.0012882 | 3.6158e-07 | 1.6851e-08 | 0.0077671 | 0.0077671 | 0.0077671 | 0.98487 | -0.10566 | 0.9848 | -0.10617 | 2.8767
5 | -0.016532 | -0.0041422 | 0.016538 | 0.0041446 | 6.9569e-06 | 2.448e-06 | 0.024971 | 0.02497 | 0.024971 | 0.98511 | -0.10392 | 0.98554 | -0.10088 | 9.2484
6 | 0.0031957 | 0.00080076 | -0.0031955 | -0.00080086 | 1.9927e-07 | -9.7617e-08 | 0.0048286 | 0.0048286 | 0.0048286 | 0.9848 | -0.10617 | 0.98473 | -0.10662 | 1.7884
7 | -0.1099 | -0.027625 | 0.11002 | 0.027668 | 0.00011187 | 4.2279e-05 | 0.16597 | 0.16597 | 0.16597 | 0.98554 | -0.10088 | 0.98658 | -0.093578 | 20.4899
8 | 0.093366 | 0.023481 | -0.093286 | -0.023451 | 8.0217e-05 | 3.0112e-05 | 0.141 | 0.141 | 0.141 | 0.98554 | -0.10088 | 0.98467 | -0.10705 | 17.4072
9 | 0.080693 | 0.020295 | -0.080586 | -0.020255 | 0.00010725 | 3.9927e-05 | 0.12197 | 0.12197 | 0.12197 | 0.98467 | -0.10705 | 0.98332 | -0.1166 | 15.0578
10 | 0.076087 | 0.019127 | -0.075969 | -0.019083 | 0.00011826 | 4.3856e-05 | 0.11516 | 0.11516 | 0.11516 | 0.98332 | -0.1166 | 0.98174 | -0.12777 | 14.2174
11 | 0.064162 | 0.016124 | -0.064157 | -0.016122 | 4.9505e-06 | 1.8086e-06 | 0.097265 | 0.097265 | 0.097265 | 0.98174 | -0.12777 | 0.98166 | -0.12833 | 12.0081
12 | -0.11821 | -0.02972 | 0.11835 | 0.029775 | 0.00014474 | 5.4831e-05 | 0.17832 | 0.17832 | 0.17832 | 0.98658 | -0.093578 | 0.98782 | -0.0848 | 22.0152
13 | 0.0059189 | 0.0014832 | -0.005917 | -0.0014829 | 1.9465e-06 | 2.4903e-07 | 0.0089272 | 0.0089274 | 0.0089274 | 0.98658 | -0.093578 | 0.98624 | -0.095955 | 3.3065
14 | 0.0022727 | 0.00056917 | -0.0022727 | -0.00056922 | 3.4635e-08 | -4.7001e-08 | 0.0034277 | 0.0034278 | 0.0034278 | 0.98658 | -0.093578 | 0.98656 | -0.093689 | 1.2695
15 | 0.064157 | 0.016122 | -0.064114 | -0.016107 | 4.2668e-05 | 1.5589e-05 | 0.097265 | 0.097266 | 0.097266 | 0.98166 | -0.12833 | 0.98099 | -0.13311 | 12.0081
16 | 0.064114 | 0.016107 | -0.064053 | -0.016084 | 6.1396e-05 | 2.3089e-05 | 0.097266 | 0.097266 | 0.097266 | 0.98099 | -0.13311 | 0.98002 | -0.14 | 18.0122
17 | 0.064053 | 0.016084 | -0.063993 | -0.016061 | 6.0035e-05 | 2.2963e-05 | 0.097266 | 0.097266 | 0.097266 | 0.98002 | -0.14 | 0.97907 | -0.14675 | 36.0244
18 | 0.0022727 | 0.00056922 | -0.0022725 | -0.00056954 | 2.3282e-07 | -3.1588e-07 | 0.0034278 | 0.0034279 | 0.0034279 | 0.98656 | -0.093689 | 0.98646 | -0.094429 | 1.2696
19 | -0.12334 | -0.031025 | 0.12341 | 0.031051 | 6.7012e-05 | 2.5415e-05 | 0.18584 | 0.18584 | 0.18584 | 0.98782 | -0.0848 | 0.98837 | -0.080906 | 22.943
20 | 0.0043393 | 0.0010875 | -0.0043392 | -0.0010875 | 6.8142e-08 | -6.3012e-09 | 0.006547 | 0.006547 | 0.006547 | 0.98624 | -0.095955 | 0.98622 | -0.096068 | 2.4248
21 | 0.02103 | 0.0052762 | -0.021026 | -0.0052746 | 4.2771e-06 | 1.5612e-06 | 0.032011 | 0.032011 | 0.032011 | 0.97764 | -0.15699 | 0.97743 | -0.15846 | 11.856
22 | 0.0086143 | 0.002157 | -0.0086102 | -0.002156 | 4.0581e-06 | 1.0866e-06 | 0.013111 | 0.013111 | 0.013111 | 0.97764 | -0.15699 | 0.97716 | -0.1604 | 4.8559
23 | -0.029645 | -0.0074332 | 0.029654 | 0.0074366 | 8.9194e-06 | 3.3425e-06 | 0.045122 | 0.045122 | 0.045122 | 0.97764 | -0.15699 | 0.97794 | -0.15482 | 16.7118
24 | 0.021026 | 0.0052746 | -0.020998 | -0.0052645 | 2.7802e-05 | 1.0149e-05 | 0.032011 | 0.032011 | 0.032011 | 0.97743 | -0.15846 | 0.9761 | -0.16801 | 11.8561
25 | 0.0063876 | 0.0015989 | -0.0063863 | -0.0015987 | 1.3246e-06 | 2.2843e-07 | 0.0097263 | 0.0097264 | 0.0097264 | 0.97716 | -0.1604 | 0.97695 | -0.16191 | 3.6024
26 | -0.033387 | -0.0083723 | 0.033425 | 0.0083864 | 3.7405e-05 | 1.4095e-05 | 0.050803 | 0.050803 | 0.050803 | 0.97794 | -0.15482 | 0.97907 | -0.14675 | 18.8159
27 | 0.030568 | 0.0076743 | -0.030548 | -0.0076668 | 1.9959e-05 | 7.4902e-06 | 0.046463 | 0.046463 | 0.046463 | 0.97907 | -0.14675 | 0.97841 | -0.15145 | 17.2086
28 | 0.030548 | 0.0076668 | -0.030509 | -0.0076523 | 3.8811e-05 | 1.4566e-05 | 0.046463 | 0.046463 | 0.046463 | 0.97841 | -0.15145 | 0.97713 | -0.16062 | 17.2086
29 | 0.029172 | 0.0073172 | -0.029157 | -0.0073114 | 1.5316e-05 | 5.7351e-06 | 0.044427 | 0.044427 | 0.044427 | 0.97713 | -0.16062 | 0.9766 | -0.1644 | 16.4545
30 | 0.012987 | 0.0032577 | -0.012946 | -0.0032438 | 4.1637e-05 | 1.3894e-05 | 0.0198 | 0.0198 | 0.0198 | 0.9761 | -0.16801 | 0.97287 | -0.19119 | 7.3335
31 | 0.0080108 | 0.0020068 | -0.0080087 | -0.0020063 | 2.0999e-06 | 5.2565e-07 | 0.012212 | 0.012212 | 0.012212 | 0.9761 | -0.16801 | 0.97584 | -0.1699 | 4.5229
32 | 0.00085767 | 0.00021397 | -0.00085758 | -0.00021493 | 8.5814e-08 | -9.5947e-07 | 0.0013115 | 0.0013118 | 0.0013118 | 0.97287 | -0.19119 | 0.97277 | -0.19191 | 0.48586
33 | 0.012088 | 0.0030298 | -0.012085 | -0.0030289 | 2.6842e-06 | 8.7618e-07 | 0.018489 | 0.018489 | 0.018489 | 0.97287 | -0.19119 | 0.97265 | -0.19279 | 6.8478
34 | 0.0069798 | 0.0017484 | -0.0069782 | -0.0017481 | 1.6508e-06 | 3.4323e-07 | 0.010643 | 0.010643 | 0.010643 | 0.97584 | -0.1699 | 0.9756 | -0.17161 | 3.9419
35 | 0.010975 | 0.0027507 | -0.010969 | -0.0027488 | 6.0268e-06 | 1.893e-06 | 0.016791 | 0.016791 | 0.016791 | 0.97265 | -0.19279 | 0.9721 | -0.19676 | 6.2188
36 | -0.12893 | -0.032435 | 0.12904 | 0.032477 | 0.00011033 | 4.1894e-05 | 0.19416 | 0.19415 | 0.19416 | 0.98837 | -0.080906 | 0.98925 | -0.074777 | 23.9698
37 | 0.00439 | 0.0010984 | -0.0043886 | -0.0010985 | 1.3988e-06 | -8.9712e-08 | 0.0066858 | 0.0066861 | 0.0066861 | 0.97695 | -0.16191 | 0.97663 | -0.16422 | 2.4763
38 | -0.0016166 | -0.00040516 | 0.0016167 | 0.0004048 | 1.2143e-07 | -3.5219e-07 | 0.002467 | 0.0024668 | 0.002467 | 0.97509 | -0.17528 | 0.97516 | -0.17474 | 0.91369
39 | -0.0030676 | -0.00076843 | 0.0030679 | 0.0007683 | 2.483e-07 | -1.311e-07 | 0.0046808 | 0.0046807 | 0.0046808 | 0.97516 | -0.17474 | 0.97524 | -0.17415 | 1.7336
40 | 0.027174 | 0.0068144 | -0.027157 | -0.0068082 | 1.6649e-05 | 6.2087e-06 | 0.041405 | 0.041405 | 0.041405 | 0.9766 | -0.1644 | 0.97598 | -0.16883 | 15.3353
41 | 0.0060038 | 0.0015039 | -0.0060012 | -0.0015035 | 2.6239e-06 | 3.8328e-07 | 0.0091569 | 0.0091571 | 0.0091571 | 0.9756 | -0.17161 | 0.97516 | -0.17477 | 3.3915
42 | -0.0021824 | -0.00054697 | 0.0021827 | 0.00054661 | 2.4867e-07 | -3.5481e-07 | 0.0033263 | 0.0033262 | 0.0033263 | 0.9763 | -0.16665 | 0.97641 | -0.16582 | 1.232
43 | -0.0027707 | -0.00069398 | 0.0027709 | 0.00069383 | 2.0804e-07 | -1.5391e-07 | 0.0042223 | 0.0042222 | 0.0042223 | 0.97641 | -0.16582 | 0.97649 | -0.16528 | 1.5638
44 | -0.12904 | -0.032477 | 0.12916 | 0.032519 | 0.00011121 | 4.2226e-05 | 0.19415 | 0.19415 | 0.19415 | 0.98925 | -0.074777 | 0.99013 | -0.068609 | 23.9697
45 | -0.12971 | -0.032659 | 0.12987 | 0.03272 | 0.000159 | 6.0377e-05 | 0.19499 | 0.19499 | 0.19499 | 0.99013 | -0.068609 | 0.99138 | -0.059846 | 24.0734
46 | -0.17423 | -0.043873 | 0.17452 | 0.043984 | 0.00029211 | 0.00011156 | 0.26159 | 0.26159 | 0.26159 | 0.99138 | -0.059846 | 0.99309 | -0.04787 | 32.2948
47 | 0.044359 | 0.011153 | -0.044346 | -0.011148 | 1.2638e-05 | 4.8019e-06 | 0.066594 | 0.066594 | 0.066594 | 0.99138 | -0.059846 | 0.99109 | -0.061892 | 24.6643
48 | -0.17508 | -0.044124 | 0.17513 | 0.044141 | 4.3509e-05 | 1.6616e-05 | 0.26242 | 0.26242 | 0.26242 | 0.99309 | -0.04787 | 0.99335 | -0.046095 | 32.3981
49 | 0.044346 | 0.011148 | -0.04428 | -0.011123 | 6.677e-05 | 2.537e-05 | 0.066594 | 0.066594 | 0.066594 | 0.99109 | -0.061892 | 0.98955 | -0.072718 | 24.6644
50 | -0.18399 | -0.046418 | 0.18408 | 0.046452 | 8.8906e-05 | 3.3974e-05 | 0.27506 | 0.27506 | 0.27506 | 0.99576 | -0.0293 | 0.99626 | -0.025857 | 33.9578
51 | 0.18238 | 0.046015 | -0.1823 | -0.045981 | 8.7829e-05 | 3.3559e-05 | 0.27265 | 0.27265 | 0.27265 | 0.99576 | -0.0293 | 0.99527 | -0.032734 | 33.6609
52 | -0.18569 | -0.046855 | 0.18578 | 0.046889 | 9.0394e-05 | 3.4546e-05 | 0.27746 | 0.27746 | 0.27746 | 0.99626 | -0.025857 | 0.99676 | -0.02239 | 34.254
53 | 0.18074 | 0.04559 | -0.1806 | -0.04554 | 0.00013074 | 4.995e-05 | 0.27032 | 0.27032 | 0.27032 | 0.99527 | -0.032734 | 0.99452 | -0.037896 | 33.3729
54 | -0.18739 | -0.047292 | 0.18754 | 0.047352 | 0.00015644 | 5.9792e-05 | 0.27986 | 0.27986 | 0.27986 | 0.99676 | -0.02239 | 0.99762 | -0.016449 | 34.5502
55 | 0.17634 | 0.04447 | -0.1762 | -0.044417 | 0.00013927 | 5.3192e-05 | 0.26393 | 0.26393 | 0.26393 | 0.99452 | -0.037896 | 0.99371 | -0.043535 | 32.5843
56 | -0.18913 | -0.047751 | 0.18925 | 0.047797 | 0.00011958 | 4.5711e-05 | 0.28223 | 0.28223 | 0.28223 | 0.99762 | -0.016449 | 0.99827 | -0.011951 | 34.8434
57 | 0.17569 | 0.044291 | -0.17563 | -0.044267 | 6.2986e-05 | 2.4056e-05 | 0.26318 | 0.26318 | 0.26318 | 0.99371 | -0.043535 | 0.99335 | -0.046095 | 32.4913
58 | -0.19085 | -0.048196 | 0.19117 | 0.048319 | 0.00032118 | 0.00012278 | 0.28461 | 0.2846 | 0.28461 | 0.99827 | -0.011951 | 1 | 0 | 35.1364
59 | 0.0063732 | 0.0015973 | -0.006373 | -0.0015972 | 1.7825e-07 | 2.7129e-08 | 0.0094972 | 0.0094972 | 0.0094972 | 0.99855 | -0.010134 | 0.99852 | -0.010336 | 3.5175
60 | -0.0080784 | -0.0020246 | 0.0080788 | 0.0020247 | 3.7891e-07 | 9.0918e-08 | 0.012038 | 0.012038 | 0.012038 | 0.99855 | -0.010134 | 0.9986 | -0.009795 | 4.4586
61 | -0.009781 | -0.0024513 | 0.0097851 | 0.0024525 | 4.1121e-06 | 1.1755e-06 | 0.014575 | 0.014574 | 0.014575 | 0.9986 | -0.009795 | 0.99903 | -0.0067588 | 5.398
62 | -0.0097851 | -0.0024525 | 0.0097869 | 0.002453 | 1.8758e-06 | 5.361e-07 | 0.014574 | 0.014574 | 0.014574 | 0.99903 | -0.0067588 | 0.99923 | -0.0053744 | 5.3979
63 | 0.010279 | 0.0025759 | -0.010277 | -0.0025754 | 1.8285e-06 | 5.4939e-07 | 0.015548 | 0.015548 | 0.015548 | 0.98373 | -0.11393 | 0.98355 | -0.11522 | 5.7584
64 | -0.010279 | -0.0025759 | 0.010282 | 0.002577 | 3.377e-06 | 1.0145e-06 | 0.015548 | 0.015548 | 0.015548 | 0.98373 | -0.11393 | 0.98406 | -0.11156 | 5.7584
65 | 0.0085658 | 0.0021466 | -0.0085652 | -0.0021464 | 6.628e-07 | 1.7466e-07 | 0.012959 | 0.012959 | 0.012959 | 0.98355 | -0.11522 | 0.98347 | -0.11578 | 4.7997
66 | -0.025533 | -0.0064002 | 0.02556 | 0.0064102 | 2.6824e-05 | 9.9503e-06 | 0.03861 | 0.03861 | 0.03861 | 0.98406 | -0.11156 | 0.98513 | -0.10398 | 14.3
67 | 0.015251 | 0.0038232 | -0.015242 | -0.00382 | 9.3619e-06 | 3.2426e-06 | 0.023062 | 0.023062 | 0.023062 | 0.98406 | -0.11156 | 0.98344 | -0.11599 | 8.5416
68 | -0.011895 | -0.0029813 | 0.011895 | 0.0029814 | 5.3666e-08 | 1.705e-08 | 0.017713 | 0.017713 | 0.017713 | 0.99923 | -0.0053744 | 0.99924 | -0.0053418 | 6.5606
69 | 0.0068571 | 0.0017183 | -0.0068564 | -0.0017182 | 7.2493e-07 | 1.4188e-07 | 0.010375 | 0.010375 | 0.010375 | 0.98347 | -0.11578 | 0.98336 | -0.11654 | 3.8426
70 | -0.03466 | -0.00869 | 0.034699 | 0.008705 | 3.9844e-05 | 1.5028e-05 | 0.052354 | 0.052354 | 0.052354 | 0.98513 | -0.10398 | 0.9863 | -0.095692 | 19.3903
71 | 0.0090993 | 0.0022798 | -0.0090968 | -0.0022792 | 2.4217e-06 | 6.6993e-07 | 0.013744 | 0.013744 | 0.013744 | 0.98513 | -0.10398 | 0.98486 | -0.1059 | 5.0904
72 | 0.0098555 | 0.00247 | -0.0098527 | -0.0024692 | 2.8181e-06 | 8.2627e-07 | 0.014912 | 0.014912 | 0.014912 | 0.98344 | -0.11599 | 0.98315 | -0.11806 | 5.5231
73 | -0.013956 | -0.0034979 | 0.01396 | 0.0034991 | 3.4024e-06 | 1.1432e-06 | 0.020783 | 0.020783 | 0.020783 | 0.99924 | -0.0053418 | 0.99949 | -0.0035814 | 7.6974
74 | -0.0030679 | -0.0007683 | 0.0030679 | 0.00076827 | 5.4863e-08 | -2.8973e-08 | 0.0046807 | 0.0046807 | 0.0046807 | 0.97524 | -0.17415 | 0.97526 | -0.17402 | 1.7336
75 | 0.021082 | 0.005284 | -0.021079 | -0.005283 | 2.8824e-06 | 1.0529e-06 | 0.032166 | 0.032166 | 0.032166 | 0.97526 | -0.17402 | 0.97512 | -0.17501 | 11.9132
76 | -0.024149 | -0.0060523 | 0.024167 | 0.0060587 | 1.7377e-05 | 6.4273e-06 | 0.036846 | 0.036846 | 0.036846 | 0.97526 | -0.17402 | 0.97598 | -0.16883 | 13.6468
77 | 0.0010958 | 0.00027445 | -0.0010958 | -0.00027455 | 1.4144e-08 | -9.9148e-08 | 0.0016581 | 0.0016582 | 0.0016582 | 0.98336 | -0.11654 | 0.98335 | -0.11663 | 0.61413
78 | 0.00054773 | 0.00013719 | -0.00054773 | -0.00013727 | 2.8285e-09 | -8.2623e-08 | 0.0008288 | 0.00082883 | 0.00082883 | 0.98335 | -0.11663 | 0.98334 | -0.11667 | 0.30698
79 | 0.043776 | 0.010996 | -0.043734 | -0.010981 | 4.2038e-05 | 1.5969e-05 | 0.065836 | 0.065836 | 0.065836 | 0.98955 | -0.072718 | 0.98857 | -0.07963 | 24.3839
80 | 0.0423 | 0.010621 | -0.042252 | -0.010603 | 4.8034e-05 | 1.8231e-05 | 0.063679 | 0.063679 | 0.063679 | 0.98857 | -0.07963 | 0.98741 | -0.087812 | 23.5847
81 | 0.041266 | 0.010356 | -0.041221 | -0.010339 | 4.5087e-05 | 1.7103e-05 | 0.062193 | 0.062193 | 0.062193 | 0.98741 | -0.087812 | 0.9863 | -0.095692 | 23.0344
82 | 0.0065219 | 0.0016337 | -0.0065207 | -0.0016335 | 1.1864e-06 | 2.0571e-07 | 0.0098392 | 0.0098393 | 0.0098393 | 0.9863 | -0.095692 | 0.98611 | -0.097007 | 3.6442
83 | 0.0065207 | 0.0016335 | -0.0065193 | -0.0016333 | 1.358e-06 | 2.356e-07 | 0.0098393 | 0.0098394 | 0.0098394 | 0.98611 | -0.097007 | 0.9859 | -0.098513 | 3.6442
84 | 0.0034424 | 0.00086215 | -0.0034419 | -0.00086235 | 5.2769e-07 | -1.9648e-07 | 0.0051954 | 0.0051955 | 0.0051955 | 0.9859 | -0.098513 | 0.98574 | -0.099622 | 1.9243
85 | 0.0018064 | 0.00045246 | -0.0018064 | -0.00045255 | 3.9458e-08 | -9.3239e-08 | 0.0027267 | 0.0027268 | 0.0027268 | 0.98574 | -0.099622 | 0.98572 | -0.09978 | 1.0099
86 | -0.015576 | -0.0039043 | 0.015581 | 0.003906 | 5.091e-06 | 1.7592e-06 | 0.02319 | 0.02319 | 0.02319 | 0.99949 | -0.0035814 | 0.99983 | -0.0012217 | 8.5888
87 | -0.017155 | -0.0043005 | 0.017158 | 0.0043015 | 2.9032e-06 | 1.023e-06 | 0.025532 | 0.025532 | 0.025532 | 0.99983 | -0.0012217 | 1 | 0 | 9.4563
88 | -0.0032183 | -0.00080626 | 0.0032185 | 0.00080615 | 2.2258e-07 | -1.0627e-07 | 0.0048632 | 0.0048631 | 0.0048632 | 0.98469 | -0.10711 | 0.98476 | -0.10661 | 1.8012
89 | 0.0015004 | 0.00037572 | -0.0015003 | -0.00037601 | 8.139e-08 | -2.9145e-07 | 0.0022672 | 0.0022673 | 0.0022673 | 0.98469 | -0.10711 | 0.98463 | -0.1075 | 0.83974
90 | -0.0066765 | -0.0016726 | 0.0066772 | 0.0016728 | 6.4806e-07 | 1.1941e-07 | 0.010088 | 0.010088 | 0.010088 | 0.98476 | -0.10661 | 0.98486 | -0.1059 | 3.7364
91 | 0.0034581 | 0.00086649 | -0.0034579 | -0.00086654 | 1.4131e-07 | -5.117e-08 | 0.0052252 | 0.0052253 | 0.0052253 | 0.98476 | -0.10661 | 0.98472 | -0.1069 | 1.9353
92 | 0.0016583 | 0.00041551 | -0.0016583 | -0.0004156 | 3.1755e-08 | -9.0882e-08 | 0.0025058 | 0.0025059 | 0.0025059 | 0.98472 | -0.1069 | 0.9847 | -0.10704 | 0.9281
93 | 0.019545 | 0.0048985 | -0.019538 | -0.004896 | 7.0971e-06 | 2.5702e-06 | 0.029825 | 0.029825 | 0.029825 | 0.97512 | -0.17501 | 0.97476 | -0.17763 | 11.0463
94 | -0.0033867 | -0.00084879 | 0.0033867 | 0.00084879 | 2.0165e-08 | -7.3063e-09 | 0.0051708 | 0.0051708 | 0.0051708 | 0.97461 | -0.17866 | 0.97462 | -0.17862 | 1.9151
95 | 0.0055148 | 0.0013817 | -0.0055143 | -0.0013817 | 5.6539e-07 | 5.8198e-08 | 0.0084197 | 0.0084197 | 0.0084197 | 0.97462 | -0.17862 | 0.97452 | -0.17936 | 3.1184
96 | -0.0089016 | -0.0022305 | 0.0089028 | 0.0022309 | 1.2109e-06 | 3.3477e-07 | 0.01359 | 0.01359 | 0.01359 | 0.97462 | -0.17862 | 0.97476 | -0.17763 | 5.0335
97 | 0.010635 | 0.0026651 | -0.01063 | -0.0026637 | 4.5752e-06 | 1.4131e-06 | 0.016235 | 0.016235 | 0.016235 | 0.97476 | -0.17763 | 0.97433 | -0.18074 | 6.0129
98 | 0.0055143 | 0.0013817 | -0.0055132 | -0.0013816 | 1.0091e-06 | 1.0396e-07 | 0.0084197 | 0.0084198 | 0.0084198 | 0.97452 | -0.17936 | 0.97433 | -0.18068 | 3.1185
99 | 0.0069592 | 0.0017438 | -0.0069583 | -0.0017436 | 9.7157e-07 | 2.036e-07 | 0.010653 | 0.010653 | 0.010653 | 0.9721 | -0.19676 | 0.97196 | -0.19777 | 3.9454
100 | 0.0043886 | 0.0010985 | -0.004388 | -0.0010985 | 6.4534e-07 | -4.1237e-08 | 0.0066861 | 0.0066862 | 0.0066862 | 0.97663 | -0.16422 | 0.97649 | -0.16528 | 2.4764
101 | 0.0090951 | 0.0022789 | -0.0090934 | -0.0022784 | 1.6651e-06 | 4.6822e-07 | 0.01389 | 0.01389 | 0.01389 | 0.97433 | -0.18074 | 0.97414 | -0.18207 | 5.1445
102 | 0.0046215 | 0.0011581 | -0.0046209 | -0.0011581 | 6.4564e-07 | -1.0323e-08 | 0.007058 | 0.007058 | 0.007058 | 0.97433 | -0.18068 | 0.97419 | -0.18169 | 2.6141
103 | 0.0061611 | 0.0015435 | -0.0061611 | -0.0015435 | 4.5461e-08 | 7.2442e-09 | 0.009411 | 0.009411 | 0.009411 | 0.97414 | -0.18207 | 0.97413 | -0.18212 | 3.4856
104 | 0.0010888 | 0.00027275 | -0.0010888 | -0.00027288 | 1.9998e-08 | -1.3788e-07 | 0.0016593 | 0.0016594 | 0.0016594 | 0.97639 | -0.16593 | 0.97638 | -0.16607 | 0.61459
105 | -0.0016169 | -0.0004051 | 0.0016171 | 0.00040467 | 1.4639e-07 | -4.2701e-07 | 0.0024641 | 0.0024639 | 0.0024641 | 0.97639 | -0.16593 | 0.97649 | -0.16528 | 0.91264
106 | 0.0019381 | 0.0004857 | -0.001938 | -0.00048572 | 9.1988e-09 | -1.7382e-08 | 0.0029612 | 0.0029612 | 0.0029612 | 0.97389 | -0.18386 | 0.97389 | -0.18389 | 1.0967
107 | -0.0019381 | -0.0004857 | 0.0019382 | 0.00048538 | 1.7201e-07 | -3.2509e-07 | 0.0029612 | 0.002961 | 0.0029612 | 0.97389 | -0.18386 | 0.97398 | -0.18322 | 1.0967
108 | -0.0045603 | -0.0011425 | 0.004561 | 0.0011425 | 6.9152e-07 | -1.8232e-08 | 0.0069669 | 0.0069668 | 0.0069669 | 0.97398 | -0.18322 | 0.97413 | -0.18212 | 2.5803
109 | 0.005088 | 0.0012746 | -0.0050868 | -0.0012746 | 1.1491e-06 | 6.0902e-08 | 0.0077637 | 0.0077638 | 0.0077638 | 0.97516 | -0.17477 | 0.97493 | -0.17641 | 2.8755
110 | 0.003906 | 0.00097862 | -0.0039053 | -0.00097875 | 7.5297e-07 | -1.3369e-07 | 0.0059615 | 0.0059617 | 0.0059617 | 0.97493 | -0.17641 | 0.97474 | -0.1778 | 2.208
111 | 0.0098527 | 0.0024692 | -0.0098507 | -0.0024686 | 1.9808e-06 | 5.8085e-07 | 0.014912 | 0.014912 | 0.014912 | 0.98315 | -0.11806 | 0.98294 | -0.11951 | 5.5231
112 | 0.006932 | 0.0017371 | -0.0069295 | -0.0017366 | 2.4758e-06 | 4.957e-07 | 0.010494 | 0.010494 | 0.010494 | 0.98294 | -0.11951 | 0.98258 | -0.12209 | 3.8866
113 | 0.003561 | 0.00089237 | -0.0035608 | -0.00089243 | 1.8692e-07 | -5.8565e-08 | 0.0053927 | 0.0053928 | 0.0053928 | 0.98258 | -0.12209 | 0.98253 | -0.12247 | 1.9973
114 | 0.001814 | 0.00045432 | -0.0018139 | -0.0004546 | 1.2756e-07 | -2.7944e-07 | 0.002777 | 0.0027771 | 0.0027771 | 0.97196 | -0.19777 | 0.97189 | -0.19828 | 1.0286
115 | 0.0018064 | 0.00045255 | -0.0018063 | -0.0004527 | 6.284e-08 | -1.4847e-07 | 0.0027268 | 0.0027268 | 0.0027268 | 0.98572 | -0.09978 | 0.98569 | -0.10003 | 1.0099

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.2107 | 0.053015

## res_load
| p_mw | q_mvar
0 | 0.00083468 | 0.00020919
1 | 0.0010587 | 0.00026534
2 | 0.0094954 | 0.0023798
3 | 0.0019448 | 0.00048741
4 | 0.0031955 | 0.00080086
5 | 0.012593 | 0.0031561
6 | 0.0044988 | 0.0011275
7 | 0.011807 | 0.0029591
8 | 0.0022725 | 0.00056954
9 | 0.0049891 | 0.0012504
10 | 0.0015777 | 0.00039541
11 | 0.0022226 | 0.00055704
12 | 0.0037337 | 0.00093575
13 | 0.0013371 | 0.0003351
14 | 0.0010289 | 0.00025786
15 | 0.00085758 | 0.00021493
16 | 0.0011101 | 0.00027823
17 | 0.0043392 | 0.0010875
18 | 0.0055244 | 0.0013845
19 | 0.0019963 | 0.00050031
20 | 0.0016166 | 0.00040516
21 | 0.0014509 | 0.00036363
22 | 0.0019833 | 0.00049705
23 | 0.00097439 | 0.0002442
24 | 0.0021824 | 0.00054697
25 | 0.00058802 | 0.00014737
26 | 0.00055875 | 0.00014004
27 | 0.00055875 | 0.00014004
28 | 0.0016093 | 0.00040332
29 | 0.0016063 | 0.00040258
30 | 0.0015606 | 0.00039112
31 | 0.0016072 | 0.00040281
32 | 0.0042695 | 0.00107
33 | 0.0015922 | 0.00039904
34 | 0.00050315 | 0.0001261
35 | 0.0015925 | 0.00039913
36 | 0.00050371 | 0.00012624
37 | 0.0017052 | 0.00042736
38 | 0.006373 | 0.0015972
39 | 0.0017022 | 0.0004266
40 | 0.001711 | 0.00042881
41 | 0.002108 | 0.00052831
42 | 0.0017081 | 0.00042809
43 | 0.0053866 | 0.00135
44 | 0.0020612 | 0.00051658
45 | 0.0057605 | 0.0014437
46 | 0.00054807 | 0.00013736
47 | 0.00054773 | 0.00013727
48 | 0.00050371 | 0.00012624
49 | 0.0014335 | 0.00035926
50 | 0.0009861 | 0.00024714
51 | 0.0030769 | 0.00077115
52 | 0.0016355 | 0.00040989
53 | 0.0016168 | 0.0004052
54 | 0.0015738 | 0.00039442
55 | 0.0015764 | 0.00039508
56 | 0.0017179 | 0.00043054
57 | 0.0015003 | 0.00037601
58 | 0.0024196 | 0.00060642
59 | 0.0017996 | 0.00045103
60 | 0.0016583 | 0.0004156
61 | 0.0015339 | 0.00038443
62 | 0.0029903 | 0.00074944
63 | 0.0033867 | 0.00084879
64 | 0.00401 | 0.001005
65 | 0.0015352 | 0.00038476
66 | 0.00089175 | 0.00022349
67 | 0.0046209 | 0.0011581
68 | 0.0029323 | 0.00073491
69 | 0.00052808 | 0.00013235
70 | 0.0010888 | 0.00027288
71 | 0.001938 | 0.00048572
72 | 0.002622 | 0.00065715
73 | 0.00091318 | 0.00022886
74 | 0.0011808 | 0.00029594
75 | 0.0039053 | 0.00097875
76 | 0.0016001 | 0.00040103
77 | 0.0029188 | 0.00073152
78 | 0.0033685 | 0.00084421
79 | 0.0051443 | 0.0012893
80 | 0.0018139 | 0.0004546
81 | 0.0035608 | 0.00089243
82 | 0.0018063 | 0.0004527

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1