## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1030-28_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1030-28_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1030-28_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1030-28_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1030-28_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1030-28_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1030-28_0_3_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_1030-28_0_3_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_1030-28_0_3_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_1030-28_0_3_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1030-28_0_3_node_74 | 0.4 | n |  | TRUE
11 | bus_LV_1030-28_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1030-28_0_3_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_1030-28_0_3_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_1030-28_0_3_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1030-28_0_3_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_1030-28_0_3_node_100 | 0.4 | n |  | TRUE
17 | bus_LV_1030-28_0_3_node_97 | 0.4 | n |  | TRUE
18 | bus_LV_1030-28_0_3_node_75 | 0.4 | n |  | TRUE
19 | bus_LV_1030-28_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1030-28_0_3_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_1030-28_0_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1030-28_0_3_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_1030-28_0_3_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_1030-28_0_3_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1030-28_0_3_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1030-28_0_3_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_1030-28_0_3_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1030-28_0_3_node_102 | 0.4 | n |  | TRUE
29 | bus_LV_1030-28_0_3_node_98 | 0.4 | n |  | TRUE
30 | bus_LV_1030-28_0_3_node_76 | 0.4 | n |  | TRUE
31 | bus_LV_1030-28_0_3_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_1030-28_0_3_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_1030-28_0_3_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_1030-28_0_3_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_1030-28_0_3_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_1030-28_0_3_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_1030-28_0_3_node_50 | 0.4 | n |  | TRUE
38 | bus_LV_1030-28_0_3_node_47 | 0.4 | n |  | TRUE
39 | bus_LV_1030-28_0_3_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_1030-28_0_3_node_77 | 0.4 | n |  | TRUE
41 | bus_LV_1030-28_0_3_node_79 | 0.4 | n |  | TRUE
42 | bus_LV_1030-28_0_3_node_109 | 0.4 | n |  | TRUE
43 | bus_LV_1030-28_0_3_node_71 | 0.4 | n |  | TRUE
44 | bus_LV_1030-28_0_3_node_94 | 0.4 | n |  | TRUE
45 | bus_LV_1030-28_0_3_node_108 | 0.4 | n |  | TRUE
46 | bus_LV_1030-28_0_3_node_69 | 0.4 | n |  | TRUE
47 | bus_LV_1030-28_0_3_node_61 | 0.4 | n |  | TRUE
48 | bus_LV_1030-28_0_3_node_72 | 0.4 | n |  | TRUE
49 | bus_LV_1030-28_0_3_node_67 | 0.4 | n |  | TRUE
50 | bus_LV_1030-28_0_3_node_96 | 0.4 | n |  | TRUE
51 | bus_LV_1030-28_0_3_node_95 | 0.4 | n |  | TRUE
52 | bus_LV_1030-28_0_3_node_92 | 0.4 | n |  | TRUE
53 | bus_LV_1030-28_0_3_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_1030-28_0_3_node_33 | 0.4 | n |  | TRUE
55 | bus_LV_1030-28_0_3_node_34 | 0.4 | n |  | TRUE
56 | bus_LV_1030-28_0_3_node_35 | 0.4 | n |  | TRUE
57 | bus_LV_1030-28_0_3_node_36 | 0.4 | n |  | TRUE
58 | bus_LV_1030-28_0_3_node_64 | 0.4 | n |  | TRUE
59 | bus_LV_1030-28_0_3_node_43 | 0.4 | n |  | TRUE
60 | bus_LV_1030-28_0_3_node_52 | 0.4 | n |  | TRUE
61 | bus_LV_1030-28_0_3_node_37 | 0.4 | n |  | TRUE
62 | bus_LV_1030-28_0_3_node_38 | 0.4 | n |  | TRUE
63 | bus_LV_1030-28_0_3_node_39 | 0.4 | n |  | TRUE
64 | bus_LV_1030-28_0_3_node_65 | 0.4 | n |  | TRUE
65 | bus_LV_1030-28_0_3_node_41 | 0.4 | n |  | TRUE
66 | bus_LV_1030-28_0_3_node_118 | 0.4 | n |  | TRUE
67 | bus_LV_1030-28_0_3_node_116 | 0.4 | n |  | TRUE
68 | bus_LV_1030-28_0_3_node_44 | 0.4 | n |  | TRUE
69 | bus_LV_1030-28_0_3_node_119 | 0.4 | n |  | TRUE
70 | bus_LV_1030-28_0_3_node_117 | 0.4 | n |  | TRUE
71 | bus_LV_1030-28_0_3_node_114 | 0.4 | n |  | TRUE
72 | bus_LV_1030-28_0_3_node_112 | 0.4 | n |  | TRUE
73 | bus_LV_1030-28_0_3_node_113 | 0.4 | n |  | TRUE
74 | bus_LV_1030-28_0_3_node_111 | 0.4 | n |  | TRUE
75 | bus_LV_1030-28_0_3_node_122 | 0.4 | n |  | TRUE
76 | bus_LV_1030-28_0_3_node_45 | 0.4 | n |  | TRUE
77 | bus_LV_1030-28_0_3_node_46 | 0.4 | n |  | TRUE
78 | bus_LV_1030-28_0_3_node_48 | 0.4 | n |  | TRUE
79 | bus_LV_1030-28_0_3_node_49 | 0.4 | n |  | TRUE
80 | bus_LV_1030-28_0_3_node_51 | 0.4 | n |  | TRUE
81 | bus_LV_1030-28_0_3_node_60 | 0.4 | n |  | TRUE
82 | bus_LV_1030-28_0_3_node_59 | 0.4 | n |  | TRUE
83 | bus_LV_1030-28_0_3_node_53 | 0.4 | n |  | TRUE
84 | bus_LV_1030-28_0_3_node_54 | 0.4 | n |  | TRUE
85 | bus_LV_1030-28_0_3_node_55 | 0.4 | n |  | TRUE
86 | bus_LV_1030-28_0_3_node_56 | 0.4 | n |  | TRUE
87 | bus_LV_1030-28_0_3_node_57 | 0.4 | n |  | TRUE
88 | bus_LV_1030-28_0_3_node_58 | 0.4 | n |  | TRUE
89 | bus_LV_1030-28_0_3_node_63 | 0.4 | n |  | TRUE
90 | bus_LV_1030-28_0_3_node_125 | 0.4 | n |  | TRUE
91 | bus_LV_1030-28_0_3_node_124 | 0.4 | n |  | TRUE
92 | bus_LV_1030-28_0_3_node_120 | 0.4 | n |  | TRUE
93 | bus_LV_1030-28_0_3_node_66 | 0.4 | n |  | TRUE
94 | bus_LV_1030-28_0_3_node_91 | 0.4 | n |  | TRUE
95 | bus_LV_1030-28_0_3_node_115 | 0.4 | n |  | TRUE
96 | bus_LV_1030-28_0_3_node_89 | 0.4 | n |  | TRUE
97 | bus_LV_1030-28_0_3_node_80 | 0.4 | n |  | TRUE
98 | bus_LV_1030-28_0_3_node_81 | 0.4 | n |  | TRUE
99 | bus_LV_1030-28_0_3_node_82 | 0.4 | n |  | TRUE
100 | bus_LV_1030-28_0_3_node_83 | 0.4 | n |  | TRUE
101 | bus_LV_1030-28_0_3_node_84 | 0.4 | n |  | TRUE
102 | bus_LV_1030-28_0_3_node_85 | 0.4 | n |  | TRUE
103 | bus_LV_1030-28_0_3_node_86 | 0.4 | n |  | TRUE
104 | bus_LV_1030-28_0_3_node_87 | 0.4 | n |  | TRUE
105 | bus_LV_1030-28_0_3_node_88 | 0.4 | n |  | TRUE
106 | bus_LV_1030-28_0_3_node_90 | 0.4 | n |  | TRUE
107 | bus_LV_1030-28_0_3_node_107 | 0.4 | n |  | TRUE
108 | bus_LV_1030-28_0_3_node_106 | 0.4 | n |  | TRUE
109 | bus_LV_1030-28_0_3_node_93 | 0.4 | n |  | TRUE
110 | bus_LV_1030-28_0_3_node_99 | 0.4 | n |  | TRUE
111 | bus_LV_1030-28_0_3_node_110 | 0.4 | n |  | TRUE
112 | bus_LV_1030-28_0_3_node_103 | 0.4 | n |  | TRUE
113 | bus_LV_1030-28_0_3_node_104 | 0.4 | n |  | TRUE
114 | bus_LV_1030-28_0_3_node_105 | 0.4 | n |  | TRUE
115 | bus_LV_1030-28_0_3_node_121 | 0.4 | n |  | TRUE
116 | bus_LV_1030-28_0_3_node_123 | 0.4 | n |  | TRUE
117 | bus_MV_470_1_node_75 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1030-28_0_3_load_0 | 0 | 0.00099023 | 0.00024817 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1030-28_0_3_load_1 | 1 | 0.00035605 | 8.9234e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1030-28_0_3_load_10 | 6 | 0.0015166 | 0.0003801 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1030-28_0_3_load_13 | 8 | 0.0062371 | 0.0015632 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1030-28_0_3_load_74 | 10 | 0.0025666 | 0.00064326 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1030-28_0_3_load_21 | 13 | 0.0017366 | 0.00043523 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1030-28_0_3_load_14 | 15 | 0.00090016 | 0.0002256 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1030-28_0_3_load_100 | 16 | 0.00022167 | 5.5555e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1030-28_0_3_load_97 | 17 | 0.0015192 | 0.00038074 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1030-28_0_3_load_75 | 18 | 0.00040365 | 0.00010116 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1030-28_0_3_load_12 | 19 | 0.0090407 | 0.0022658 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1030-28_0_3_load_24 | 20 | 0.00030223 | 7.5746e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1030-28_0_3_load_18 | 21 | 0.0020499 | 0.00051376 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1030-28_0_3_load_22 | 22 | 0.0020694 | 0.00051864 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1030-28_0_3_load_23 | 23 | 0.0015599 | 0.00039094 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1030-28_0_3_load_19 | 24 | 0.0029913 | 0.00074968 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1030-28_0_3_load_17 | 25 | 0.002811 | 0.0007045 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1030-28_0_3_load_15 | 27 | 0.00052714 | 0.00013211 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1030-28_0_3_load_102 | 28 | 0.0018941 | 0.00047472 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1030-28_0_3_load_98 | 29 | 0.00041611 | 0.00010429 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1030-28_0_3_load_76 | 30 | 0.00046504 | 0.00011655 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1030-28_0_3_load_25 | 31 | 0.00039727 | 9.9565e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1030-28_0_3_load_30 | 34 | 0.003927 | 0.0009842 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1030-28_0_3_load_28 | 35 | 0.0017844 | 0.00044722 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1030-28_0_3_load_50 | 37 | 0.0045384 | 0.0011374 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1030-28_0_3_load_26 | 39 | 0.00030406 | 7.6205e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1030-28_0_3_load_77 | 40 | 0.00030666 | 7.6857e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1030-28_0_3_load_79 | 41 | 0.00065052 | 0.00016304 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1030-28_0_3_load_109 | 42 | 0.00065052 | 0.00016304 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1030-28_0_3_load_108 | 45 | 0.0005295 | 0.0001327 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1030-28_0_3_load_61 | 47 | 0.00082406 | 0.00020653 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1030-28_0_3_load_67 | 49 | 0.0010763 | 0.00026975 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1030-28_0_3_load_96 | 50 | 0.00061179 | 0.00015333 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1030-28_0_3_load_95 | 51 | 0.00043394 | 0.00010876 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1030-28_0_3_load_32 | 53 | 0.0021342 | 0.00053489 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1030-28_0_3_load_33 | 54 | 0.0021614 | 0.0005417 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1030-28_0_3_load_34 | 55 | 0.0028118 | 0.0007047 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1030-28_0_3_load_35 | 56 | 0.0014131 | 0.00035415 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1030-28_0_3_load_36 | 57 | 0.0011167 | 0.00027987 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1030-28_0_3_load_52 | 60 | 0.0045575 | 0.0011422 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1030-28_0_3_load_37 | 61 | 0.00024328 | 6.0971e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1030-28_0_3_load_38 | 62 | 0.010399 | 0.0026063 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1030-28_0_3_load_39 | 63 | 0.00068768 | 0.00017235 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1030-28_0_3_load_65 | 64 | 0.002316 | 0.00058044 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1030-28_0_3_load_118 | 66 | 0.00034882 | 8.7422e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1030-28_0_3_load_44 | 68 | 0.00024863 | 6.2313e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1030-28_0_3_load_119 | 69 | 0.00045716 | 0.00011458 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1030-28_0_3_load_117 | 70 | 0.0031786 | 0.00079664 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1030-28_0_3_load_114 | 71 | 0.0018631 | 0.00046694 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1030-28_0_3_load_111 | 74 | 0.000271 | 6.792e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1030-28_0_3_load_122 | 75 | 0.0011538 | 0.00028917 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1030-28_0_3_load_45 | 76 | 0.0018045 | 0.00045224 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1030-28_0_3_load_46 | 77 | 0.0018318 | 0.0004591 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1030-28_0_3_load_48 | 78 | 0.0010828 | 0.00027137 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1030-28_0_3_load_49 | 79 | 0.0028874 | 0.00072366 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1030-28_0_3_load_59 | 82 | 0.0010922 | 0.00027373 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1030-28_0_3_load_53 | 83 | 0.0006852 | 0.00017173 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1030-28_0_3_load_56 | 86 | 0.0005342 | 0.00013388 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1030-28_0_3_load_57 | 87 | 0.00057804 | 0.00014487 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1030-28_0_3_load_63 | 89 | 0.00055515 | 0.00013913 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1030-28_0_3_load_125 | 90 | 0.0015251 | 0.00038222 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1030-28_0_3_load_124 | 91 | 0.0015977 | 0.00040043 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1030-28_0_3_load_120 | 92 | 0.0012972 | 0.00032511 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1030-28_0_3_load_66 | 93 | 0.00314 | 0.00078695 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1030-28_0_3_load_91 | 94 | 0.00067435 | 0.00016901 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1030-28_0_3_load_115 | 95 | 0.0034643 | 0.00086824 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1030-28_0_3_load_89 | 96 | 0.0051714 | 0.0012961 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1030-28_0_3_load_80 | 97 | 0.00054231 | 0.00013592 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1030-28_0_3_load_83 | 100 | 0.0012188 | 0.00030546 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1030-28_0_3_load_84 | 101 | 0.00088572 | 0.00022198 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1030-28_0_3_load_85 | 102 | 0.0023505 | 0.0005891 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1030-28_0_3_load_87 | 104 | 0.0020632 | 0.00051709 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1030-28_0_3_load_88 | 105 | 0.00080933 | 0.00020284 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1030-28_0_3_load_90 | 106 | 0.0041743 | 0.0010462 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1030-28_0_3_load_107 | 107 | 0.00042404 | 0.00010627 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1030-28_0_3_load_106 | 108 | 0.0021496 | 0.00053873 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1030-28_0_3_load_93 | 109 | 0.0037224 | 0.00093293 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1030-28_0_3_load_99 | 110 | 0.00099996 | 0.00025061 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1030-28_0_3_load_110 | 111 | 0.00096696 | 0.00024234 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1030-28_0_3_load_103 | 112 | 0.014792 | 0.0037072 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1030-28_0_3_load_104 | 113 | 0.0048682 | 0.0012201 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1030-28_0_3_load_105 | 114 | 0.00072381 | 0.00018141 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1030-28_0_3_load_121 | 115 | 0.0013361 | 0.00033487 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1030-28_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.010532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1030-28_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0075979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1030-28_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.079372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1030-28_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.016243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1030-28_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.0095121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1030-28_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.015631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1030-28_0_3_line_6 | NAYY 4x150 SE | 3 | 7 | 0.033881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1030-28_0_3_line_7 | NAYY 4x150 SE | 4 | 8 | 0.030648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1030-28_0_3_line_8 | NAYY 4x150 SE | 5 | 9 | 0.041963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1030-28_0_3_line_9 | NAYY 4x150 SE | 5 | 10 | 0.060216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1030-28_0_3_line_10 | NAYY 4x150 SE | 7 | 18 | 0.04973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1030-28_0_3_line_11 | NAYY 4x150 SE | 8 | 20 | 0.068814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1030-28_0_3_line_12 | NAYY 4x150 SE | 9 | 16 | 0.033606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1030-28_0_3_line_13 | NAYY 4x150 SE | 9 | 17 | 0.010262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1030-28_0_3_line_14 | NAYY 4x150 SE | 10 | 21 | 0.064875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1030-28_0_3_line_15 | NAYY 4x150 SE | 11 | 12 | 0.005458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1030-28_0_3_line_16 | NAYY 4x150 SE | 11 | 13 | 0.010251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_1030-28_0_3_line_17 | NAYY 4x150 SE | 12 | 24 | 0.018512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1030-28_0_3_line_18 | NAYY 4x150 SE | 12 | 14 | 0.004621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1030-28_0_3_line_19 | NAYY 4x150 SE | 13 | 19 | 0.071314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1030-28_0_3_line_20 | NAYY 4x150 SE | 14 | 15 | 0.0044861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1030-28_0_3_line_21 | NAYY 4x150 SE | 15 | 27 | 0.01079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1030-28_0_3_line_22 | NAYY 4x150 SE | 16 | 28 | 0.041411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1030-28_0_3_line_23 | NAYY 4x150 SE | 17 | 29 | 0.020511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1030-28_0_3_line_24 | NAYY 4x150 SE | 18 | 30 | 0.03892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1030-28_0_3_line_25 | NAYY 4x150 SE | 20 | 31 | 0.025724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1030-28_0_3_line_26 | NAYY 4x150 SE | 21 | 27 | 0.051543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1030-28_0_3_line_27 | NAYY 4x150 SE | 22 | 23 | 0.0034076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1030-28_0_3_line_28 | NAYY 4x150 SE | 23 | 37 | 0.01467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1030-28_0_3_line_29 | NAYY 4x150 SE | 24 | 32 | 0.027526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_1030-28_0_3_line_30 | NAYY 4x150 SE | 25 | 26 | 0.010874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1030-28_0_3_line_31 | NAYY 4x150 SE | 26 | 32 | 0.005188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1030-28_0_3_line_32 | NAYY 4x150 SE | 28 | 111 | 0.001316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1030-28_0_3_line_33 | NAYY 4x150 SE | 29 | 110 | 0.021216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1030-28_0_3_line_34 | NAYY 4x150 SE | 30 | 68 | 0.17798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1030-28_0_3_line_35 | NAYY 4x150 SE | 31 | 39 | 0.0017447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1030-28_0_3_line_36 | NAYY 4x150 SE | 32 | 33 | 0.011609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
37 | LV_1030-28_0_3_line_37 | NAYY 4x150 SE | 32 | 34 | 0.025485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1030-28_0_3_line_38 | NAYY 4x150 SE | 33 | 41 | 0.022376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1030-28_0_3_line_39 | NAYY 4x150 SE | 33 | 42 | 0.010793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
40 | LV_1030-28_0_3_line_40 | NAYY 4x150 SE | 35 | 36 | 0.027721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1030-28_0_3_line_41 | NAYY 4x150 SE | 36 | 43 | 0.024244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1030-28_0_3_line_42 | NAYY 4x150 SE | 36 | 44 | 0.030504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1030-28_0_3_line_43 | NAYY 4x150 SE | 37 | 38 | 0.024486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1030-28_0_3_line_44 | NAYY 4x150 SE | 38 | 79 | 0.0081665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1030-28_0_3_line_45 | NAYY 4x150 SE | 38 | 76 | 0.0306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1030-28_0_3_line_46 | NAYY 4x150 SE | 39 | 40 | 0.020825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1030-28_0_3_line_47 | NAYY 4x150 SE | 42 | 45 | 0.022223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
48 | LV_1030-28_0_3_line_48 | NAYY 4x150 SE | 43 | 45 | 0.03231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_1030-28_0_3_line_49 | NAYY 4x150 SE | 43 | 46 | 0.018565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1030-28_0_3_line_50 | NAYY 4x150 SE | 43 | 47 | 0.024837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
51 | LV_1030-28_0_3_line_51 | NAYY 4x150 SE | 44 | 51 | 0.0045343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1030-28_0_3_line_52 | NAYY 4x150 SE | 44 | 52 | 0.002988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1030-28_0_3_line_53 | NAYY 4x150 SE | 46 | 48 | 0.0099857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1030-28_0_3_line_54 | NAYY 4x150 SE | 46 | 49 | 0.011887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1030-28_0_3_line_55 | NAYY 4x150 SE | 47 | 87 | 0.0077274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1030-28_0_3_line_56 | NAYY 4x150 SE | 48 | 50 | 0.021826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1030-28_0_3_line_57 | NAYY 4x150 SE | 49 | 93 | 0.0014609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1030-28_0_3_line_58 | NAYY 4x150 SE | 51 | 104 | 0.016163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1030-28_0_3_line_59 | NAYY 4x150 SE | 52 | 94 | 0.0098769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1030-28_0_3_line_60 | NAYY 4x150 SE | 53 | 54 | 0.011252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1030-28_0_3_line_61 | NAYY 4x150 SE | 53 | 55 | 0.0148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1030-28_0_3_line_62 | NAYY 4x150 SE | 54 | 56 | 0.017593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1030-28_0_3_line_63 | NAYY 4x150 SE | 56 | 57 | 0.0043821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1030-28_0_3_line_64 | NAYY 4x150 SE | 57 | 58 | 0.018544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1030-28_0_3_line_65 | NAYY 4x150 SE | 58 | 59 | 0.023991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1030-28_0_3_line_66 | NAYY 4x150 SE | 58 | 60 | 0.0071992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1030-28_0_3_line_67 | NAYY 4x150 SE | 59 | 64 | 0.0084206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1030-28_0_3_line_68 | NAYY 4x150 SE | 59 | 63 | 0.050921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1030-28_0_3_line_69 | NAYY 4x150 SE | 60 | 79 | 0.044301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1030-28_0_3_line_70 | NAYY 4x150 SE | 61 | 62 | 0.11607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1030-28_0_3_line_71 | NAYY 4x150 SE | 62 | 63 | 0.038505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1030-28_0_3_line_72 | NAYY 4x150 SE | 64 | 75 | 0.011614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1030-28_0_3_line_73 | NAYY 4x150 SE | 65 | 66 | 0.020092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1030-28_0_3_line_74 | NAYY 4x150 SE | 65 | 67 | 0.007117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1030-28_0_3_line_75 | NAYY 4x150 SE | 66 | 69 | 0.025031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1030-28_0_3_line_76 | NAYY 4x150 SE | 67 | 70 | 0.022588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1030-28_0_3_line_77 | NAYY 4x150 SE | 67 | 71 | 0.069436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1030-28_0_3_line_78 | NAYY 4x150 SE | 71 | 73 | 0.095546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1030-28_0_3_line_79 | NAYY 4x150 SE | 72 | 73 | 0.20267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1030-28_0_3_line_80 | NAYY 4x150 SE | 72 | 74 | 0.077054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1030-28_0_3_line_81 | NAYY 4x150 SE | 74 | 111 | 0.029004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1030-28_0_3_line_82 | NAYY 4x150 SE | 75 | 92 | 0.034333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1030-28_0_3_line_83 | NAYY 4x150 SE | 76 | 77 | 0.021321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1030-28_0_3_line_84 | NAYY 4x150 SE | 77 | 78 | 0.0098027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1030-28_0_3_line_85 | NAYY 4x150 SE | 78 | 80 | 0.018278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1030-28_0_3_line_86 | NAYY 4x150 SE | 80 | 81 | 0.009221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1030-28_0_3_line_87 | NAYY 4x150 SE | 81 | 82 | 0.0063337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1030-28_0_3_line_88 | NAYY 4x150 SE | 82 | 85 | 0.012871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1030-28_0_3_line_89 | NAYY 4x150 SE | 83 | 84 | 0.0068379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1030-28_0_3_line_90 | NAYY 4x150 SE | 83 | 85 | 0.013107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1030-28_0_3_line_91 | NAYY 4x150 SE | 84 | 86 | 0.010011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1030-28_0_3_line_92 | NAYY 4x150 SE | 84 | 87 | 0.014041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1030-28_0_3_line_93 | NAYY 4x150 SE | 85 | 88 | 0.012231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1030-28_0_3_line_94 | NAYY 4x150 SE | 88 | 89 | 0.019036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1030-28_0_3_line_95 | NAYY 4x150 SE | 90 | 91 | 0.007377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1030-28_0_3_line_96 | NAYY 4x150 SE | 91 | 116 | 0.013541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1030-28_0_3_line_97 | NAYY 4x150 SE | 92 | 115 | 0.003935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1030-28_0_3_line_98 | NAYY 4x150 SE | 94 | 109 | 0.006772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1030-28_0_3_line_99 | NAYY 4x150 SE | 95 | 96 | 0.018338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1030-28_0_3_line_100 | NAYY 4x150 SE | 96 | 102 | 0.059911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1030-28_0_3_line_101 | NAYY 4x150 SE | 97 | 98 | 0.010157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1030-28_0_3_line_102 | NAYY 4x150 SE | 97 | 99 | 0.020928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1030-28_0_3_line_103 | NAYY 4x150 SE | 98 | 100 | 0.0025663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1030-28_0_3_line_104 | NAYY 4x150 SE | 98 | 101 | 0.039166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1030-28_0_3_line_105 | NAYY 4x150 SE | 99 | 102 | 0.025195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1030-28_0_3_line_106 | NAYY 4x150 SE | 99 | 103 | 0.08409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1030-28_0_3_line_107 | NAYY 4x150 SE | 100 | 104 | 0.025158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1030-28_0_3_line_108 | NAYY 4x150 SE | 101 | 105 | 0.049752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1030-28_0_3_line_109 | NAYY 4x150 SE | 103 | 106 | 0.014918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1030-28_0_3_line_110 | NAYY 4x150 SE | 105 | 107 | 0.0059802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1030-28_0_3_line_111 | NAYY 4x150 SE | 107 | 108 | 0.024208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1030-28_0_3_line_112 | NAYY 4x150 SE | 108 | 114 | 0.010963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1030-28_0_3_line_113 | NAYY 4x150 SE | 112 | 113 | 0.032216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1030-28_0_3_line_114 | NAYY 4x150 SE | 113 | 114 | 0.023949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1030-28_0_3_line_115 | NAYY 4x150 SE | 115 | 116 | 0.11171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1030-28_0_3_trafo_21 | 0.25 MVA 20/0.4 kV | 117 | 13 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2661687.4148 | 1231949.9672 | 2661692.863 | 1231940.954
1 | 2661683.4844 | 1231956.4696 | 2661687.4148 | 1231949.9672
2 | 2661733.9217 | 1231873.0274 | 2661692.863 | 1231940.954
3 | 2661683.4844 | 1231956.4696 | 2661675.0783 | 1231970.3804
4 | 2661675.4189 | 1231951.4271 | 2661679.3011 | 1231953.8578 | 2661683.4844 | 1231956.4696
5 | 2661733.9217 | 1231873.0274 | 2661748.6247 | 1231878.4502
6 | 2661733.9217 | 1231873.0274 | 2661751.5716 | 1231844.0806
7 | 2661675.0783 | 1231970.3804 | 2661676.5384 | 1231971.2516 | 2661696.5826 | 1231982.2445 | 2661702.4026 | 1231984.0283
8 | 2661661.8151 | 1231916.7078 | 2661661.4241 | 1231919.3611 | 2661666.4737 | 1231932.6332 | 2661679.112 | 1231945.0835 | 2661675.4189 | 1231951.4271
9 | 2661675.4189 | 1231951.4271 | 2661665.5269 | 1231968.4134 | 2661644.1771 | 1232002.8985
10 | 2661751.5716 | 1231844.0806 | 2661765.0513 | 1231849.9021 | 2661771.8172 | 1231853.9528 | 2661777.5447 | 1231862.4512 | 2661783.5772 | 1231872.9429 | 2661787.4659 | 1231875.7754
11 | 2661761.3617 | 1231961.07 | 2661758.258 | 1231960.0034 | 2661754.5519 | 1231959.5647 | 2661750.8388 | 1231960.5379 | 2661747.1601 | 1231962.5676 | 2661744.5389 | 1231965.5869 | 2661736.6609 | 1231976.0341 | 2661733.1205 | 1231979.3328 | 2661730.4164 | 1231980.8502 | 2661727.9103 | 1231982.2696 | 2661722.0027 | 1231983.8204 | 2661713.6151 | 1231985.0008 | 2661706.9156 | 1231984.7867 | 2661702.4026 | 1231984.0283 | 2661702.4026 | 1231984.0283
12 | 2661661.8151 | 1231916.7078 | 2661666.7041 | 1231883.4597
13 | 2661661.8151 | 1231916.7078 | 2661652.6556 | 1231912.0795
14 | 2661611.1925 | 1232058.7586 | 2661637.362 | 1232013.9067 | 2661644.1771 | 1232002.8985
15 | 2661591.4504 | 1232117.5765 | 2661593.713 | 1232112.6078
16 | 2661593.713 | 1232112.6078 | 2661598.1175 | 1232103.3513
17 | 2661591.4504 | 1232117.5765 | 2661584.4019 | 1232134.6946
18 | 2661587.1365 | 1232115.8862 | 2661591.4504 | 1232117.5765
19 | 2661632.2334 | 1232040.803 | 2661620.1263 | 1232060.703 | 2661609.0327 | 1232080.4121 | 2661598.1175 | 1232103.3513
20 | 2661587.1365 | 1232115.8862 | 2661582.9583 | 1232114.253
21 | 2661587.2799 | 1232104.3666 | 2661582.9583 | 1232114.253
22 | 2661666.7041 | 1231883.4597 | 2661670.9648 | 1231854.4843 | 2661672.1956 | 1231842.4226
23 | 2661652.6556 | 1231912.0795 | 2661634.349 | 1231902.8292
24 | 2661823.7576 | 1231889.7492 | 2661788.1919 | 1231876.3042 | 2661787.4659 | 1231875.7754
25 | 2661785.6893 | 1231969.4304 | 2661761.3617 | 1231961.07
26 | 2661611.1925 | 1232058.7586 | 2661599.0148 | 1232079.63 | 2661587.3949 | 1232104.1034 | 2661587.2799 | 1232104.3666
27 | 2661629.2201 | 1232141.0122 | 2661632.1664 | 1232142.7243
28 | 2661643.0888 | 1232151.8365 | 2661640.76 | 1232147.7181 | 2661632.1664 | 1232142.7243
29 | 2661575.8952 | 1232160.8325 | 2661580.9793 | 1232143.0069 | 2661584.4019 | 1232134.6946
30 | 2661571.2449 | 1232158.7274 | 2661574.7312 | 1232148.4276
31 | 2661571.2449 | 1232158.7274 | 2661574.6117 | 1232159.7407 | 2661575.8952 | 1232160.8325
32 | 2661672.4663 | 1231841.1347 | 2661672.1956 | 1231842.4226 | 2661672.1956 | 1231842.4226
33 | 2661615.4136 | 1231893.2609 | 2661618.0319 | 1231894.5841 | 2661634.349 | 1231902.8292
34 | 2661823.7576 | 1231889.7492 | 2662001.6848 | 1231885.5921
35 | 2661787.3392 | 1231969.9975 | 2661785.6893 | 1231969.4304
36 | 2661572.7052 | 1232171.9957 | 2661575.8952 | 1232160.8325
37 | 2661575.8952 | 1232160.8325 | 2661577.0663 | 1232161.8231 | 2661583.6964 | 1232168.7184 | 2661588.99 | 1232177.4345 | 2661590.7661 | 1232181.2264
38 | 2661572.7052 | 1232171.9957 | 2661575.5632 | 1232170.2241 | 2661577.959 | 1232169.9376 | 2661580.5633 | 1232170.7318 | 2661582.4466 | 1232172.4079 | 2661588.0693 | 1232182.2745
39 | 2661572.7052 | 1232171.9957 | 2661570.5507 | 1232175.2977 | 2661569.1576 | 1232178.9301 | 2661568.3965 | 1232181.7905
40 | 2661552.6042 | 1232216.2387 | 2661559.8219 | 1232197.112 | 2661561.8979 | 1232190.1361
41 | 2661552.6042 | 1232216.2387 | 2661547.4165 | 1232228.0038 | 2661550.398 | 1232229.658 | 2661557.3698 | 1232233.5326
42 | 2661552.6042 | 1232216.2387 | 2661549.3154 | 1232215.015 | 2661531.0154 | 1232200.8942 | 2661527.9285 | 1232198.4495
43 | 2661656.2489 | 1232172.2169 | 2661650.0259 | 1232165.5035 | 2661644.9465 | 1232155.1219 | 2661643.0888 | 1232151.8365
44 | 2661656.2489 | 1232172.2169 | 2661663.778 | 1232169.0538
45 | 2661656.2489 | 1232172.2169 | 2661651.7279 | 1232179.5526 | 2661644.5802 | 1232200.3415
46 | 2661807.0333 | 1231976.7655 | 2661787.3392 | 1231969.9975
47 | 2661562.2705 | 1232203.1428 | 2661564.5168 | 1232196.3713 | 2661568.3965 | 1232181.7905
48 | 2661557.3698 | 1232233.5326 | 2661561.1855 | 1232225.5669 | 2661558.765 | 1232220.1939 | 2661558.6243 | 1232216.2343 | 2661559.3893 | 1232211.8283 | 2661562.2705 | 1232203.1428
49 | 2661557.3698 | 1232233.5326 | 2661553.6782 | 1232241.2217 | 2661547.8775 | 1232243.452 | 2661545.6011 | 1232245.363 | 2661545.0714 | 1232246.058
50 | 2661557.3698 | 1232233.5326 | 2661579.064 | 1232245.6256
51 | 2661527.9285 | 1232198.4495 | 2661524.3742 | 1232195.634
52 | 2661526.0492 | 1232200.776 | 2661527.9285 | 1232198.4495
53 | 2661535.8968 | 1232242.116 | 2661540.1939 | 1232243.9617 | 2661545.0714 | 1232246.058
54 | 2661545.0714 | 1232246.058 | 2661541.4405 | 1232250.8124 | 2661538.9301 | 1232256.1565
55 | 2661579.064 | 1232245.6256 | 2661585.8136 | 1232249.388
56 | 2661535.8968 | 1232242.116 | 2661526.8738 | 1232261.9898
57 | 2661538.309 | 1232257.4788 | 2661538.9301 | 1232256.1565
58 | 2661524.3742 | 1232195.634 | 2661511.7046 | 1232185.5978
59 | 2661526.0492 | 1232200.776 | 2661519.8377 | 1232208.4554
60 | 2661699.0448 | 1232216.7793 | 2661697.5054 | 1232220.1538 | 2661694.7179 | 1232227.1625
61 | 2661689.2481 | 1232240.9151 | 2661694.7179 | 1232227.1625
62 | 2661699.0448 | 1232216.7793 | 2661706.3462 | 1232200.7733
63 | 2661706.3462 | 1232200.7733 | 2661708.1649 | 1232196.7865
64 | 2661712.745 | 1232178.9184 | 2661710.1203 | 1232192.5 | 2661708.1649 | 1232196.7865
65 | 2661736.3407 | 1232183.2772 | 2661728.0639 | 1232182.5686 | 2661720.3044 | 1232180.8981 | 2661712.745 | 1232178.9184
66 | 2661712.745 | 1232178.9184 | 2661705.9603 | 1232176.5108
67 | 2661736.3407 | 1232183.2772 | 2661744.7578 | 1232183.5181
68 | 2661736.3407 | 1232183.2772 | 2661736.9381 | 1232178.9806 | 2661749.0093 | 1232153.3892 | 2661755.8939 | 1232136.4467
69 | 2661705.9603 | 1232176.5108 | 2661690.6998 | 1232171.0956 | 2661676.4758 | 1232166.2783 | 2661667.4062 | 1232167.5295 | 2661663.778 | 1232169.0538
70 | 2661769.8886 | 1232100.5781 | 2661777.6687 | 1232080.0167 | 2661780.0946 | 1232074.6606 | 2661790.6487 | 1232057.3701 | 2661797.3052 | 1232037.682 | 2661810.7826 | 1232005.0785 | 2661815.0024 | 1231993.9693
71 | 2661769.8886 | 1232100.5781 | 2661762.0337 | 1232121.3369 | 2661755.8939 | 1232136.4467
72 | 2661756.3668 | 1232183.8503 | 2661744.7578 | 1232183.5181
73 | 2661911.9937 | 1231570.0029 | 2661901.5929 | 1231587.1931
74 | 2661915.7449 | 1231563.9491 | 2661911.9937 | 1231570.0029
75 | 2661888.6354 | 1231608.6092 | 2661901.5929 | 1231587.1931
76 | 2661915.7449 | 1231563.9491 | 2661927.4144 | 1231544.6092
77 | 2661915.7449 | 1231563.9491 | 2661891.4723 | 1231554.557 | 2661879.8086 | 1231553.9242 | 2661848.1512 | 1231551.8025
78 | 2661754.6367 | 1231543.9612 | 2661758.6509 | 1231548.2946 | 2661768.2333 | 1231549.5282 | 2661784.5836 | 1231549.5425 | 2661824.0332 | 1231550.1862 | 2661848.1512 | 1231551.8025
79 | 2661693.5978 | 1231737.2204 | 2661754.6367 | 1231543.9612
80 | 2661693.5978 | 1231737.2204 | 2661691.6413 | 1231749.8861 | 2661678.4309 | 1231812.7508
81 | 2661678.4309 | 1231812.7508 | 2661672.4663 | 1231841.1347
82 | 2661790.6484 | 1232185.6321 | 2661768.0595 | 1232184.1849 | 2661756.3668 | 1232183.8503
83 | 2661637.2778 | 1232220.368 | 2661640.7499 | 1232211.4819 | 2661644.5802 | 1232200.3415
84 | 2661633.7102 | 1232229.4985 | 2661637.2778 | 1232220.368
85 | 2661618.8528 | 1232239.0396 | 2661629.306 | 1232235.0564 | 2661633.7102 | 1232229.4985
86 | 2661618.8528 | 1232239.0396 | 2661618.7938 | 1232243.2751 | 2661619.6364 | 1232248.187
87 | 2661619.6364 | 1232248.187 | 2661618.707 | 1232254.4522
88 | 2661614.773 | 1232266.6376 | 2661618.1872 | 1232257.9562 | 2661618.707 | 1232254.4522
89 | 2661598.0781 | 1232256.2245 | 2661604.2989 | 1232259.0632
90 | 2661614.773 | 1232266.6376 | 2661609.2473 | 1232261.3213 | 2661604.2989 | 1232259.0632
91 | 2661598.0781 | 1232256.2245 | 2661603.8346 | 1232248.0343
92 | 2661598.0781 | 1232256.2245 | 2661585.8136 | 1232249.388
93 | 2661614.773 | 1232266.6376 | 2661620.1413 | 1232277.6337
94 | 2661620.1413 | 1232277.6337 | 2661624.9283 | 1232276.7717 | 2661628.3778 | 1232277.1076 | 2661639.0208 | 1232278.2666
95 | 2661765.2089 | 1232290.7271 | 2661760.0987 | 1232295.8863 | 2661760.0209 | 1232295.9713
96 | 2661774.738 | 1232281.1065 | 2661765.2089 | 1232290.7271
97 | 2661790.6484 | 1232185.6321 | 2661794.5754 | 1232185.8837
98 | 2661515.5789 | 1232213.7206 | 2661519.8377 | 1232208.4554
99 | 2661399.8787 | 1232238.6991 | 2661403.4883 | 1232233.275 | 2661409.2709 | 1232222.963
100 | 2661439.3212 | 1232171.1894 | 2661435.0406 | 1232177.0086 | 2661409.2709 | 1232222.963
101 | 2661488.9394 | 1232169.8165 | 2661479.7533 | 1232165.484
102 | 2661460.1124 | 1232158.7335 | 2661464.067 | 1232159.2858 | 2661469.6331 | 1232160.711 | 2661479.7533 | 1232165.484
103 | 2661488.9394 | 1232169.8165 | 2661491.0873 | 1232171.221
104 | 2661488.9394 | 1232169.8165 | 2661498.5651 | 1232141.8867 | 2661501.4599 | 1232132.7086
105 | 2661460.1124 | 1232158.7335 | 2661453.195 | 1232159.8294 | 2661446.4019 | 1232163.5616 | 2661441.3231 | 1232168.4679 | 2661439.3212 | 1232171.1894
106 | 2661460.1124 | 1232158.7335 | 2661457.8156 | 1232154.5626 | 2661454.7003 | 1232151.1949 | 2661434.9237 | 1232139.2383 | 2661411.9162 | 1232131.4178 | 2661385.4688 | 1232123.7842
107 | 2661491.0873 | 1232171.221 | 2661505.2309 | 1232180.4697 | 2661511.7046 | 1232185.5978
108 | 2661507.0309 | 1232084.2084 | 2661509.5818 | 1232101.0295 | 2661505.5489 | 1232119.7444 | 2661501.4599 | 1232132.7086
109 | 2661385.4688 | 1232123.7842 | 2661370.9706 | 1232120.2714
110 | 2661507.0309 | 1232084.2084 | 2661506.1343 | 1232078.2958
111 | 2661497.4858 | 1232055.7293 | 2661505.8885 | 1232076.6754 | 2661506.1343 | 1232078.2958
112 | 2661492.6432 | 1232045.8996 | 2661493.0602 | 1232046.7232 | 2661496.9488 | 1232054.3906 | 2661497.4858 | 1232055.7293
113 | 2661481.4504 | 1232024.7479 | 2661473.9842 | 1232013.1152 | 2661465.7295 | 1232008.0488 | 2661457.6417 | 1232004.8225
114 | 2661492.6432 | 1232045.8996 | 2661483.7469 | 1232028.326 | 2661481.4504 | 1232024.7479
115 | 2661774.738 | 1232281.1065 | 2661778.2781 | 1232271.2702 | 2661793.2028 | 1232238.5149 | 2661810.2587 | 1232211.2744 | 2661810.9198 | 1232200.8633 | 2661804.4129 | 1232191.6119 | 2661794.5754 | 1232185.8837

## bus_geodata
| x | y | coords
0 | 2661687.4148 | 1231949.9672
1 | 2661692.863 | 1231940.954
2 | 2661683.4844 | 1231956.4696
3 | 2661733.9217 | 1231873.0273
4 | 2661675.0783 | 1231970.3804
5 | 2661675.4189 | 1231951.4271
6 | 2661748.6247 | 1231878.4502
7 | 2661751.5716 | 1231844.0806
8 | 2661702.4026 | 1231984.0283
9 | 2661661.8151 | 1231916.7078
10 | 2661644.1771 | 1232002.8985
11 | 2661593.713 | 1232112.6078
12 | 2661591.4504 | 1232117.5765
13 | 2661598.1175 | 1232103.3513
14 | 2661587.1365 | 1232115.8862
15 | 2661582.9583 | 1232114.253
16 | 2661666.7041 | 1231883.4597
17 | 2661652.6556 | 1231912.0795
18 | 2661787.4659 | 1231875.7753
19 | 2661632.2334 | 1232040.803
20 | 2661761.3617 | 1231961.07
21 | 2661611.1925 | 1232058.7586
22 | 2661629.2201 | 1232141.0122
23 | 2661632.1664 | 1232142.7243
24 | 2661584.4019 | 1232134.6946
25 | 2661574.7312 | 1232148.4276
26 | 2661571.2449 | 1232158.7274
27 | 2661587.2799 | 1232104.3666
28 | 2661672.1956 | 1231842.4226
29 | 2661634.349 | 1231902.8292
30 | 2661823.7576 | 1231889.7492
31 | 2661785.6893 | 1231969.4304
32 | 2661575.8952 | 1232160.8325
33 | 2661572.7052 | 1232171.9957
34 | 2661590.7661 | 1232181.2264
35 | 2661561.8979 | 1232190.1361
36 | 2661552.6042 | 1232216.2387
37 | 2661643.0888 | 1232151.8365
38 | 2661656.2489 | 1232172.2169
39 | 2661787.3392 | 1231969.9975
40 | 2661807.0333 | 1231976.7655
41 | 2661588.0693 | 1232182.2745
42 | 2661568.3965 | 1232181.7905
43 | 2661557.3698 | 1232233.5326
44 | 2661527.9285 | 1232198.4495
45 | 2661562.2705 | 1232203.1428
46 | 2661545.0714 | 1232246.058
47 | 2661579.064 | 1232245.6256
48 | 2661535.8968 | 1232242.116
49 | 2661538.9301 | 1232256.1565
50 | 2661526.8738 | 1232261.9898
51 | 2661524.3742 | 1232195.634
52 | 2661526.0492 | 1232200.776
53 | 2661694.7179 | 1232227.1625
54 | 2661699.0448 | 1232216.7793
55 | 2661689.2481 | 1232240.9151
56 | 2661706.3462 | 1232200.7733
57 | 2661708.1649 | 1232196.7865
58 | 2661712.745 | 1232178.9184
59 | 2661736.3407 | 1232183.2772
60 | 2661705.9603 | 1232176.5108
61 | 2661815.0024 | 1231993.9693
62 | 2661769.8886 | 1232100.5781
63 | 2661755.8939 | 1232136.4467
64 | 2661744.7578 | 1232183.5181
65 | 2661911.9937 | 1231570.0029
66 | 2661901.5929 | 1231587.1931
67 | 2661915.7449 | 1231563.9491
68 | 2662001.6848 | 1231885.5921
69 | 2661888.6354 | 1231608.6092
70 | 2661927.4144 | 1231544.6092
71 | 2661848.1512 | 1231551.8025
72 | 2661693.5978 | 1231737.2204
73 | 2661754.6367 | 1231543.9612
74 | 2661678.4309 | 1231812.7508
75 | 2661756.3668 | 1232183.8503
76 | 2661644.5802 | 1232200.3415
77 | 2661637.2778 | 1232220.368
78 | 2661633.7102 | 1232229.4985
79 | 2661663.778 | 1232169.0538
80 | 2661618.8528 | 1232239.0396
81 | 2661619.6364 | 1232248.187
82 | 2661618.707 | 1232254.4522
83 | 2661604.2989 | 1232259.0632
84 | 2661598.0781 | 1232256.2245
85 | 2661614.773 | 1232266.6376
86 | 2661603.8346 | 1232248.0343
87 | 2661585.8136 | 1232249.388
88 | 2661620.1413 | 1232277.6337
89 | 2661639.0208 | 1232278.2666
90 | 2661760.0209 | 1232295.9713
91 | 2661765.2089 | 1232290.7271
92 | 2661790.6484 | 1232185.6321
93 | 2661538.309 | 1232257.4788
94 | 2661519.8377 | 1232208.4554
95 | 2661399.8787 | 1232238.6991
96 | 2661409.2709 | 1232222.963
97 | 2661479.7533 | 1232165.484
98 | 2661488.9394 | 1232169.8165
99 | 2661460.1124 | 1232158.7335
100 | 2661491.0873 | 1232171.221
101 | 2661501.4599 | 1232132.7086
102 | 2661439.3212 | 1232171.1894
103 | 2661385.4688 | 1232123.7842
104 | 2661511.7046 | 1232185.5978
105 | 2661507.0309 | 1232084.2084
106 | 2661370.9706 | 1232120.2714
107 | 2661506.1343 | 1232078.2958
108 | 2661497.4858 | 1232055.7293
109 | 2661515.5789 | 1232213.7206
110 | 2661615.4136 | 1231893.2609
111 | 2661672.4663 | 1231841.1347
112 | 2661457.6417 | 1232004.8225
113 | 2661481.4504 | 1232024.7479
114 | 2661492.6432 | 1232045.8996
115 | 2661794.5754 | 1232185.8837
116 | 2661774.738 | 1232281.1065
117 | 2661593.713 | 1232112.6078

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99063 | -0.065714 | 0.00099023 | 0.00024817
1 | 0.99059 | -0.066038 | 0.00035605 | 8.9234e-05
2 | 0.99068 | -0.065403 | 0 | 0
3 | 0.99029 | -0.068192 | 0 | 0
4 | 0.9905 | -0.066652 | 0 | 0
5 | 0.99083 | -0.064283 | 0 | 0
6 | 0.99025 | -0.068434 | 0.0015166 | 0.0003801
7 | 0.99023 | -0.068587 | 0 | 0
8 | 0.99017 | -0.06901 | 0.0062371 | 0.0015632
9 | 0.9901 | -0.069492 | 0 | 0
10 | 0.99289 | -0.049749 | 0.0025666 | 0.00064326
11 | 0.99887 | -0.0077562 | 0 | 0
12 | 0.99827 | -0.011893 | 0 | 0
13 | 1 | 0 | -0.16386 | -0.041211
14 | 0.99808 | -0.013275 | 0 | 0
15 | 0.99788 | -0.014617 | 0.00090016 | 0.0002256
16 | 0.98965 | -0.072662 | 0.00022167 | 5.5555e-05
17 | 0.99005 | -0.0698 | 0.0015192 | 0.00038074
18 | 0.99015 | -0.069164 | 0.00040365 | 0.00010116
19 | 0.99908 | -0.006443 | 0.0090407 | 0.0022658
20 | 0.99004 | -0.069934 | 0.00030223 | 7.5746e-05
21 | 0.99534 | -0.032475 | 0.0020499 | 0.00051376
22 | 0.97572 | -0.17021 | 0.0020694 | 0.00051864
23 | 0.97573 | -0.17013 | 0.0015599 | 0.00039094
24 | 0.99664 | -0.023184 | 0.0029913 | 0.00074968
25 | 0.9942 | -0.04008 | 0.002811 | 0.0007045
26 | 0.99424 | -0.039772 | 0 | 0
27 | 0.99744 | -0.017749 | 0.00052714 | 0.00013211
28 | 0.98911 | -0.076476 | 0.0018941 | 0.00047472
29 | 0.99001 | -0.070096 | 0.00041611 | 0.00010429
30 | 0.99011 | -0.069455 | 0.00046504 | 0.00011655
31 | 0.99 | -0.070199 | 0.00039727 | 9.9565e-05
32 | 0.99426 | -0.039624 | 0 | 0
33 | 0.99331 | -0.046186 | 0 | 0
34 | 0.99412 | -0.040635 | 0.003927 | 0.0009842
35 | 0.98621 | -0.095851 | 0.0017844 | 0.00044722
36 | 0.98629 | -0.095343 | 0 | 0
37 | 0.97581 | -0.16958 | 0.0045384 | 0.0011374
38 | 0.9761 | -0.16748 | 0 | 0
39 | 0.99 | -0.070209 | 0.00030406 | 7.6205e-05
40 | 0.98999 | -0.070275 | 0.00030666 | 7.6857e-05
41 | 0.99329 | -0.046333 | 0.00065052 | 0.00016304
42 | 0.99244 | -0.052261 | 0.00065052 | 0.00016304
43 | 0.98806 | -0.082852 | 0 | 0
44 | 0.98413 | -0.11056 | 0 | 0
45 | 0.99065 | -0.06473 | 0.0005295 | 0.0001327
46 | 0.98793 | -0.08377 | 0 | 0
47 | 0.98706 | -0.089825 | 0.00082406 | 0.00020653
48 | 0.98792 | -0.083833 | 0 | 0
49 | 0.98786 | -0.084282 | 0.0010763 | 0.00026975
50 | 0.9879 | -0.083969 | 0.00061179 | 0.00015333
51 | 0.98384 | -0.11262 | 0.00043394 | 0.00010876
52 | 0.98411 | -0.1107 | 0 | 0
53 | 0.97249 | -0.19339 | 0.0021342 | 0.00053489
54 | 0.97257 | -0.1928 | 0.0021614 | 0.0005417
55 | 0.97243 | -0.19383 | 0.0028118 | 0.0007047
56 | 0.97276 | -0.19148 | 0.0014131 | 0.00035415
57 | 0.97281 | -0.19109 | 0.0011167 | 0.00027987
58 | 0.97307 | -0.1892 | 0 | 0
59 | 0.97235 | -0.19441 | 0 | 0
60 | 0.97339 | -0.18691 | 0.0045575 | 0.0011422
61 | 0.97086 | -0.20516 | 0.00024328 | 6.0971e-05
62 | 0.9709 | -0.20486 | 0.010399 | 0.0026063
63 | 0.9715 | -0.20052 | 0.00068768 | 0.00017235
64 | 0.97224 | -0.19523 | 0.002316 | 0.00058044
65 | 0.98526 | -0.1039 | 0 | 0
66 | 0.98524 | -0.10407 | 0.00034882 | 8.7422e-05
67 | 0.98527 | -0.10384 | 0 | 0
68 | 0.99005 | -0.069921 | 0.00024863 | 6.2313e-05
69 | 0.98522 | -0.10419 | 0.00045716 | 0.00011458
70 | 0.98517 | -0.10458 | 0.0031786 | 0.00079664
71 | 0.98567 | -0.10099 | 0.0018631 | 0.00046694
72 | 0.98819 | -0.083036 | 0 | 0
73 | 0.98648 | -0.095237 | 0 | 0
74 | 0.98884 | -0.078398 | 0.000271 | 6.792e-05
75 | 0.97212 | -0.19608 | 0.0011538 | 0.00028917
76 | 0.97815 | -0.15281 | 0.0018045 | 0.00045224
77 | 0.97964 | -0.14222 | 0.0018318 | 0.0004591
78 | 0.98035 | -0.13718 | 0.0010828 | 0.00027137
79 | 0.97565 | -0.17071 | 0.0028874 | 0.00072366
80 | 0.9817 | -0.12759 | 0 | 0
81 | 0.98239 | -0.12277 | 0 | 0
82 | 0.98285 | -0.11945 | 0.0010922 | 0.00027373
83 | 0.98483 | -0.10554 | 0.0006852 | 0.00017173
84 | 0.98536 | -0.10181 | 0 | 0
85 | 0.98383 | -0.11259 | 0 | 0
86 | 0.98535 | -0.10187 | 0.0005342 | 0.00013388
87 | 0.98645 | -0.094106 | 0.00057804 | 0.00014487
88 | 0.98382 | -0.11266 | 0 | 0
89 | 0.9838 | -0.11277 | 0.00055515 | 0.00013913
90 | 0.97121 | -0.20262 | 0.0015251 | 0.00038222
91 | 0.97123 | -0.20251 | 0.0015977 | 0.00040043
92 | 0.97183 | -0.19818 | 0.0012972 | 0.00032511
93 | 0.98785 | -0.084329 | 0.00314 | 0.00078695
94 | 0.98405 | -0.11114 | 0.00067435 | 0.00016901
95 | 0.97919 | -0.14569 | 0.0034643 | 0.00086824
96 | 0.97929 | -0.14503 | 0.0051714 | 0.0012961
97 | 0.9809 | -0.13347 | 0.00054231 | 0.00013592
98 | 0.98114 | -0.13182 | 0 | 0
99 | 0.98044 | -0.13677 | 0 | 0
100 | 0.98129 | -0.13074 | 0.0012188 | 0.00030546
101 | 0.97973 | -0.14185 | 0.00088572 | 0.00022198
102 | 0.98004 | -0.13965 | 0.0023505 | 0.0005891
103 | 0.97993 | -0.14042 | 0 | 0
104 | 0.98281 | -0.11991 | 0.0020632 | 0.00051709
105 | 0.978 | -0.15417 | 0.00080933 | 0.00020284
106 | 0.97984 | -0.14107 | 0.0041743 | 0.0010462
107 | 0.9778 | -0.1556 | 0.00042404 | 0.00010627
108 | 0.977 | -0.16131 | 0.0021496 | 0.00053873
109 | 0.98401 | -0.1114 | 0.0037224 | 0.00093293
110 | 0.98998 | -0.070312 | 0.00099996 | 0.00025061
111 | 0.9891 | -0.076572 | 0.00096696 | 0.00024234
112 | 0.97529 | -0.17357 | 0.014792 | 0.0037072
113 | 0.97599 | -0.16857 | 0.0048682 | 0.0012201
114 | 0.97667 | -0.16364 | 0.00072381 | 0.00018141
115 | 0.9718 | -0.19836 | 0.0013361 | 0.00033487
116 | 0.97129 | -0.20206 | 0 | 0
117 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0029911 | 0.00074458 | -0.002991 | -0.00074467 | 1.3256e-07 | -8.4604e-08 | 0.0044912 | 0.0044912 | 0.0044912 | 0.99063 | -0.065714 | 0.99059 | -0.066038 | 1.6634
1 | -0.0039814 | -0.00099276 | 0.0039815 | 0.00099272 | 1.6946e-07 | -3.2647e-08 | 0.0059786 | 0.0059785 | 0.0059786 | 0.99063 | -0.065714 | 0.99068 | -0.065403 | 2.2143
2 | 0.002635 | 0.00065543 | -0.0026342 | -0.00065616 | 7.7532e-07 | -7.2327e-07 | 0.0039564 | 0.0039567 | 0.0039567 | 0.99059 | -0.066038 | 0.99029 | -0.068192 | 1.4655
3 | 0.0075513 | 0.001891 | -0.00755 | -0.0018907 | 1.3038e-06 | 2.9235e-07 | 0.011342 | 0.011342 | 0.011342 | 0.99068 | -0.065403 | 0.9905 | -0.066652 | 4.2006
4 | -0.011533 | -0.0028837 | 0.011535 | 0.0028842 | 1.7806e-06 | 5.6235e-07 | 0.01732 | 0.01732 | 0.01732 | 0.99068 | -0.065403 | 0.99083 | -0.064283 | 6.4149
5 | 0.0015167 | 0.00037992 | -0.0015166 | -0.0003801 | 5.0657e-08 | -1.8161e-07 | 0.0022789 | 0.002279 | 0.002279 | 0.99029 | -0.068192 | 0.99025 | -0.068434 | 0.84407
6 | 0.0011175 | 0.00027623 | -0.0011174 | -0.00027665 | 5.9521e-08 | -4.1298e-07 | 0.0016778 | 0.001678 | 0.001678 | 0.99029 | -0.068192 | 0.99023 | -0.068587 | 0.62147
7 | 0.00755 | 0.0018907 | -0.0075475 | -0.0018901 | 2.4601e-06 | 5.5185e-07 | 0.011342 | 0.011342 | 0.011342 | 0.9905 | -0.066652 | 0.99017 | -0.06901 | 4.2007
8 | 0.012176 | 0.0030478 | -0.012168 | -0.0030449 | 8.7546e-06 | 2.8271e-06 | 0.018285 | 0.018285 | 0.018285 | 0.99083 | -0.064283 | 0.9901 | -0.069492 | 6.7722
9 | -0.023711 | -0.005932 | 0.023759 | 0.0059496 | 4.7633e-05 | 1.7543e-05 | 0.035605 | 0.035605 | 0.035605 | 0.99083 | -0.064283 | 0.99289 | -0.049749 | 13.187
10 | 0.0011174 | 0.00027665 | -0.0011174 | -0.00027725 | 8.7385e-08 | -6.0608e-07 | 0.001678 | 0.0016782 | 0.0016782 | 0.99023 | -0.068587 | 0.99015 | -0.069164 | 0.62156
11 | 0.0013104 | 0.00032695 | -0.0013103 | -0.00032777 | 1.6647e-07 | -8.2098e-07 | 0.0019688 | 0.0019691 | 0.0019691 | 0.99017 | -0.06901 | 0.99004 | -0.069934 | 0.7293
12 | 0.0092321 | 0.0023099 | -0.009228 | -0.0023088 | 4.0362e-06 | 1.1204e-06 | 0.013873 | 0.013874 | 0.013874 | 0.9901 | -0.069492 | 0.98965 | -0.072662 | 5.1384
13 | 0.0029354 | 0.00073505 | -0.0029353 | -0.00073514 | 1.2462e-07 | -8.4044e-08 | 0.0044114 | 0.0044115 | 0.0044115 | 0.9901 | -0.069492 | 0.99005 | -0.0698 | 1.6339
14 | -0.026325 | -0.0065928 | 0.026388 | 0.0066162 | 6.3006e-05 | 2.3392e-05 | 0.039451 | 0.039451 | 0.039451 | 0.99289 | -0.049749 | 0.99534 | -0.032475 | 14.6116
15 | 0.15385 | 0.038879 | -0.15376 | -0.038844 | 8.9535e-05 | 3.4294e-05 | 0.2293 | 0.2293 | 0.2293 | 0.99887 | -0.0077562 | 0.99827 | -0.011893 | 42.4629
16 | -0.15385 | -0.038879 | 0.15402 | 0.038943 | 0.00016816 | 6.4408e-05 | 0.2293 | 0.2293 | 0.2293 | 0.99887 | -0.0077562 | 1 | 0 | 42.4629
17 | 0.12381 | 0.031326 | -0.12361 | -0.031251 | 0.00019694 | 7.5265e-05 | 0.18466 | 0.18466 | 0.18466 | 0.99827 | -0.011893 | 0.99664 | -0.023184 | 34.1955
18 | 0.029948 | 0.0075183 | -0.029942 | -0.0075162 | 5.747e-06 | 2.15e-06 | 0.044644 | 0.044644 | 0.044644 | 0.99827 | -0.011893 | 0.99808 | -0.013275 | 16.5348
19 | 0.0090488 | 0.002268 | -0.0090407 | -0.0022658 | 8.068e-06 | 2.1684e-06 | 0.013465 | 0.013465 | 0.013465 | 1 | 0 | 0.99908 | -0.006443 | 4.9871
20 | 0.029942 | 0.0075162 | -0.029936 | -0.0075141 | 5.5793e-06 | 2.0872e-06 | 0.044644 | 0.044644 | 0.044644 | 0.99808 | -0.013275 | 0.99788 | -0.014617 | 16.5348
21 | 0.029036 | 0.0072885 | -0.029023 | -0.0072838 | 1.2624e-05 | 4.7146e-06 | 0.043302 | 0.043302 | 0.043302 | 0.99788 | -0.014617 | 0.99744 | -0.017749 | 16.0377
22 | 0.0090064 | 0.0022532 | -0.0090016 | -0.0022519 | 4.7377e-06 | 1.2904e-06 | 0.01354 | 0.013541 | 0.013541 | 0.98965 | -0.072662 | 0.98911 | -0.076476 | 5.015
23 | 0.0014162 | 0.0003544 | -0.0014161 | -0.00035464 | 5.7974e-08 | -2.4146e-07 | 0.0021282 | 0.0021283 | 0.0021283 | 0.99005 | -0.0698 | 0.99001 | -0.070096 | 0.78827
24 | 0.00071371 | 0.00017609 | -0.00071368 | -0.00017658 | 2.7893e-08 | -4.8985e-07 | 0.0010716 | 0.0010718 | 0.0010718 | 0.99015 | -0.069164 | 0.99011 | -0.069455 | 0.39695
25 | 0.001008 | 0.00025202 | -0.001008 | -0.00025234 | 3.6838e-08 | -3.1661e-07 | 0.0015148 | 0.001515 | 0.001515 | 0.99004 | -0.069934 | 0.99 | -0.070199 | 0.5611
26 | -0.028438 | -0.00713 | 0.028496 | 0.0071517 | 5.8137e-05 | 2.1689e-05 | 0.042516 | 0.042515 | 0.042516 | 0.99534 | -0.032475 | 0.99744 | -0.017749 | 15.7465
27 | -0.0020694 | -0.00051864 | 0.0020694 | 0.00051861 | 2.1178e-08 | -3.4416e-08 | 0.0031559 | 0.0031559 | 0.0031559 | 0.97572 | -0.17021 | 0.97573 | -0.17013 | 1.1689
28 | -0.0036293 | -0.00090955 | 0.0036296 | 0.00090947 | 2.8043e-07 | -7.5395e-08 | 0.0055348 | 0.0055347 | 0.0055348 | 0.97573 | -0.17013 | 0.97581 | -0.16958 | 2.0499
29 | 0.12062 | 0.030501 | -0.12034 | -0.030395 | 0.00027884 | 0.00010653 | 0.18019 | 0.18019 | 0.18019 | 0.99664 | -0.023184 | 0.99426 | -0.039624 | 33.3685
30 | -0.002811 | -0.0007045 | 0.0028111 | 0.00070441 | 1.201e-07 | -9.4819e-08 | 0.0042072 | 0.0042072 | 0.0042072 | 0.9942 | -0.04008 | 0.99424 | -0.039772 | 1.5582
31 | -0.0028111 | -0.00070441 | 0.0028112 | 0.00070436 | 5.7301e-08 | -4.5243e-08 | 0.0042072 | 0.0042072 | 0.0042072 | 0.99424 | -0.039772 | 0.99426 | -0.039624 | 1.5582
32 | 0.0071075 | 0.0017772 | -0.0071074 | -0.0017772 | 9.3861e-08 | 1.9209e-08 | 0.010691 | 0.010691 | 0.010691 | 0.98911 | -0.076476 | 0.9891 | -0.076572 | 3.9596
33 | 0.00099999 | 0.00025035 | -0.00099996 | -0.00025061 | 2.9904e-08 | -2.6129e-07 | 0.0015029 | 0.001503 | 0.001503 | 0.99001 | -0.070096 | 0.98998 | -0.070312 | 0.55667
34 | 0.00024865 | 6.003e-05 | -0.00024863 | -6.2313e-05 | 1.5475e-08 | -2.2829e-06 | 0.00037289 | 0.00037369 | 0.00037369 | 0.99011 | -0.069455 | 0.99005 | -0.069921 | 0.1384
35 | 0.00061073 | 0.00015277 | -0.00061073 | -0.0001528 | 9.1715e-10 | -2.2081e-08 | 0.00091785 | 0.00091786 | 0.00091786 | 0.99 | -0.070199 | 0.99 | -0.070209 | 0.33995
36 | 0.11361 | 0.028706 | -0.1135 | -0.028666 | 0.00010481 | 4.0009e-05 | 0.1701 | 0.17011 | 0.17011 | 0.99426 | -0.039624 | 0.99331 | -0.046186 | 31.5009
37 | 0.0039275 | 0.00098408 | -0.003927 | -0.0009842 | 5.4943e-07 | -1.1914e-07 | 0.0058779 | 0.005878 | 0.005878 | 0.99426 | -0.039624 | 0.99412 | -0.040635 | 2.177
38 | 0.00065054 | 0.00016275 | -0.00065052 | -0.00016304 | 1.3259e-08 | -2.8453e-07 | 0.00097442 | 0.00097452 | 0.00097452 | 0.99331 | -0.046186 | 0.99329 | -0.046333 | 0.36093
39 | 0.11285 | 0.028503 | -0.11275 | -0.028467 | 9.6326e-05 | 3.6769e-05 | 0.16913 | 0.16913 | 0.16913 | 0.99331 | -0.046186 | 0.99244 | -0.052261 | 31.3205
40 | -0.0017844 | -0.00044722 | 0.0017846 | 0.00044691 | 1.2539e-07 | -3.0553e-07 | 0.0026924 | 0.0026923 | 0.0026924 | 0.98621 | -0.095851 | 0.98629 | -0.095343 | 0.99718
41 | -0.050635 | -0.012735 | 0.050723 | 0.012768 | 8.8324e-05 | 3.3661e-05 | 0.076409 | 0.076409 | 0.076409 | 0.98629 | -0.095343 | 0.98806 | -0.082852 | 28.2998
42 | 0.048851 | 0.012288 | -0.048747 | -0.012248 | 0.00010344 | 3.9395e-05 | 0.073717 | 0.073717 | 0.073717 | 0.98629 | -0.095343 | 0.98413 | -0.11056 | 27.3027
43 | -0.0081679 | -0.0020469 | 0.0081703 | 0.0020475 | 2.3703e-06 | 6.0567e-07 | 0.012455 | 0.012455 | 0.012455 | 0.97581 | -0.16958 | 0.9761 | -0.16748 | 4.6131
44 | 0.037784 | 0.0094824 | -0.037767 | -0.009476 | 1.691e-05 | 6.4017e-06 | 0.057605 | 0.057605 | 0.057605 | 0.9761 | -0.16748 | 0.97565 | -0.17071 | 21.3351
45 | -0.045954 | -0.01153 | 0.046048 | 0.011566 | 9.3723e-05 | 3.5664e-05 | 0.07006 | 0.07006 | 0.07006 | 0.9761 | -0.16748 | 0.97815 | -0.15281 | 25.9481
46 | 0.00030667 | 7.6591e-05 | -0.00030666 | -7.6857e-05 | 2.7603e-09 | -2.667e-07 | 0.00046084 | 0.00046094 | 0.00046094 | 0.99 | -0.070209 | 0.98999 | -0.070275 | 0.17072
47 | 0.1121 | 0.028304 | -0.11191 | -0.028229 | 0.00019605 | 7.4831e-05 | 0.16816 | 0.16816 | 0.16816 | 0.99244 | -0.052261 | 0.99065 | -0.06473 | 31.1399
48 | -0.1111 | -0.027988 | 0.11138 | 0.028096 | 0.00028236 | 0.00010777 | 0.16736 | 0.16736 | 0.16736 | 0.98806 | -0.082852 | 0.99065 | -0.06473 | 30.9927
49 | 0.004829 | 0.0012096 | -0.0048284 | -0.0012096 | 6.1266e-07 | -2.1085e-09 | 0.0072722 | 0.0072723 | 0.0072723 | 0.98806 | -0.082852 | 0.98793 | -0.08377 | 2.6934
50 | 0.055543 | 0.01401 | -0.055488 | -0.01399 | 5.4261e-05 | 2.0234e-05 | 0.083679 | 0.083679 | 0.083679 | 0.98806 | -0.082852 | 0.98706 | -0.089825 | 15.4962
51 | 0.04435 | 0.011147 | -0.044337 | -0.011142 | 1.2727e-05 | 4.8375e-06 | 0.067069 | 0.067069 | 0.067069 | 0.98413 | -0.11056 | 0.98384 | -0.11262 | 24.8402
52 | 0.0043973 | 0.0011019 | -0.0043972 | -0.0011019 | 8.242e-08 | -6.2655e-09 | 0.0066486 | 0.0066487 | 0.0066487 | 0.98413 | -0.11056 | 0.98411 | -0.1107 | 2.4625
53 | 0.0006118 | 0.00015293 | -0.0006118 | -0.00015305 | 5.2897e-09 | -1.2583e-07 | 0.00092135 | 0.00092139 | 0.00092139 | 0.98793 | -0.08377 | 0.98792 | -0.083833 | 0.34126
54 | 0.0042166 | 0.0010566 | -0.0042163 | -0.0010567 | 2.9918e-07 | -3.7124e-08 | 0.006351 | 0.006351 | 0.006351 | 0.98793 | -0.08377 | 0.98786 | -0.084282 | 2.3522
55 | 0.054664 | 0.013784 | -0.054632 | -0.013771 | 3.2769e-05 | 1.2505e-05 | 0.082437 | 0.082437 | 0.082437 | 0.98706 | -0.089825 | 0.98645 | -0.094106 | 30.5323
56 | 0.0006118 | 0.00015305 | -0.00061179 | -0.00015333 | 1.1564e-08 | -2.7502e-07 | 0.00092139 | 0.00092149 | 0.00092149 | 0.98792 | -0.083833 | 0.9879 | -0.083969 | 0.34129
57 | 0.00314 | 0.00078694 | -0.00314 | -0.00078695 | 2.0393e-08 | -1.086e-08 | 0.0047298 | 0.0047298 | 0.0047298 | 0.98786 | -0.084282 | 0.98785 | -0.084329 | 1.7518
58 | 0.043903 | 0.011033 | -0.043859 | -0.011016 | 4.4484e-05 | 1.6904e-05 | 0.066412 | 0.066412 | 0.066412 | 0.98384 | -0.11262 | 0.98281 | -0.11991 | 24.5972
59 | 0.0043972 | 0.0011019 | -0.0043969 | -0.0011019 | 2.7244e-07 | -2.0699e-08 | 0.0066487 | 0.0066487 | 0.0066487 | 0.98411 | -0.1107 | 0.98405 | -0.11114 | 2.4625
60 | -0.0049462 | -0.0012395 | 0.0049466 | 0.0012395 | 4.0214e-07 | 1.5051e-08 | 0.0075681 | 0.007568 | 0.0075681 | 0.97249 | -0.19339 | 0.97257 | -0.1928 | 2.803
61 | 0.0028119 | 0.00070458 | -0.0028118 | -0.0007047 | 1.7096e-07 | -1.1787e-07 | 0.0043025 | 0.0043026 | 0.0043026 | 0.97249 | -0.19339 | 0.97243 | -0.19383 | 1.5935
62 | -0.007108 | -0.0017812 | 0.0071093 | 0.0017815 | 1.2983e-06 | 2.8098e-07 | 0.010875 | 0.010875 | 0.010875 | 0.97257 | -0.1928 | 0.97276 | -0.19148 | 4.0278
63 | -0.0085223 | -0.0021356 | 0.0085228 | 0.0021357 | 4.6471e-07 | 1.2433e-07 | 0.013036 | 0.013036 | 0.013036 | 0.97276 | -0.19148 | 0.97281 | -0.19109 | 4.8283
64 | -0.0096395 | -0.0024156 | 0.009642 | 0.0024163 | 2.5157e-06 | 7.3726e-07 | 0.014744 | 0.014744 | 0.014744 | 0.97281 | -0.19109 | 0.97307 | -0.1892 | 5.4609
65 | 0.020593 | 0.0051606 | -0.020578 | -0.0051552 | 1.4845e-05 | 5.4117e-06 | 0.03149 | 0.03149 | 0.03149 | 0.97307 | -0.1892 | 0.97235 | -0.19441 | 11.6629
66 | -0.030234 | -0.007577 | 0.030244 | 0.0075806 | 9.6027e-06 | 3.6039e-06 | 0.046234 | 0.046234 | 0.046234 | 0.97307 | -0.1892 | 0.97339 | -0.18691 | 17.1238
67 | 0.0092314 | 0.002312 | -0.0092303 | -0.0023117 | 1.0486e-06 | 2.9886e-07 | 0.014126 | 0.014126 | 0.014126 | 0.97235 | -0.19441 | 0.97224 | -0.19523 | 5.232
68 | 0.011346 | 0.0028433 | -0.011337 | -0.0028402 | 9.5799e-06 | 3.0535e-06 | 0.017363 | 0.017364 | 0.017364 | 0.97235 | -0.19441 | 0.9715 | -0.20052 | 6.431
69 | -0.034802 | -0.0087228 | 0.03488 | 0.0087523 | 7.8242e-05 | 2.9541e-05 | 0.053201 | 0.053201 | 0.053201 | 0.97339 | -0.18691 | 0.97565 | -0.17071 | 19.7041
70 | -0.00024328 | -6.0971e-05 | 0.00024329 | 5.954e-05 | 1.0055e-08 | -1.4315e-06 | 0.00037287 | 0.00037235 | 0.00037287 | 0.97086 | -0.20516 | 0.9709 | -0.20486 | 0.1381
71 | -0.010643 | -0.0026659 | 0.010649 | 0.0026678 | 6.3919e-06 | 1.982e-06 | 0.016311 | 0.01631 | 0.016311 | 0.9709 | -0.20486 | 0.9715 | -0.20052 | 6.0409
72 | 0.0069143 | 0.0017312 | -0.0069135 | -0.0017311 | 8.1149e-07 | 1.6811e-07 | 0.010582 | 0.010582 | 0.010582 | 0.97224 | -0.19523 | 0.97212 | -0.19608 | 3.9192
73 | 0.000806 | 0.00020143 | -0.00080598 | -0.00020168 | 1.8573e-08 | -2.4873e-07 | 0.0012171 | 0.0012172 | 0.0012172 | 0.98526 | -0.1039 | 0.98524 | -0.10407 | 0.4508
74 | -0.000806 | -0.00020143 | 0.00080601 | 0.00020134 | 6.5782e-09 | -8.8109e-08 | 0.0012171 | 0.001217 | 0.0012171 | 0.98526 | -0.1039 | 0.98527 | -0.10384 | 0.45077
75 | 0.00045717 | 0.00011426 | -0.00045716 | -0.00011458 | 7.4451e-09 | -3.159e-07 | 0.00069035 | 0.00069046 | 0.00069046 | 0.98524 | -0.10407 | 0.98522 | -0.10419 | 0.25573
76 | 0.003179 | 0.00079648 | -0.0031786 | -0.00079664 | 3.2488e-07 | -1.6268e-07 | 0.004801 | 0.0048011 | 0.0048011 | 0.98527 | -0.10384 | 0.98517 | -0.10458 | 1.7782
77 | -0.003985 | -0.00099782 | 0.0039865 | 0.00099754 | 1.5691e-06 | -2.8116e-07 | 0.006018 | 0.0060177 | 0.006018 | 0.98527 | -0.10384 | 0.98567 | -0.10099 | 2.2289
78 | -0.0058496 | -0.0014645 | 0.0058543 | 0.001465 | 4.6487e-06 | 5.6913e-07 | 0.0088303 | 0.0088299 | 0.0088303 | 0.98567 | -0.10099 | 0.98648 | -0.095237 | 3.2705
79 | 0.0058642 | 0.0014662 | -0.0058543 | -0.001465 | 9.8592e-06 | 1.2e-06 | 0.008829 | 0.0088299 | 0.0088299 | 0.98819 | -0.083036 | 0.98648 | -0.095237 | 3.2703
80 | -0.0058642 | -0.0014662 | 0.0058679 | 0.0014667 | 3.7479e-06 | 4.5367e-07 | 0.008829 | 0.0088286 | 0.008829 | 0.98819 | -0.083036 | 0.98884 | -0.078398 | 3.27
81 | -0.0061389 | -0.0015346 | 0.0061405 | 0.0015348 | 1.544e-06 | 2.2168e-07 | 0.0092365 | 0.0092363 | 0.0092365 | 0.98884 | -0.078398 | 0.9891 | -0.076572 | 3.4209
82 | 0.0057597 | 0.0014419 | -0.0057581 | -0.0014417 | 1.665e-06 | 2.1487e-07 | 0.0088158 | 0.0088159 | 0.0088159 | 0.97212 | -0.19608 | 0.97183 | -0.19818 | 3.2652
83 | -0.047853 | -0.012018 | 0.047923 | 0.012045 | 7.0519e-05 | 2.6855e-05 | 0.072805 | 0.072805 | 0.072805 | 0.97815 | -0.15281 | 0.97964 | -0.14222 | 26.9647
84 | -0.049755 | -0.012504 | 0.04979 | 0.012517 | 3.4948e-05 | 1.3318e-05 | 0.075587 | 0.075587 | 0.075587 | 0.97964 | -0.14222 | 0.98035 | -0.13718 | 27.9952
85 | -0.050873 | -0.012788 | 0.050941 | 0.012814 | 6.8027e-05 | 2.5934e-05 | 0.07723 | 0.07723 | 0.07723 | 0.98035 | -0.13718 | 0.9817 | -0.12759 | 28.6039
86 | -0.050941 | -0.012814 | 0.050975 | 0.012827 | 3.4319e-05 | 1.3083e-05 | 0.07723 | 0.07723 | 0.07723 | 0.9817 | -0.12759 | 0.98239 | -0.12277 | 28.6038
87 | -0.050975 | -0.012827 | 0.050999 | 0.012836 | 2.3573e-05 | 8.9863e-06 | 0.07723 | 0.07723 | 0.07723 | 0.98239 | -0.12277 | 0.98285 | -0.11945 | 28.6038
88 | -0.052091 | -0.01311 | 0.052141 | 0.013129 | 4.9977e-05 | 1.9059e-05 | 0.078884 | 0.078884 | 0.078884 | 0.98285 | -0.11945 | 0.98383 | -0.11259 | 29.2163
89 | -0.053433 | -0.01346 | 0.053461 | 0.01347 | 2.7828e-05 | 1.0616e-05 | 0.080759 | 0.080759 | 0.080759 | 0.98483 | -0.10554 | 0.98536 | -0.10181 | 29.9106
90 | 0.052748 | 0.013288 | -0.052696 | -0.013268 | 5.1983e-05 | 1.9827e-05 | 0.079723 | 0.079723 | 0.079723 | 0.98483 | -0.10554 | 0.98383 | -0.11259 | 29.5272
91 | 0.0005342 | 0.00013376 | -0.0005342 | -0.00013388 | 4.0651e-09 | -1.2595e-07 | 0.00080667 | 0.00080671 | 0.00080671 | 0.98536 | -0.10181 | 0.98535 | -0.10187 | 0.29878
92 | -0.053995 | -0.013604 | 0.054054 | 0.013626 | 5.8291e-05 | 2.224e-05 | 0.081565 | 0.081565 | 0.081565 | 0.98536 | -0.10181 | 0.98645 | -0.094106 | 30.2093
93 | 0.00055516 | 0.00013874 | -0.00055516 | -0.00013889 | 5.3796e-09 | -1.5324e-07 | 0.00083953 | 0.00083958 | 0.00083958 | 0.98383 | -0.11259 | 0.98382 | -0.11266 | 0.31096
94 | 0.00055516 | 0.00013889 | -0.00055515 | -0.00013913 | 8.3739e-09 | -2.3849e-07 | 0.00083958 | 0.00083967 | 0.00083967 | 0.98382 | -0.11266 | 0.9838 | -0.11277 | 0.31099
95 | -0.0015251 | -0.00038222 | 0.0015251 | 0.00038213 | 2.5131e-08 | -8.1624e-08 | 0.0023366 | 0.0023365 | 0.0023366 | 0.97121 | -0.20262 | 0.97123 | -0.20251 | 0.8654
96 | -0.0031228 | -0.00078256 | 0.003123 | 0.00078247 | 1.9341e-07 | -9.3194e-08 | 0.0047844 | 0.0047843 | 0.0047844 | 0.97123 | -0.20251 | 0.97129 | -0.20206 | 1.772
97 | 0.0044608 | 0.0011166 | -0.0044607 | -0.0011166 | 1.1453e-07 | -4.7039e-09 | 0.0068297 | 0.0068297 | 0.0068297 | 0.97183 | -0.19818 | 0.9718 | -0.19836 | 2.5295
98 | 0.0037226 | 0.00093289 | -0.0037224 | -0.00093293 | 1.339e-07 | -3.4531e-08 | 0.005629 | 0.005629 | 0.005629 | 0.98405 | -0.11114 | 0.98401 | -0.1114 | 2.0848
99 | -0.0034643 | -0.00086824 | 0.0034646 | 0.00086813 | 3.1714e-07 | -1.0872e-07 | 0.0052645 | 0.0052644 | 0.0052645 | 0.97919 | -0.14569 | 0.97929 | -0.14503 | 1.9498
100 | -0.008636 | -0.0021642 | 0.0086424 | 0.0021659 | 6.4372e-06 | 1.7215e-06 | 0.013122 | 0.013122 | 0.013122 | 0.97929 | -0.14503 | 0.98004 | -0.13965 | 4.8601
101 | -0.015723 | -0.0039406 | 0.015727 | 0.0039419 | 3.6056e-06 | 1.2586e-06 | 0.023852 | 0.023852 | 0.023852 | 0.9809 | -0.13347 | 0.98114 | -0.13182 | 8.8341
102 | 0.015181 | 0.0038047 | -0.015174 | -0.0038023 | 6.926e-06 | 2.3998e-06 | 0.023029 | 0.02303 | 0.02303 | 0.9809 | -0.13347 | 0.98044 | -0.13677 | 8.5295
103 | -0.040508 | -0.010167 | 0.040514 | 0.01017 | 6.0451e-06 | 2.2926e-06 | 0.061441 | 0.061441 | 0.061441 | 0.98114 | -0.13182 | 0.98129 | -0.13074 | 22.7557
104 | 0.024781 | 0.0062255 | -0.024746 | -0.0062127 | 3.453e-05 | 1.2787e-05 | 0.037588 | 0.037589 | 0.037589 | 0.98114 | -0.13182 | 0.97973 | -0.14185 | 13.9217
105 | 0.010997 | 0.0027564 | -0.010993 | -0.002755 | 4.3797e-06 | 1.3669e-06 | 0.016691 | 0.016691 | 0.016691 | 0.98044 | -0.13677 | 0.98004 | -0.13965 | 6.1818
106 | 0.0041768 | 0.0010459 | -0.0041747 | -0.0010461 | 2.1085e-06 | -2.4896e-07 | 0.0063388 | 0.0063392 | 0.0063392 | 0.98044 | -0.13677 | 0.97993 | -0.14042 | 2.3479
107 | -0.041733 | -0.010475 | 0.041795 | 0.010499 | 6.288e-05 | 2.3866e-05 | 0.063289 | 0.063289 | 0.063289 | 0.98129 | -0.13074 | 0.98281 | -0.11991 | 23.4403
108 | 0.02386 | 0.0059907 | -0.02382 | -0.0059756 | 4.078e-05 | 1.5059e-05 | 0.036243 | 0.036244 | 0.036244 | 0.97973 | -0.14185 | 0.978 | -0.15417 | 13.4235
109 | 0.0041747 | 0.0010461 | -0.0041743 | -0.0010462 | 3.7408e-07 | -4.404e-08 | 0.0063392 | 0.0063393 | 0.0063393 | 0.97993 | -0.14042 | 0.97984 | -0.14107 | 2.3479
110 | 0.02301 | 0.0057728 | -0.023006 | -0.0057711 | 4.5744e-06 | 1.6844e-06 | 0.035012 | 0.035012 | 0.035012 | 0.978 | -0.15417 | 0.9778 | -0.1556 | 12.9675
111 | 0.022582 | 0.0056648 | -0.022564 | -0.0056583 | 1.7841e-05 | 6.5585e-06 | 0.034367 | 0.034367 | 0.034367 | 0.9778 | -0.1556 | 0.977 | -0.16131 | 12.7285
112 | 0.020414 | 0.0051195 | -0.020408 | -0.0051171 | 6.6135e-06 | 2.4064e-06 | 0.031093 | 0.031093 | 0.031093 | 0.977 | -0.16131 | 0.97667 | -0.16364 | 11.516
113 | -0.014792 | -0.0037072 | 0.014802 | 0.0037108 | 1.0239e-05 | 3.5357e-06 | 0.022568 | 0.022568 | 0.022568 | 0.97529 | -0.17357 | 0.97599 | -0.16857 | 8.3587
114 | -0.01967 | -0.0049309 | 0.019684 | 0.0049357 | 1.3441e-05 | 4.8702e-06 | 0.029991 | 0.02999 | 0.029991 | 0.97599 | -0.16857 | 0.97667 | -0.16364 | 11.1076
115 | 0.0031246 | 0.0007817 | -0.003123 | -0.00078247 | 1.5955e-06 | -7.6976e-07 | 0.0047838 | 0.0047843 | 0.0047843 | 0.9718 | -0.19836 | 0.97129 | -0.20206 | 1.772

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.1656 | 0.041646

## res_load
| p_mw | q_mvar
0 | 0.00099023 | 0.00024817
1 | 0.00035605 | 8.9234e-05
2 | 0.0015166 | 0.0003801
3 | 0.0062371 | 0.0015632
4 | 0.0025666 | 0.00064326
5 | 0.0017366 | 0.00043523
6 | 0.00090016 | 0.0002256
7 | 0.00022167 | 5.5555e-05
8 | 0.0015192 | 0.00038074
9 | 0.00040365 | 0.00010116
10 | 0.0090407 | 0.0022658
11 | 0.00030223 | 7.5746e-05
12 | 0.0020499 | 0.00051376
13 | 0.0020694 | 0.00051864
14 | 0.0015599 | 0.00039094
15 | 0.0029913 | 0.00074968
16 | 0.002811 | 0.0007045
17 | 0.00052714 | 0.00013211
18 | 0.0018941 | 0.00047472
19 | 0.00041611 | 0.00010429
20 | 0.00046504 | 0.00011655
21 | 0.00039727 | 9.9565e-05
22 | 0.003927 | 0.0009842
23 | 0.0017844 | 0.00044722
24 | 0.0045384 | 0.0011374
25 | 0.00030406 | 7.6205e-05
26 | 0.00030666 | 7.6857e-05
27 | 0.00065052 | 0.00016304
28 | 0.00065052 | 0.00016304
29 | 0.0005295 | 0.0001327
30 | 0.00082406 | 0.00020653
31 | 0.0010763 | 0.00026975
32 | 0.00061179 | 0.00015333
33 | 0.00043394 | 0.00010876
34 | 0.0021342 | 0.00053489
35 | 0.0021614 | 0.0005417
36 | 0.0028118 | 0.0007047
37 | 0.0014131 | 0.00035415
38 | 0.0011167 | 0.00027987
39 | 0.0045575 | 0.0011422
40 | 0.00024328 | 6.0971e-05
41 | 0.010399 | 0.0026063
42 | 0.00068768 | 0.00017235
43 | 0.002316 | 0.00058044
44 | 0.00034882 | 8.7422e-05
45 | 0.00024863 | 6.2313e-05
46 | 0.00045716 | 0.00011458
47 | 0.0031786 | 0.00079664
48 | 0.0018631 | 0.00046694
49 | 0.000271 | 6.792e-05
50 | 0.0011538 | 0.00028917
51 | 0.0018045 | 0.00045224
52 | 0.0018318 | 0.0004591
53 | 0.0010828 | 0.00027137
54 | 0.0028874 | 0.00072366
55 | 0.0010922 | 0.00027373
56 | 0.0006852 | 0.00017173
57 | 0.0005342 | 0.00013388
58 | 0.00057804 | 0.00014487
59 | 0.00055515 | 0.00013913
60 | 0.0015251 | 0.00038222
61 | 0.0015977 | 0.00040043
62 | 0.0012972 | 0.00032511
63 | 0.00314 | 0.00078695
64 | 0.00067435 | 0.00016901
65 | 0.0034643 | 0.00086824
66 | 0.0051714 | 0.0012961
67 | 0.00054231 | 0.00013592
68 | 0.0012188 | 0.00030546
69 | 0.00088572 | 0.00022198
70 | 0.0023505 | 0.0005891
71 | 0.0020632 | 0.00051709
72 | 0.00080933 | 0.00020284
73 | 0.0041743 | 0.0010462
74 | 0.00042404 | 0.00010627
75 | 0.0021496 | 0.00053873
76 | 0.0037224 | 0.00093293
77 | 0.00099996 | 0.00025061
78 | 0.00096696 | 0.00024234
79 | 0.014792 | 0.0037072
80 | 0.0048682 | 0.0012201
81 | 0.00072381 | 0.00018141
82 | 0.0013361 | 0.00033487

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1