## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1030-2_1_3_node_152 | 0.4 | n |  | TRUE
1 | bus_LV_1030-2_1_3_node_151 | 0.4 | n |  | TRUE
2 | bus_LV_1030-2_1_3_node_56 | 0.4 | n |  | TRUE
3 | bus_LV_1030-2_1_3_node_57 | 0.4 | n |  | TRUE
4 | bus_LV_1030-2_1_3_node_59 | 0.4 | n |  | TRUE
5 | bus_LV_1030-2_1_3_node_155 | 0.4 | n |  | TRUE
6 | bus_LV_1030-2_1_3_node_158 | 0.4 | n |  | TRUE
7 | bus_LV_1030-2_1_3_node_60 | 0.4 | n |  | TRUE
8 | bus_LV_1030-2_1_3_node_61 | 0.4 | n |  | TRUE
9 | bus_LV_1030-2_1_3_node_62 | 0.4 | n |  | TRUE
10 | bus_LV_1030-2_1_3_node_63 | 0.4 | n |  | TRUE
11 | bus_LV_1030-2_1_3_node_64 | 0.4 | n |  | TRUE
12 | bus_LV_1030-2_1_3_node_101 | 0.4 | n |  | TRUE
13 | bus_LV_1030-2_1_3_node_90 | 0.4 | n |  | TRUE
14 | bus_LV_1030-2_1_3_node_99 | 0.4 | n |  | TRUE
15 | bus_LV_1030-2_1_3_node_89 | 0.4 | n |  | TRUE
16 | bus_LV_1030-2_1_3_node_102 | 0.4 | n |  | TRUE
17 | bus_LV_1030-2_1_3_node_124 | 0.4 | n |  | TRUE
18 | bus_LV_1030-2_1_3_node_117 | 0.4 | n |  | TRUE
19 | bus_LV_1030-2_1_3_node_94 | 0.4 | n |  | TRUE
20 | bus_LV_1030-2_1_3_node_125 | 0.4 | n |  | TRUE
21 | bus_LV_1030-2_1_3_node_65 | 0.4 | n |  | TRUE
22 | bus_LV_1030-2_1_3_node_87 | 0.4 | n |  | TRUE
23 | bus_LV_1030-2_1_3_node_91 | 0.4 | n |  | TRUE
24 | bus_LV_1030-2_1_3_node_92 | 0.4 | n |  | TRUE
25 | bus_LV_1030-2_1_3_node_93 | 0.4 | n |  | TRUE
26 | bus_LV_1030-2_1_3_node_85 | 0.4 | n |  | TRUE
27 | bus_LV_1030-2_1_3_node_97 | 0.4 | n |  | TRUE
28 | bus_LV_1030-2_1_3_node_98 | 0.4 | n |  | TRUE
29 | bus_LV_1030-2_1_3_node_100 | 0.4 | n |  | TRUE
30 | bus_LV_1030-2_1_3_node_66 | 0.4 | n |  | TRUE
31 | bus_LV_1030-2_1_3_node_88 | 0.4 | n |  | TRUE
32 | bus_LV_1030-2_1_3_node_95 | 0.4 | n |  | TRUE
33 | bus_LV_1030-2_1_3_node_123 | 0.4 | n |  | TRUE
34 | bus_LV_1030-2_1_3_node_83 | 0.4 | n |  | TRUE
35 | bus_LV_1030-2_1_3_node_71 | 0.4 | n |  | TRUE
36 | bus_LV_1030-2_1_3_node_106 | 0.4 | n |  | TRUE
37 | bus_LV_1030-2_1_3_node_67 | 0.4 | n |  | TRUE
38 | bus_LV_1030-2_1_3_node_68 | 0.4 | n |  | TRUE
39 | bus_LV_1030-2_1_3_node_69 | 0.4 | n |  | TRUE
40 | bus_LV_1030-2_1_3_node_70 | 0.4 | n |  | TRUE
41 | bus_LV_1030-2_1_3_node_128 | 0.4 | n |  | TRUE
42 | bus_LV_1030-2_1_3_node_126 | 0.4 | n |  | TRUE
43 | bus_LV_1030-2_1_3_node_72 | 0.4 | n |  | TRUE
44 | bus_LV_1030-2_1_3_node_73 | 0.4 | n |  | TRUE
45 | bus_LV_1030-2_1_3_node_74 | 0.4 | n |  | TRUE
46 | bus_LV_1030-2_1_3_node_75 | 0.4 | n |  | TRUE
47 | bus_LV_1030-2_1_3_node_76 | 0.4 | n |  | TRUE
48 | bus_LV_1030-2_1_3_node_96 | 0.4 | n |  | TRUE
49 | bus_LV_1030-2_1_3_node_122 | 0.4 | n |  | TRUE
50 | bus_LV_1030-2_1_3_node_105 | 0.4 | n |  | TRUE
51 | bus_LV_1030-2_1_3_node_131 | 0.4 | n |  | TRUE
52 | bus_LV_1030-2_1_3_node_119 | 0.4 | n |  | TRUE
53 | bus_LV_1030-2_1_3_node_115 | 0.4 | n |  | TRUE
54 | bus_LV_1030-2_1_3_node_121 | 0.4 | n |  | TRUE
55 | bus_LV_1030-2_1_3_node_77 | 0.4 | n |  | TRUE
56 | bus_LV_1030-2_1_3_node_78 | 0.4 | n |  | TRUE
57 | bus_LV_1030-2_1_3_node_79 | 0.4 | n |  | TRUE
58 | bus_LV_1030-2_1_3_node_80 | 0.4 | n |  | TRUE
59 | bus_LV_1030-2_1_3_node_81 | 0.4 | n |  | TRUE
60 | bus_LV_1030-2_1_3_node_103 | 0.4 | n |  | TRUE
61 | bus_LV_1030-2_1_3_node_86 | 0.4 | n |  | TRUE
62 | bus_LV_1030-2_1_3_node_104 | 0.4 | n |  | TRUE
63 | bus_LV_1030-2_1_3_node_84 | 0.4 | n |  | TRUE
64 | bus_LV_1030-2_1_3_node_82 | 0.4 | n |  | TRUE
65 | bus_LV_1030-2_1_3_node_172 | 0.4 | n |  | TRUE
66 | bus_LV_1030-2_1_3_node_163 | 0.4 | n |  | TRUE
67 | bus_LV_1030-2_1_3_node_107 | 0.4 | n |  | TRUE
68 | bus_LV_1030-2_1_3_node_108 | 0.4 | n |  | TRUE
69 | bus_LV_1030-2_1_3_node_109 | 0.4 | n |  | TRUE
70 | bus_LV_1030-2_1_3_node_110 | 0.4 | n |  | TRUE
71 | bus_LV_1030-2_1_3_node_111 | 0.4 | n |  | TRUE
72 | bus_LV_1030-2_1_3_node_153 | 0.4 | n |  | TRUE
73 | bus_LV_1030-2_1_3_node_146 | 0.4 | n |  | TRUE
74 | bus_LV_1030-2_1_3_node_156 | 0.4 | n |  | TRUE
75 | bus_LV_1030-2_1_3_node_145 | 0.4 | n |  | TRUE
76 | bus_LV_1030-2_1_3_node_112 | 0.4 | n |  | TRUE
77 | bus_LV_1030-2_1_3_node_113 | 0.4 | n |  | TRUE
78 | bus_LV_1030-2_1_3_node_114 | 0.4 | n |  | TRUE
79 | bus_LV_1030-2_1_3_node_116 | 0.4 | n |  | TRUE
80 | bus_LV_1030-2_1_3_node_118 | 0.4 | n |  | TRUE
81 | bus_LV_1030-2_1_3_node_132 | 0.4 | n |  | TRUE
82 | bus_LV_1030-2_1_3_node_133 | 0.4 | n |  | TRUE
83 | bus_LV_1030-2_1_3_node_139 | 0.4 | n |  | TRUE
84 | bus_LV_1030-2_1_3_node_120 | 0.4 | n |  | TRUE
85 | bus_LV_1030-2_1_3_node_169 | 0.4 | n |  | TRUE
86 | bus_LV_1030-2_1_3_node_166 | 0.4 | n |  | TRUE
87 | bus_LV_1030-2_1_3_node_171 | 0.4 | n |  | TRUE
88 | bus_LV_1030-2_1_3_node_127 | 0.4 | n |  | TRUE
89 | bus_LV_1030-2_1_3_node_129 | 0.4 | n |  | TRUE
90 | bus_LV_1030-2_1_3_node_130 | 0.4 | n |  | TRUE
91 | bus_LV_1030-2_1_3_node_147 | 0.4 | n |  | TRUE
92 | bus_LV_1030-2_1_3_node_136 | 0.4 | n |  | TRUE
93 | bus_LV_1030-2_1_3_node_134 | 0.4 | n |  | TRUE
94 | bus_LV_1030-2_1_3_node_135 | 0.4 | n |  | TRUE
95 | bus_LV_1030-2_1_3_node_137 | 0.4 | n |  | TRUE
96 | bus_LV_1030-2_1_3_node_138 | 0.4 | n |  | TRUE
97 | bus_LV_1030-2_1_3_node_162 | 0.4 | n |  | TRUE
98 | bus_LV_1030-2_1_3_node_160 | 0.4 | n |  | TRUE
99 | bus_LV_1030-2_1_3_node_140 | 0.4 | n |  | TRUE
100 | bus_LV_1030-2_1_3_node_141 | 0.4 | n |  | TRUE
101 | bus_LV_1030-2_1_3_node_142 | 0.4 | n |  | TRUE
102 | bus_LV_1030-2_1_3_node_143 | 0.4 | n |  | TRUE
103 | bus_LV_1030-2_1_3_node_144 | 0.4 | n |  | TRUE
104 | bus_LV_1030-2_1_3_node_154 | 0.4 | n |  | TRUE
105 | bus_LV_1030-2_1_3_node_159 | 0.4 | n |  | TRUE
106 | bus_LV_1030-2_1_3_node_157 | 0.4 | n |  | TRUE
107 | bus_LV_1030-2_1_3_node_161 | 0.4 | n |  | TRUE
108 | bus_LV_1030-2_1_3_node_164 | 0.4 | n |  | TRUE
109 | bus_LV_1030-2_1_3_node_165 | 0.4 | n |  | TRUE
110 | bus_LV_1030-2_1_3_node_167 | 0.4 | n |  | TRUE
111 | bus_LV_1030-2_1_3_node_170 | 0.4 | n |  | TRUE
112 | bus_MV_470_1_node_81 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1030-2_1_3_load_152 | 0 | 0.0002706 | 6.7818e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1030-2_1_3_load_151 | 1 | 0.00031308 | 7.8466e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1030-2_1_3_load_56 | 2 | 0.00094124 | 0.0002359 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1030-2_1_3_load_57 | 3 | 0.0035496 | 0.00088962 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1030-2_1_3_load_59 | 4 | 0.0045324 | 0.0011359 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1030-2_1_3_load_155 | 5 | 0.0014536 | 0.00036431 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1030-2_1_3_load_158 | 6 | 0.0029645 | 0.00074297 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1030-2_1_3_load_60 | 7 | 0.00058175 | 0.0001458 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1030-2_1_3_load_61 | 8 | 0.00064857 | 0.00016255 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1030-2_1_3_load_62 | 9 | 0.0013309 | 0.00033357 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1030-2_1_3_load_63 | 10 | 0.0022734 | 0.00056976 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1030-2_1_3_load_64 | 11 | 0.00040111 | 0.00010053 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1030-2_1_3_load_101 | 12 | 0.00086337 | 0.00021638 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1030-2_1_3_load_90 | 13 | 0.00043841 | 0.00010988 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1030-2_1_3_load_102 | 16 | 0.0010392 | 0.00026044 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1030-2_1_3_load_124 | 17 | 0.00092435 | 0.00023166 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1030-2_1_3_load_117 | 18 | 0.00063358 | 0.00015879 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1030-2_1_3_load_94 | 19 | 0.0007399 | 0.00018544 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1030-2_1_3_load_125 | 20 | 0.00063317 | 0.00015869 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1030-2_1_3_load_65 | 21 | 0.0022581 | 0.00056593 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1030-2_1_3_load_87 | 22 | 0.0029429 | 0.00073757 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1030-2_1_3_load_91 | 23 | 0.00092956 | 0.00023297 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1030-2_1_3_load_92 | 24 | 0.00038627 | 9.6808e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1030-2_1_3_load_93 | 25 | 0.00038627 | 9.6808e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1030-2_1_3_load_97 | 27 | 0.0014056 | 0.00035228 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1030-2_1_3_load_100 | 29 | 0.00086325 | 0.00021635 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1030-2_1_3_load_66 | 30 | 0.0047852 | 0.0011993 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1030-2_1_3_load_95 | 32 | 0.00058126 | 0.00014568 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1030-2_1_3_load_123 | 33 | 0.00065136 | 0.00016325 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1030-2_1_3_load_83 | 34 | 0.00041703 | 0.00010452 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1030-2_1_3_load_71 | 35 | 0.0013872 | 0.00034767 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1030-2_1_3_load_106 | 36 | 0.00038914 | 9.7526e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1030-2_1_3_load_67 | 37 | 0.0032227 | 0.00080768 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1030-2_1_3_load_68 | 38 | 0.0051658 | 0.0012947 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1030-2_1_3_load_69 | 39 | 0.00077854 | 0.00019512 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1030-2_1_3_load_70 | 40 | 0.0011588 | 0.00029043 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1030-2_1_3_load_128 | 41 | 0.0027386 | 0.00068635 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1030-2_1_3_load_126 | 42 | 0.0025271 | 0.00063334 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1030-2_1_3_load_72 | 43 | 0.00038959 | 9.7639e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1030-2_1_3_load_73 | 44 | 0.0043823 | 0.0010983 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1030-2_1_3_load_74 | 45 | 0.00051798 | 0.00012982 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1030-2_1_3_load_75 | 46 | 0.0015616 | 0.00039137 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1030-2_1_3_load_122 | 49 | 0.00063009 | 0.00015792 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1030-2_1_3_load_105 | 50 | 0.0016654 | 0.00041739 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1030-2_1_3_load_131 | 51 | 0.0020491 | 0.00051355 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1030-2_1_3_load_119 | 52 | 0.002719 | 0.00068145 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1030-2_1_3_load_77 | 55 | 0.0017728 | 0.00044432 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1030-2_1_3_load_78 | 56 | 0.0038582 | 0.00096696 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1030-2_1_3_load_79 | 57 | 0.0013283 | 0.00033289 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1030-2_1_3_load_80 | 58 | 0.0024015 | 0.00060187 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1030-2_1_3_load_81 | 59 | 0.0013291 | 0.0003331 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1030-2_1_3_load_103 | 60 | 0.0013011 | 0.00032609 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1030-2_1_3_load_86 | 61 | 0.00067659 | 0.00016957 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1030-2_1_3_load_104 | 62 | 0.0013006 | 0.00032597 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1030-2_1_3_load_84 | 63 | 0.00018748 | 4.6988e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1030-2_1_3_load_82 | 64 | 0.00018748 | 4.6988e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1030-2_1_3_load_172 | 65 | 0.00047971 | 0.00012023 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1030-2_1_3_load_163 | 66 | 0.0020716 | 0.00051918 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1030-2_1_3_load_107 | 67 | 0.0050363 | 0.0012622 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1030-2_1_3_load_108 | 68 | 0.0065549 | 0.0016428 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1030-2_1_3_load_109 | 69 | 0.0015807 | 0.00039616 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1030-2_1_3_load_110 | 70 | 0.0013235 | 0.00033171 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1030-2_1_3_load_153 | 72 | 0.0016599 | 0.000416 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1030-2_1_3_load_146 | 73 | 0.0011359 | 0.00028469 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1030-2_1_3_load_156 | 74 | 0.001016 | 0.00025464 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1030-2_1_3_load_145 | 75 | 0.0013604 | 0.00034095 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1030-2_1_3_load_112 | 76 | 0.0022345 | 0.00056003 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1030-2_1_3_load_113 | 77 | 0.0030166 | 0.00075603 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1030-2_1_3_load_114 | 78 | 0.0022927 | 0.00057461 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1030-2_1_3_load_116 | 79 | 0.002799 | 0.00070149 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1030-2_1_3_load_118 | 80 | 0.0017023 | 0.00042663 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1030-2_1_3_load_132 | 81 | 0.001657 | 0.00041528 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1030-2_1_3_load_133 | 82 | 0.001582 | 0.00039649 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1030-2_1_3_load_139 | 83 | 0.00097586 | 0.00024457 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1030-2_1_3_load_120 | 84 | 0.0020404 | 0.00051137 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1030-2_1_3_load_169 | 85 | 0.00030083 | 7.5394e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1030-2_1_3_load_147 | 91 | 0.0058677 | 0.0014706 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1030-2_1_3_load_134 | 93 | 0.00078251 | 0.00019611 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1030-2_1_3_load_135 | 94 | 0.0030675 | 0.00076878 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1030-2_1_3_load_138 | 96 | 0.0017394 | 0.00043593 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1030-2_1_3_load_162 | 97 | 0.00087527 | 0.00021936 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1030-2_1_3_load_140 | 99 | 0.0021632 | 0.00054215 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1030-2_1_3_load_141 | 100 | 0.004884 | 0.0012241 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1030-2_1_3_load_142 | 101 | 0.00080581 | 0.00020196 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1030-2_1_3_load_143 | 102 | 0.00086239 | 0.00021613 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1030-2_1_3_load_144 | 103 | 0.00082409 | 0.00020654 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1030-2_1_3_load_154 | 104 | 0.00162 | 0.000406 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1030-2_1_3_load_159 | 105 | 0.00077917 | 0.00019528 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1030-2_1_3_load_157 | 106 | 0.001728 | 0.00043309 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1030-2_1_3_load_161 | 107 | 0.0009597 | 0.00024052 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1030-2_1_3_load_164 | 108 | 0.0005597 | 0.00014027 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1030-2_1_3_load_165 | 109 | 0.00081578 | 0.00020445 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1030-2_1_3_load_167 | 110 | 0.0003338 | 8.3658e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1030-2_1_3_load_170 | 111 | 0.00040883 | 0.00010246 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 46 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1030-2_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.00024268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1030-2_1_3_line_1 | NAYY 4x150 SE | 1 | 95 | 0.0048874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1030-2_1_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.022529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1030-2_1_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.042971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1030-2_1_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.0060146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1030-2_1_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.029907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1030-2_1_3_line_6 | NAYY 4x150 SE | 6 | 103 | 0.0019155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1030-2_1_3_line_7 | NAYY 4x150 SE | 7 | 8 | 0.018653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1030-2_1_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.0071456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1030-2_1_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.019293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1030-2_1_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.021449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1030-2_1_3_line_11 | NAYY 4x150 SE | 9 | 12 | 0.062487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1030-2_1_3_line_12 | NAYY 4x150 SE | 10 | 21 | 0.022686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1030-2_1_3_line_13 | NAYY 4x150 SE | 11 | 26 | 0.014788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1030-2_1_3_line_14 | NAYY 4x150 SE | 12 | 29 | 0.0072178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1030-2_1_3_line_15 | NAYY 4x150 SE | 13 | 14 | 0.018428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1030-2_1_3_line_16 | NAYY 4x150 SE | 13 | 15 | 0.0037981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1030-2_1_3_line_17 | NAYY 4x150 SE | 14 | 16 | 0.013544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1030-2_1_3_line_18 | NAYY 4x150 SE | 15 | 22 | 0.019501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1030-2_1_3_line_19 | NAYY 4x150 SE | 16 | 17 | 0.022714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1030-2_1_3_line_20 | NAYY 4x150 SE | 17 | 20 | 0.0030446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1030-2_1_3_line_21 | NAYY 4x150 SE | 18 | 19 | 0.0037695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1030-2_1_3_line_22 | NAYY 4x150 SE | 19 | 24 | 0.013715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1030-2_1_3_line_23 | NAYY 4x150 SE | 21 | 30 | 0.0024395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1030-2_1_3_line_24 | NAYY 4x150 SE | 22 | 31 | 0.040722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1030-2_1_3_line_25 | NAYY 4x150 SE | 23 | 24 | 0.0042442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1030-2_1_3_line_26 | NAYY 4x150 SE | 23 | 25 | 0.0040647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1030-2_1_3_line_27 | NAYY 4x150 SE | 25 | 32 | 0.015517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1030-2_1_3_line_28 | NAYY 4x150 SE | 26 | 33 | 0.019211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1030-2_1_3_line_29 | NAYY 4x150 SE | 26 | 34 | 0.019977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1030-2_1_3_line_30 | NAYY 4x150 SE | 27 | 28 | 0.032944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1030-2_1_3_line_31 | NAYY 4x150 SE | 28 | 29 | 0.027419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1030-2_1_3_line_32 | NAYY 4x150 SE | 30 | 35 | 0.061058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1030-2_1_3_line_33 | NAYY 4x150 SE | 31 | 40 | 0.01828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1030-2_1_3_line_34 | NAYY 4x150 SE | 32 | 36 | 0.0023495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1030-2_1_3_line_35 | NAYY 4x150 SE | 33 | 65 | 0.026245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1030-2_1_3_line_36 | NAYY 4x150 SE | 34 | 64 | 0.011371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1030-2_1_3_line_37 | NAYY 4x150 SE | 35 | 36 | 0.0066127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1030-2_1_3_line_38 | NAYY 4x150 SE | 35 | 39 | 0.019764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1030-2_1_3_line_39 | NAYY 4x150 SE | 37 | 38 | 0.0055819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1030-2_1_3_line_40 | NAYY 4x150 SE | 37 | 39 | 0.0025107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1030-2_1_3_line_41 | NAYY 4x150 SE | 38 | 40 | 0.025777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1030-2_1_3_line_42 | NAYY 4x150 SE | 41 | 42 | 0.075284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1030-2_1_3_line_43 | NAYY 4x150 SE | 42 | 88 | 0.018487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1030-2_1_3_line_44 | NAYY 4x150 SE | 43 | 44 | 0.048957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1030-2_1_3_line_45 | NAYY 4x150 SE | 43 | 45 | 0.03445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1030-2_1_3_line_46 | NAYY 4x150 SE | 44 | 46 | 0.030707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1030-2_1_3_line_47 | NAYY 4x150 SE | 45 | 47 | 0.013672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1030-2_1_3_line_48 | NAYY 4x150 SE | 46 | 48 | 0.014383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_1030-2_1_3_line_49 | NAYY 4x150 SE | 47 | 49 | 0.016223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1030-2_1_3_line_50 | NAYY 4x150 SE | 48 | 50 | 0.0054972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1030-2_1_3_line_51 | NAYY 4x150 SE | 48 | 51 | 0.006978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1030-2_1_3_line_52 | NAYY 4x150 SE | 49 | 54 | 0.0018631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1030-2_1_3_line_53 | NAYY 4x150 SE | 50 | 62 | 0.013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1030-2_1_3_line_54 | NAYY 4x150 SE | 51 | 66 | 0.02284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1030-2_1_3_line_55 | NAYY 4x150 SE | 52 | 53 | 0.010807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1030-2_1_3_line_56 | NAYY 4x150 SE | 53 | 80 | 0.013207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1030-2_1_3_line_57 | NAYY 4x150 SE | 53 | 77 | 0.016948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1030-2_1_3_line_58 | NAYY 4x150 SE | 54 | 84 | 0.055325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1030-2_1_3_line_59 | NAYY 4x150 SE | 55 | 56 | 0.028647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1030-2_1_3_line_60 | NAYY 4x150 SE | 55 | 57 | 0.015098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1030-2_1_3_line_61 | NAYY 4x150 SE | 56 | 58 | 0.01764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1030-2_1_3_line_62 | NAYY 4x150 SE | 57 | 59 | 0.0074352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1030-2_1_3_line_63 | NAYY 4x150 SE | 58 | 60 | 0.0067321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1030-2_1_3_line_64 | NAYY 4x150 SE | 59 | 61 | 0.0014311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1030-2_1_3_line_65 | NAYY 4x150 SE | 60 | 62 | 0.0070268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1030-2_1_3_line_66 | NAYY 4x150 SE | 61 | 63 | 0.015112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1030-2_1_3_line_67 | NAYY 4x150 SE | 63 | 64 | 0.0072334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1030-2_1_3_line_68 | NAYY 4x150 SE | 65 | 87 | 0.10562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1030-2_1_3_line_69 | NAYY 4x150 SE | 66 | 89 | 0.036028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1030-2_1_3_line_70 | NAYY 4x150 SE | 67 | 68 | 0.027918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1030-2_1_3_line_71 | NAYY 4x150 SE | 67 | 69 | 0.027327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1030-2_1_3_line_72 | NAYY 4x150 SE | 68 | 70 | 0.023344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1030-2_1_3_line_73 | NAYY 4x150 SE | 69 | 71 | 0.014814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1030-2_1_3_line_74 | NAYY 4x150 SE | 71 | 72 | 0.016642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1030-2_1_3_line_75 | NAYY 4x150 SE | 71 | 73 | 0.005044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1030-2_1_3_line_76 | NAYY 4x150 SE | 72 | 74 | 0.0056814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1030-2_1_3_line_77 | NAYY 4x150 SE | 73 | 75 | 0.012741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1030-2_1_3_line_78 | NAYY 4x150 SE | 74 | 106 | 0.010941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1030-2_1_3_line_79 | NAYY 4x150 SE | 75 | 91 | 0.0069304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1030-2_1_3_line_80 | NAYY 4x150 SE | 76 | 77 | 0.028268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1030-2_1_3_line_81 | NAYY 4x150 SE | 76 | 78 | 0.036877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1030-2_1_3_line_82 | NAYY 4x150 SE | 78 | 79 | 0.016583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1030-2_1_3_line_83 | NAYY 4x150 SE | 79 | 81 | 0.0063288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1030-2_1_3_line_84 | NAYY 4x150 SE | 80 | 82 | 0.01684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1030-2_1_3_line_85 | NAYY 4x150 SE | 81 | 83 | 0.027998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1030-2_1_3_line_86 | NAYY 4x150 SE | 83 | 92 | 0.024787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1030-2_1_3_line_87 | NAYY 4x150 SE | 85 | 86 | 0.079098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1030-2_1_3_line_88 | NAYY 4x150 SE | 86 | 108 | 0.024462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1030-2_1_3_line_89 | NAYY 4x150 SE | 87 | 111 | 0.029681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1030-2_1_3_line_90 | NAYY 4x150 SE | 88 | 89 | 0.014716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1030-2_1_3_line_91 | NAYY 4x150 SE | 89 | 90 | 0.020958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1030-2_1_3_line_92 | NAYY 4x150 SE | 90 | 91 | 0.01586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1030-2_1_3_line_93 | NAYY 4x150 SE | 92 | 96 | 0.015442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1030-2_1_3_line_94 | NAYY 4x150 SE | 92 | 93 | 0.022024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1030-2_1_3_line_95 | NAYY 4x150 SE | 93 | 94 | 0.0059516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1030-2_1_3_line_96 | NAYY 4x150 SE | 94 | 95 | 0.042322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1030-2_1_3_line_97 | NAYY 4x150 SE | 96 | 97 | 0.015239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1030-2_1_3_line_98 | NAYY 4x150 SE | 97 | 98 | 0.024728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1030-2_1_3_line_99 | NAYY 4x150 SE | 98 | 105 | 0.0099288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1030-2_1_3_line_100 | NAYY 4x150 SE | 98 | 107 | 0.0020015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1030-2_1_3_line_101 | NAYY 4x150 SE | 99 | 100 | 0.01351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1030-2_1_3_line_102 | NAYY 4x150 SE | 99 | 101 | 0.019722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1030-2_1_3_line_103 | NAYY 4x150 SE | 100 | 102 | 0.0086843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1030-2_1_3_line_104 | NAYY 4x150 SE | 101 | 103 | 0.004662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1030-2_1_3_line_105 | NAYY 4x150 SE | 102 | 104 | 0.00026647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1030-2_1_3_line_106 | NAYY 4x150 SE | 104 | 105 | 0.0090058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1030-2_1_3_line_107 | NAYY 4x150 SE | 106 | 107 | 0.011119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1030-2_1_3_line_108 | NAYY 4x150 SE | 108 | 109 | 0.0437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1030-2_1_3_line_109 | NAYY 4x150 SE | 109 | 110 | 0.031527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1030-2_1_3_line_110 | NAYY 4x150 SE | 110 | 111 | 0.14315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1030-2_1_3_trafo_75 | 0.25 MVA 20/0.4 kV | 112 | 46 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2664571.9895 | 1232417.0699 | 2664572.1944 | 1232417.2
1 | 2664573.941 | 1232413.207 | 2664571.5021 | 1232416.7606 | 2664571.9895 | 1232417.0699
2 | 2664467.0763 | 1232508.2806 | 2664466.1803 | 1232501.2958 | 2664466.6985 | 1232494.0078 | 2664467.2803 | 1232485.8484
3 | 2664467.2803 | 1232485.8484 | 2664470.1548 | 1232445.5355 | 2664470.0739 | 1232442.9807
4 | 2664470.0739 | 1232442.9807 | 2664469.8837 | 1232436.9691
5 | 2664468.9377 | 1232407.0775 | 2664469.8837 | 1232436.9691
6 | 2664468.8771 | 1232405.163 | 2664468.9377 | 1232407.0775
7 | 2664501.6734 | 1232078.748 | 2664491.6086 | 1232094.4531
8 | 2664506.1657 | 1232073.2792 | 2664506.1419 | 1232073.2808 | 2664503.8322 | 1232075.3793 | 2664501.6734 | 1232078.748
9 | 2664481.1989 | 1232110.6966 | 2664491.6086 | 1232094.4531
10 | 2664506.1657 | 1232073.2792 | 2664508.9381 | 1232073.0999 | 2664511.5615 | 1232074.1957 | 2664524.5388 | 1232083.2575
11 | 2664506.1657 | 1232073.2792 | 2664495.5345 | 1232011.703
12 | 2664481.1989 | 1232110.6966 | 2664476.3556 | 1232118.254 | 2664474.292 | 1232120.711 | 2664466.9229 | 1232128.1918
13 | 2664536.6636 | 1232091.724 | 2664524.5388 | 1232083.2575
14 | 2664495.5345 | 1232011.703 | 2664492.6273 | 1232013.039 | 2664488.6121 | 1232013.1956
15 | 2664394.7936 | 1231997.2018 | 2664385.6106 | 1232013.1793
16 | 2664383.718 | 1232016.4723 | 2664385.6106 | 1232013.1793
17 | 2664394.7936 | 1231997.2018 | 2664406.4089 | 1232004.1668
18 | 2664383.718 | 1232016.4723 | 2664373.8839 | 1232033.3127
19 | 2664406.4089 | 1232004.1668 | 2664425.8889 | 1232015.8478
20 | 2664428.5 | 1232017.4135 | 2664425.8889 | 1232015.8478
21 | 2664444.3925 | 1232049.7736 | 2664442.3594 | 1232052.9479
22 | 2664442.3594 | 1232052.9479 | 2664434.9623 | 1232064.4971
23 | 2664465.211 | 1232129.9298 | 2664466.9229 | 1232128.1918
24 | 2664353.3489 | 1232068.4778 | 2664373.8839 | 1232033.3127
25 | 2664432.6732 | 1232068.0711 | 2664434.9623 | 1232064.4971
26 | 2664430.4809 | 1232071.4939 | 2664432.6732 | 1232068.0711
27 | 2664430.4809 | 1232071.4939 | 2664422.1118 | 1232084.5608
28 | 2664536.6636 | 1232091.724 | 2664547.1131 | 1232075.6038
29 | 2664536.6636 | 1232091.724 | 2664524.7333 | 1232107.747
30 | 2664476.3629 | 1231991.2483 | 2664472.0643 | 1231984.7197 | 2664468.1425 | 1231981.1415 | 2664451.5686 | 1231970.2749
31 | 2664476.3629 | 1231991.2483 | 2664477.5513 | 1232003.1579 | 2664478.7909 | 1232006.1622 | 2664484.927 | 1232011.5434 | 2664488.6121 | 1232013.1956
32 | 2664465.211 | 1232129.9298 | 2664417.278 | 1232092.1077
33 | 2664353.3489 | 1232068.4778 | 2664364.3464 | 1232075.2791 | 2664368.9593 | 1232077.9871
34 | 2664420.8446 | 1232086.5392 | 2664422.1118 | 1232084.5608
35 | 2664561.3885 | 1232053.5813 | 2664547.1131 | 1232075.6038
36 | 2664524.7333 | 1232107.747 | 2664517.9426 | 1232116.8674
37 | 2664417.278 | 1232092.1077 | 2664417.278 | 1232092.1077 | 2664420.8446 | 1232086.5392
38 | 2664399.3777 | 1232092.7835 | 2664405.3094 | 1232095.269 | 2664409.2612 | 1232096.0679 | 2664411.7025 | 1232095.7942 | 2664413.739 | 1232095.1492 | 2664415.783 | 1232093.8037 | 2664417.278 | 1232092.1077
39 | 2664397.0621 | 1232091.8133 | 2664391.9139 | 1232089.6561
40 | 2664399.3777 | 1232092.7835 | 2664397.0621 | 1232091.8133
41 | 2664368.9593 | 1232077.9871 | 2664376.6568 | 1232082.506 | 2664390.6549 | 1232089.1285 | 2664391.9139 | 1232089.6561
42 | 2664400.8123 | 1232172.7491 | 2664398.2135 | 1232205.7315 | 2664394.0014 | 1232241.5428 | 2664392.3858 | 1232247.4675
43 | 2664391.6653 | 1232265.6556 | 2664390.5553 | 1232254.1805 | 2664392.3858 | 1232247.4675
44 | 2664530.0596 | 1232175.8315 | 2664527.4694 | 1232176.2132 | 2664515.3762 | 1232181.0963 | 2664484.4186 | 1232193.3569
45 | 2664530.0596 | 1232175.8315 | 2664532.2477 | 1232175.509 | 2664546.712 | 1232176.122 | 2664562.65 | 1232177.0067 | 2664564.4395 | 1232176.831
46 | 2664484.4186 | 1232193.3569 | 2664478.0503 | 1232195.879 | 2664472.9816 | 1232199.6154 | 2664461.0648 | 1232212.5139
47 | 2664578.0461 | 1232175.4951 | 2664564.4395 | 1232176.831
48 | 2664448.8207 | 1232218.9218 | 2664454.7679 | 1232217.9634 | 2664458.9059 | 1232214.8506 | 2664461.0648 | 1232212.5139
49 | 2664578.0461 | 1232175.4951 | 2664593.7665 | 1232171.4872
50 | 2664448.8207 | 1232218.9218 | 2664451.0471 | 1232213.8956
51 | 2664448.8207 | 1232218.9218 | 2664446.7088 | 1232224.4358 | 2664445.9823 | 1232225.2259
52 | 2664595.5718 | 1232171.0269 | 2664593.7665 | 1232171.4872
53 | 2664456.3121 | 1232202.01 | 2664451.0471 | 1232213.8956
54 | 2664445.9823 | 1232225.2259 | 2664430.5222 | 1232242.0387
55 | 2664568.5837 | 1232247.6843 | 2664574.6892 | 1232238.767
56 | 2664568.5837 | 1232247.6843 | 2664565.4771 | 1232248.5622 | 2664559.2889 | 1232256.3903
57 | 2664568.5837 | 1232247.6843 | 2664571.5274 | 1232247.8608 | 2664582.7501 | 1232256.2294
58 | 2664595.5718 | 1232171.0269 | 2664600.9514 | 1232174.2208 | 2664603.4899 | 1232179.6408 | 2664613.0056 | 1232221.6601
59 | 2664487.4556 | 1232151.5663 | 2664475.3632 | 1232163.662 | 2664469.2749 | 1232172.7464 | 2664469.029 | 1232173.3014
60 | 2664498.1301 | 1232140.8888 | 2664487.4556 | 1232151.5663
61 | 2664461.8846 | 1232189.4301 | 2664469.029 | 1232173.3014
62 | 2664498.1301 | 1232140.8888 | 2664503.3868 | 1232135.6306
63 | 2664461.8846 | 1232189.4301 | 2664459.158 | 1232195.5853
64 | 2664504.3986 | 1232134.6186 | 2664503.3868 | 1232135.6306
65 | 2664456.3121 | 1232202.01 | 2664459.158 | 1232195.5853
66 | 2664504.3986 | 1232134.6186 | 2664505.6793 | 1232133.3375 | 2664513.6227 | 1232122.6692
67 | 2664513.6227 | 1232122.6692 | 2664517.9426 | 1232116.8674
68 | 2664627.9677 | 1231971.7811 | 2664596.8618 | 1232006.3659 | 2664569.5419 | 1232041.0031 | 2664561.3885 | 1232053.5813
69 | 2664406.1348 | 1232268.5587 | 2664418.1115 | 1232255.5354 | 2664430.5222 | 1232242.0387
70 | 2664471.8842 | 1232293.2282 | 2664474.5196 | 1232293.0714 | 2664480.3566 | 1232293.8907 | 2664488.3671 | 1232293.9777 | 2664493.9171 | 1232291.236 | 2664497.4233 | 1232287.4192
71 | 2664446.5226 | 1232300.5666 | 2664451.5321 | 1232296.3799 | 2664457.6149 | 1232294.0777 | 2664471.8842 | 1232293.2282
72 | 2664514.7816 | 1232273.5396 | 2664512.7332 | 1232273.1949 | 2664509.3586 | 1232274.348 | 2664499.6106 | 1232285.0382 | 2664497.4233 | 1232287.4192
73 | 2664435.7851 | 1232310.7409 | 2664441.5905 | 1232304.6888 | 2664446.5226 | 1232300.5666
74 | 2664435.7851 | 1232310.7409 | 2664447.8349 | 1232321.0005 | 2664448.4765 | 1232321.5043
75 | 2664435.7851 | 1232310.7409 | 2664434.6609 | 1232309.6614 | 2664431.9429 | 1232307.4794
76 | 2664452.9448 | 1232325.0131 | 2664448.4765 | 1232321.5043
77 | 2664422.0076 | 1232299.5035 | 2664431.9429 | 1232307.4794
78 | 2664452.9448 | 1232325.0131 | 2664461.5495 | 1232331.77
79 | 2664416.5694 | 1232295.2189 | 2664416.8169 | 1232295.3364 | 2664422.0076 | 1232299.5035
80 | 2664579.4921 | 1232279.6538 | 2664586.3099 | 1232270.047 | 2664588.2912 | 1232265.4099 | 2664587.9766 | 1232261.6151 | 2664586.28 | 1232258.8616 | 2664582.7501 | 1232256.2294
81 | 2664579.4921 | 1232279.6538 | 2664558.1493 | 1232309.7271
82 | 2664548.7163 | 1232323.3621 | 2664551.5279 | 1232319.0572 | 2664558.1493 | 1232309.7271
83 | 2664548.7163 | 1232323.3621 | 2664545.2556 | 1232328.6609
84 | 2664548.8454 | 1232269.6012 | 2664559.2889 | 1232256.3903
85 | 2664529.9458 | 1232352.1024 | 2664545.2556 | 1232328.6609
86 | 2664516.3916 | 1232372.8558 | 2664529.9458 | 1232352.1024
87 | 2664852.3916 | 1232116.2415 | 2664789.2238 | 1232125.0588 | 2664773.9488 | 1232126.2036
88 | 2664852.3916 | 1232116.2415 | 2664837.1796 | 1232097.085
89 | 2664627.9677 | 1231971.7811 | 2664636.2541 | 1231970.2257 | 2664651.3816 | 1231974.6597 | 2664656.3069 | 1231977.0768
90 | 2664391.6653 | 1232265.6556 | 2664406.1348 | 1232268.5587
91 | 2664401.952 | 1232289.0935 | 2664406.1348 | 1232268.5587
92 | 2664401.952 | 1232289.0935 | 2664410.8729 | 1232292.5146 | 2664416.5694 | 1232295.2189
93 | 2664516.3916 | 1232372.8558 | 2664503.9836 | 1232363.664
94 | 2664516.3916 | 1232372.8558 | 2664534.5605 | 1232385.3034
95 | 2664539.4704 | 1232388.6671 | 2664534.5605 | 1232385.3034
96 | 2664573.941 | 1232413.207 | 2664558.3098 | 1232401.5741 | 2664539.4704 | 1232388.6671
97 | 2664491.7387 | 1232354.593 | 2664503.9836 | 1232363.664
98 | 2664471.869 | 1232339.8734 | 2664491.7387 | 1232354.593
99 | 2664471.869 | 1232339.8734 | 2664468.7907 | 1232349.3129 | 2664468.7907 | 1232349.3129
100 | 2664471.869 | 1232339.8734 | 2664470.2948 | 1232338.6373
101 | 2664468.8132 | 1232380.7793 | 2664468.8035 | 1232367.2695
102 | 2664468.8273 | 1232400.5017 | 2664468.8132 | 1232380.7793
103 | 2664468.7973 | 1232358.5852 | 2664468.8035 | 1232367.2695
104 | 2664468.8273 | 1232400.5017 | 2664468.8296 | 1232403.6603 | 2664468.8771 | 1232405.163
105 | 2664468.7973 | 1232358.5852 | 2664468.7971 | 1232358.3187
106 | 2664468.7971 | 1232358.3187 | 2664468.7907 | 1232349.3129
107 | 2664470.2948 | 1232338.6373 | 2664461.5495 | 1232331.77
108 | 2664837.1796 | 1232097.085 | 2664833.7242 | 1232092.7336 | 2664805.9768 | 1232066.5616
109 | 2664780.8887 | 1232047.5776 | 2664799.9271 | 1232060.8553 | 2664805.9768 | 1232066.5616
110 | 2664656.3069 | 1231977.0768 | 2664780.8887 | 1232047.5776

## bus_geodata
| x | y | coords
0 | 2664572.1944 | 1232417.2
1 | 2664571.9895 | 1232417.0699
2 | 2664467.0763 | 1232508.2806
3 | 2664467.2803 | 1232485.8484
4 | 2664470.0739 | 1232442.9807
5 | 2664469.8837 | 1232436.9691
6 | 2664468.9377 | 1232407.0775
7 | 2664501.6734 | 1232078.748
8 | 2664491.6086 | 1232094.4531
9 | 2664506.1657 | 1232073.2792
10 | 2664481.1989 | 1232110.6966
11 | 2664524.5388 | 1232083.2575
12 | 2664495.5345 | 1232011.703
13 | 2664385.6106 | 1232013.1793
14 | 2664394.7936 | 1231997.2018
15 | 2664383.718 | 1232016.4723
16 | 2664406.4089 | 1232004.1668
17 | 2664425.8889 | 1232015.8478
18 | 2664444.3925 | 1232049.7736
19 | 2664442.3594 | 1232052.9479
20 | 2664428.5 | 1232017.4135
21 | 2664466.9229 | 1232128.1918
22 | 2664373.8839 | 1232033.3127
23 | 2664432.6732 | 1232068.0711
24 | 2664434.9623 | 1232064.4971
25 | 2664430.4809 | 1232071.4939
26 | 2664536.6636 | 1232091.724
27 | 2664451.5686 | 1231970.2749
28 | 2664476.3629 | 1231991.2483
29 | 2664488.6121 | 1232013.1956
30 | 2664465.211 | 1232129.9298
31 | 2664353.3489 | 1232068.4778
32 | 2664422.1118 | 1232084.5608
33 | 2664547.1131 | 1232075.6038
34 | 2664524.7333 | 1232107.747
35 | 2664417.278 | 1232092.1077
36 | 2664420.8446 | 1232086.5392
37 | 2664397.0621 | 1232091.8133
38 | 2664391.9139 | 1232089.6561
39 | 2664399.3777 | 1232092.7835
40 | 2664368.9593 | 1232077.9871
41 | 2664400.8123 | 1232172.7491
42 | 2664392.3858 | 1232247.4675
43 | 2664530.0596 | 1232175.8315
44 | 2664484.4186 | 1232193.3569
45 | 2664564.4395 | 1232176.831
46 | 2664461.0648 | 1232212.5139
47 | 2664578.0461 | 1232175.4951
48 | 2664448.8207 | 1232218.9218
49 | 2664593.7665 | 1232171.4872
50 | 2664451.0471 | 1232213.8956
51 | 2664445.9823 | 1232225.2259
52 | 2664574.6892 | 1232238.767
53 | 2664568.5837 | 1232247.6843
54 | 2664595.5718 | 1232171.0269
55 | 2664487.4556 | 1232151.5663
56 | 2664469.029 | 1232173.3014
57 | 2664498.1301 | 1232140.8888
58 | 2664461.8846 | 1232189.4301
59 | 2664503.3868 | 1232135.6306
60 | 2664459.158 | 1232195.5853
61 | 2664504.3986 | 1232134.6186
62 | 2664456.3121 | 1232202.01
63 | 2664513.6227 | 1232122.6692
64 | 2664517.9426 | 1232116.8674
65 | 2664561.3885 | 1232053.5813
66 | 2664430.5222 | 1232242.0387
67 | 2664471.8842 | 1232293.2282
68 | 2664497.4233 | 1232287.4192
69 | 2664446.5226 | 1232300.5666
70 | 2664514.7816 | 1232273.5396
71 | 2664435.7851 | 1232310.7409
72 | 2664448.4765 | 1232321.5043
73 | 2664431.9429 | 1232307.4794
74 | 2664452.9448 | 1232325.0131
75 | 2664422.0076 | 1232299.5035
76 | 2664579.4921 | 1232279.6538
77 | 2664582.7501 | 1232256.2294
78 | 2664558.1493 | 1232309.7271
79 | 2664548.7163 | 1232323.3621
80 | 2664559.2889 | 1232256.3903
81 | 2664545.2556 | 1232328.6609
82 | 2664548.8454 | 1232269.6012
83 | 2664529.9458 | 1232352.1024
84 | 2664613.0056 | 1232221.6601
85 | 2664773.9488 | 1232126.2036
86 | 2664852.3916 | 1232116.2415
87 | 2664627.9677 | 1231971.7811
88 | 2664391.6653 | 1232265.6556
89 | 2664406.1348 | 1232268.5587
90 | 2664401.952 | 1232289.0935
91 | 2664416.5694 | 1232295.2189
92 | 2664516.3916 | 1232372.8558
93 | 2664534.5605 | 1232385.3034
94 | 2664539.4704 | 1232388.6671
95 | 2664573.941 | 1232413.207
96 | 2664503.9836 | 1232363.664
97 | 2664491.7387 | 1232354.593
98 | 2664471.869 | 1232339.8734
99 | 2664468.8132 | 1232380.7793
100 | 2664468.8035 | 1232367.2695
101 | 2664468.8273 | 1232400.5017
102 | 2664468.7973 | 1232358.5852
103 | 2664468.8771 | 1232405.163
104 | 2664468.7971 | 1232358.3187
105 | 2664468.7907 | 1232349.3129
106 | 2664461.5495 | 1232331.77
107 | 2664470.2948 | 1232338.6373
108 | 2664837.1796 | 1232097.085
109 | 2664805.9768 | 1232066.5616
110 | 2664780.8887 | 1232047.5776
111 | 2664656.3069 | 1231977.0768
112 | 2664448.8207 | 1232218.9218

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97741 | -0.15854 | 0.0002706 | 6.7818e-05
1 | 0.97741 | -0.15854 | 0.00031308 | 7.8466e-05
2 | 0.97692 | -0.1621 | 0.00094124 | 0.0002359
3 | 0.97695 | -0.16187 | 0.0035496 | 0.00088962
4 | 0.97723 | -0.15986 | 0.0045324 | 0.0011359
5 | 0.97731 | -0.15929 | 0.0014536 | 0.00036431
6 | 0.97777 | -0.15601 | 0.0029645 | 0.00074297
7 | 0.98567 | -0.10026 | 0.00058175 | 0.0001458
8 | 0.98481 | -0.10635 | 0.00064857 | 0.00016255
9 | 0.98601 | -0.097893 | 0.0013309 | 0.00033357
10 | 0.98394 | -0.11253 | 0.0022734 | 0.00056976
11 | 0.98715 | -0.089801 | 0.00040111 | 0.00010053
12 | 0.98573 | -0.099909 | 0.00086337 | 0.00021638
13 | 0.97946 | -0.14449 | 0.00043841 | 0.00010988
14 | 0.97939 | -0.14499 | 0 | 0
15 | 0.97948 | -0.14437 | 0 | 0
16 | 0.97934 | -0.14535 | 0.0010392 | 0.00026044
17 | 0.97929 | -0.14572 | 0.00092435 | 0.00023166
18 | 0.98079 | -0.13497 | 0.00063358 | 0.00015879
19 | 0.9808 | -0.13494 | 0.0007399 | 0.00018544
20 | 0.97929 | -0.14574 | 0.00063317 | 0.00015869
21 | 0.983 | -0.11927 | 0.0022581 | 0.00056593
22 | 0.97957 | -0.14375 | 0.0029429 | 0.00073757
23 | 0.98084 | -0.13467 | 0.00092956 | 0.00023297
24 | 0.98082 | -0.13475 | 0.00038627 | 9.6808e-05
25 | 0.98085 | -0.13456 | 0.00038627 | 9.6808e-05
26 | 0.98795 | -0.084171 | 0 | 0
27 | 0.98558 | -0.10095 | 0.0014056 | 0.00035228
28 | 0.98565 | -0.10047 | 0 | 0
29 | 0.9857 | -0.10008 | 0.00086325 | 0.00021635
30 | 0.9829 | -0.11994 | 0.0047852 | 0.0011993
31 | 0.97992 | -0.14121 | 0 | 0
32 | 0.98092 | -0.13406 | 0.00058126 | 0.00014568
33 | 0.98785 | -0.084878 | 0.00065136 | 0.00016325
34 | 0.98913 | -0.075847 | 0.00041703 | 0.00010452
35 | 0.98097 | -0.1337 | 0.0013872 | 0.00034767
36 | 0.98093 | -0.13397 | 0.00038914 | 9.7526e-05
37 | 0.98045 | -0.13745 | 0.0032227 | 0.00080768
38 | 0.98035 | -0.13816 | 0.0051658 | 0.0012947
39 | 0.9805 | -0.13704 | 0.00077854 | 0.00019512
40 | 0.98008 | -0.14008 | 0.0011588 | 0.00029043
41 | 0.98968 | -0.071654 | 0.0027386 | 0.00068635
42 | 0.98998 | -0.069551 | 0.0025271 | 0.00063334
43 | 0.9994 | -0.0042029 | 0.00038959 | 9.7639e-05
44 | 0.99965 | -0.002446 | 0.0043823 | 0.0010983
45 | 0.99924 | -0.0053042 | 0.00051798 | 0.00012982
46 | 1 | 0 | -0.15742 | -0.039562
47 | 0.99919 | -0.0056702 | 0 | 0
48 | 0.99848 | -0.01052 | 0 | 0
49 | 0.99913 | -0.0061044 | 0.00063009 | 0.00015792
50 | 0.99802 | -0.013671 | 0.0016654 | 0.00041739
51 | 0.99757 | -0.016749 | 0.0020491 | 0.00051355
52 | 0.97455 | -0.17906 | 0.002719 | 0.00068145
53 | 0.97459 | -0.17875 | 0 | 0
54 | 0.99913 | -0.0061425 | 0 | 0
55 | 0.99269 | -0.050845 | 0.0017728 | 0.00044432
56 | 0.99462 | -0.037321 | 0.0038582 | 0.00096696
57 | 0.99171 | -0.057723 | 0.0013283 | 0.00033289
58 | 0.99591 | -0.028334 | 0.0024015 | 0.00060187
59 | 0.99124 | -0.061014 | 0.0013291 | 0.0003331
60 | 0.99643 | -0.024748 | 0.0013011 | 0.00032609
61 | 0.99115 | -0.061628 | 0.00067659 | 0.00016957
62 | 0.99698 | -0.020917 | 0.0013006 | 0.00032597
63 | 0.99024 | -0.06802 | 0.00018748 | 4.6988e-05
64 | 0.98981 | -0.07107 | 0.00018748 | 4.6988e-05
65 | 0.98774 | -0.085668 | 0.00047971 | 0.00012023
66 | 0.99468 | -0.036747 | 0.0020716 | 0.00051918
67 | 0.98253 | -0.1221 | 0.0050363 | 0.0012622
68 | 0.98221 | -0.12438 | 0.0065549 | 0.0016428
69 | 0.98304 | -0.11845 | 0.0015807 | 0.00039616
70 | 0.98216 | -0.1247 | 0.0013235 | 0.00033171
71 | 0.98335 | -0.11624 | 0 | 0
72 | 0.98197 | -0.12601 | 0.0016599 | 0.000416
73 | 0.98388 | -0.11252 | 0.0011359 | 0.00028469
74 | 0.98152 | -0.12925 | 0.001016 | 0.00025464
75 | 0.98522 | -0.10302 | 0.0013604 | 0.00034095
76 | 0.97512 | -0.175 | 0.0022345 | 0.00056003
77 | 0.97474 | -0.17768 | 0.0030166 | 0.00075603
78 | 0.97572 | -0.17065 | 0.0022927 | 0.00057461
79 | 0.97605 | -0.16829 | 0.002799 | 0.00070149
80 | 0.97453 | -0.17921 | 0.0017023 | 0.00042663
81 | 0.9762 | -0.1672 | 0.001657 | 0.00041528
82 | 0.97449 | -0.17949 | 0.001582 | 0.00039649
83 | 0.97694 | -0.16193 | 0.00097586 | 0.00024457
84 | 0.99896 | -0.0072727 | 0.0020404 | 0.00051137
85 | 0.98668 | -0.093314 | 0.00030083 | 7.5394e-05
86 | 0.98671 | -0.093067 | 0 | 0
87 | 0.98737 | -0.088324 | 0 | 0
88 | 0.99012 | -0.068558 | 0 | 0
89 | 0.99023 | -0.067768 | 0 | 0
90 | 0.9878 | -0.08481 | 0 | 0
91 | 0.98596 | -0.097762 | 0.0058677 | 0.0014706
92 | 0.97763 | -0.15701 | 0 | 0
93 | 0.97748 | -0.15803 | 0.00078251 | 0.00019611
94 | 0.97745 | -0.15825 | 0.0030675 | 0.00076878
95 | 0.97742 | -0.15851 | 0 | 0
96 | 0.97815 | -0.15323 | 0.0017394 | 0.00043593
97 | 0.97871 | -0.14923 | 0.00087527 | 0.00021936
98 | 0.97965 | -0.14252 | 0 | 0
99 | 0.97834 | -0.15195 | 0.0021632 | 0.00054215
100 | 0.97867 | -0.14952 | 0.004884 | 0.0012241
101 | 0.9779 | -0.15505 | 0.00080581 | 0.00020196
102 | 0.97895 | -0.14752 | 0.00086239 | 0.00021613
103 | 0.9778 | -0.15574 | 0.00082409 | 0.00020654
104 | 0.97896 | -0.14745 | 0.00162 | 0.000406
105 | 0.97929 | -0.14514 | 0.00077917 | 0.00019528
106 | 0.98065 | -0.1354 | 0.001728 | 0.00043309
107 | 0.9798 | -0.14145 | 0.0009597 | 0.00024052
108 | 0.98672 | -0.092989 | 0.0005597 | 0.00014027
109 | 0.98678 | -0.092598 | 0.00081578 | 0.00020445
110 | 0.98685 | -0.092051 | 0.0003338 | 8.3658e-05
111 | 0.98727 | -0.089069 | 0.00040883 | 0.00010246
112 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0002706 | -6.7818e-05 | 0.0002706 | 6.7815e-05 | 2.5729e-11 | -3.0315e-09 | 0.00041196 | 0.00041196 | 0.00041196 | 0.97741 | -0.15854 | 0.97741 | -0.15854 | 0.15258
1 | -0.00058368 | -0.00014628 | 0.00058368 | 0.00014622 | 2.4081e-09 | -6.0329e-08 | 0.0008886 | 0.00088857 | 0.0008886 | 0.97741 | -0.15854 | 0.97742 | -0.15851 | 0.32911
2 | -0.00094124 | -0.0002359 | 0.00094126 | 0.00023562 | 2.8892e-08 | -2.7097e-07 | 0.0014337 | 0.0014336 | 0.0014337 | 0.97692 | -0.1621 | 0.97695 | -0.16187 | 0.53099
3 | -0.0044909 | -0.0011252 | 0.0044921 | 0.0011252 | 1.2545e-06 | -5.5714e-08 | 0.0068401 | 0.0068399 | 0.0068401 | 0.97695 | -0.16187 | 0.97723 | -0.15986 | 2.5334
4 | -0.0090245 | -0.0022611 | 0.0090252 | 0.0022613 | 7.0868e-07 | 1.9721e-07 | 0.013741 | 0.013741 | 0.013741 | 0.97723 | -0.15986 | 0.97731 | -0.15929 | 5.0894
5 | -0.010479 | -0.0026256 | 0.010484 | 0.0026271 | 4.7502e-06 | 1.4521e-06 | 0.015954 | 0.015954 | 0.015954 | 0.97731 | -0.15929 | 0.97777 | -0.15601 | 5.9091
6 | -0.013448 | -0.00337 | 0.013449 | 0.0033702 | 5.0063e-07 | 1.6852e-07 | 0.020466 | 0.020466 | 0.020466 | 0.97777 | -0.15601 | 0.9778 | -0.15574 | 7.5799
7 | 0.031843 | 0.0079947 | -0.031816 | -0.0079845 | 2.6903e-05 | 1.011e-05 | 0.048076 | 0.048076 | 0.048076 | 0.98567 | -0.10026 | 0.98481 | -0.10635 | 17.806
8 | -0.032424 | -0.0081405 | 0.032435 | 0.0081445 | 1.0686e-05 | 4.0188e-06 | 0.048954 | 0.048954 | 0.048954 | 0.98567 | -0.10026 | 0.98601 | -0.097893 | 18.1312
9 | 0.031167 | 0.007822 | -0.03114 | -0.007812 | 2.6702e-05 | 1.0025e-05 | 0.047096 | 0.047096 | 0.047096 | 0.98481 | -0.10635 | 0.98394 | -0.11253 | 17.443
10 | -0.036899 | -0.0092618 | 0.036941 | 0.0092775 | 4.1511e-05 | 1.5692e-05 | 0.055691 | 0.055691 | 0.055691 | 0.98601 | -0.097893 | 0.98715 | -0.089801 | 20.6262
11 | 0.0031333 | 0.00078377 | -0.0031324 | -0.00078423 | 8.7169e-07 | -4.6151e-07 | 0.004728 | 0.0047283 | 0.0047283 | 0.98601 | -0.097893 | 0.98573 | -0.099909 | 1.7512
12 | 0.028867 | 0.0072422 | -0.02884 | -0.0072321 | 2.6982e-05 | 1.009e-05 | 0.043658 | 0.043658 | 0.043658 | 0.98394 | -0.11253 | 0.983 | -0.11927 | 16.1697
13 | -0.037342 | -0.009378 | 0.037371 | 0.0093891 | 2.9245e-05 | 1.1059e-05 | 0.056295 | 0.056295 | 0.056295 | 0.98715 | -0.089801 | 0.98795 | -0.084171 | 20.8501
14 | 0.0022691 | 0.00056785 | -0.002269 | -0.00056792 | 5.2834e-08 | -7.1685e-08 | 0.003425 | 0.003425 | 0.003425 | 0.98573 | -0.099909 | 0.9857 | -0.10008 | 1.2685
15 | 0.0025971 | 0.00065021 | -0.0025969 | -0.00065038 | 1.7899e-07 | -1.6308e-07 | 0.0039453 | 0.0039454 | 0.0039454 | 0.97946 | -0.14449 | 0.97939 | -0.14499 | 1.4612
16 | -0.0030355 | -0.00076009 | 0.0030355 | 0.00076006 | 5.0397e-08 | -2.8421e-08 | 0.0046113 | 0.0046113 | 0.0046113 | 0.97946 | -0.14449 | 0.97948 | -0.14437 | 1.7079
17 | 0.0025969 | 0.00065038 | -0.0025968 | -0.0006505 | 1.3155e-07 | -1.1983e-07 | 0.0039454 | 0.0039454 | 0.0039454 | 0.97939 | -0.14499 | 0.97934 | -0.14535 | 1.4613
18 | -0.0030355 | -0.00076006 | 0.0030358 | 0.00075991 | 2.5875e-07 | -1.4595e-07 | 0.0046113 | 0.0046112 | 0.0046113 | 0.97948 | -0.14437 | 0.97957 | -0.14375 | 1.7079
19 | 0.0015576 | 0.00039006 | -0.0015575 | -0.00039031 | 7.9381e-08 | -2.5526e-07 | 0.0023665 | 0.0023666 | 0.0023666 | 0.97934 | -0.14535 | 0.97929 | -0.14572 | 0.87653
20 | 0.00063318 | 0.00015865 | -0.00063317 | -0.00015869 | 1.7585e-09 | -3.7629e-08 | 0.00096209 | 0.0009621 | 0.0009621 | 0.97929 | -0.14572 | 0.97929 | -0.14574 | 0.35633
21 | -0.00063358 | -0.00015879 | 0.00063358 | 0.00015874 | 2.1734e-09 | -4.6737e-08 | 0.00096124 | 0.00096122 | 0.00096124 | 0.98079 | -0.13497 | 0.9808 | -0.13494 | 0.35602
22 | -0.0013735 | -0.00034418 | 0.0013735 | 0.00034402 | 3.7159e-08 | -1.588e-07 | 0.0020838 | 0.0020837 | 0.0020838 | 0.9808 | -0.13494 | 0.98082 | -0.13475 | 0.77177
23 | 0.026582 | 0.0066662 | -0.026579 | -0.0066653 | 2.4649e-06 | 9.1713e-07 | 0.04024 | 0.04024 | 0.04024 | 0.983 | -0.11927 | 0.9829 | -0.11994 | 14.9037
24 | -0.0059787 | -0.0014975 | 0.0059808 | 0.0014978 | 2.0957e-06 | 2.9324e-07 | 0.0090817 | 0.0090815 | 0.0090817 | 0.97957 | -0.14375 | 0.97992 | -0.14121 | 3.3636
25 | 0.0017598 | 0.00044078 | -0.0017598 | -0.00044083 | 1.8876e-08 | -4.6307e-08 | 0.0026697 | 0.0026697 | 0.0026697 | 0.98084 | -0.13467 | 0.98082 | -0.13475 | 0.98878
26 | -0.0026894 | -0.00067375 | 0.0026894 | 0.00067372 | 4.222e-08 | -3.5064e-08 | 0.0040799 | 0.0040799 | 0.0040799 | 0.98084 | -0.13467 | 0.98085 | -0.13456 | 1.5111
27 | -0.0030757 | -0.00077052 | 0.0030759 | 0.00077041 | 2.108e-07 | -1.1479e-07 | 0.0046659 | 0.0046658 | 0.0046659 | 0.98085 | -0.13456 | 0.98092 | -0.13406 | 1.7281
28 | 0.0035528 | 0.00088436 | -0.0035524 | -0.00088447 | 3.4298e-07 | -1.1405e-07 | 0.0053489 | 0.005349 | 0.005349 | 0.98795 | -0.084171 | 0.98785 | -0.084878 | 1.9811
29 | -0.040924 | -0.010273 | 0.040971 | 0.010291 | 4.7369e-05 | 1.7963e-05 | 0.061644 | 0.061644 | 0.061644 | 0.98795 | -0.084171 | 0.98913 | -0.075847 | 22.8312
30 | -0.0014056 | -0.00035228 | 0.0014057 | 0.00035189 | 9.2573e-08 | -3.8425e-07 | 0.0021222 | 0.002122 | 0.0021222 | 0.98558 | -0.10095 | 0.98565 | -0.10047 | 0.78598
31 | -0.0014057 | -0.00035189 | 0.0014058 | 0.00035157 | 7.7037e-08 | -3.1985e-07 | 0.002122 | 0.0021219 | 0.002122 | 0.98565 | -0.10047 | 0.9857 | -0.10008 | 0.78593
32 | 0.021794 | 0.005466 | -0.021753 | -0.0054508 | 4.1481e-05 | 1.5182e-05 | 0.032996 | 0.032996 | 0.032996 | 0.9829 | -0.11994 | 0.98097 | -0.1337 | 12.2208
33 | -0.0059808 | -0.0014978 | 0.0059818 | 0.0014979 | 9.4073e-07 | 1.315e-07 | 0.0090815 | 0.0090814 | 0.0090815 | 0.97992 | -0.14121 | 0.98008 | -0.14008 | 3.3635
34 | -0.0036571 | -0.00091609 | 0.0036572 | 0.00091608 | 4.5119e-08 | -1.2305e-08 | 0.0055476 | 0.0055476 | 0.0055476 | 0.98092 | -0.13406 | 0.98093 | -0.13397 | 2.0547
35 | 0.0029011 | 0.00072122 | -0.0029008 | -0.00072144 | 3.1244e-07 | -2.1579e-07 | 0.0043679 | 0.004368 | 0.004368 | 0.98785 | -0.084878 | 0.98774 | -0.085668 | 1.6178
36 | -0.041388 | -0.010396 | 0.041416 | 0.010406 | 2.7514e-05 | 1.0436e-05 | 0.062271 | 0.062271 | 0.062271 | 0.98913 | -0.075847 | 0.98981 | -0.07107 | 23.0635
37 | 0.0040465 | 0.0010136 | -0.0040463 | -0.0010136 | 1.5545e-07 | -2.3692e-08 | 0.0061378 | 0.0061379 | 0.0061379 | 0.98097 | -0.1337 | 0.98093 | -0.13397 | 2.2733
38 | 0.016319 | 0.0040896 | -0.016312 | -0.0040869 | 7.557e-06 | 2.6571e-06 | 0.024754 | 0.024754 | 0.024754 | 0.98097 | -0.1337 | 0.9805 | -0.13704 | 9.1682
39 | 0.012309 | 0.0030838 | -0.012308 | -0.0030834 | 1.2156e-06 | 3.9715e-07 | 0.018682 | 0.018682 | 0.018682 | 0.98045 | -0.13745 | 0.98035 | -0.13816 | 6.9191
40 | -0.015532 | -0.0038915 | 0.015533 | 0.0038918 | 8.7053e-07 | 3.0316e-07 | 0.023573 | 0.023573 | 0.023573 | 0.98045 | -0.13745 | 0.9805 | -0.13704 | 8.7306
41 | 0.0071425 | 0.0017887 | -0.0071406 | -0.0017883 | 1.8903e-06 | 4.0212e-07 | 0.010841 | 0.010841 | 0.010841 | 0.98035 | -0.13816 | 0.98008 | -0.14008 | 4.0151
42 | -0.0027386 | -0.00068635 | 0.0027394 | 0.00068569 | 7.9639e-07 | -6.6139e-07 | 0.0041175 | 0.0041172 | 0.0041175 | 0.98968 | -0.071654 | 0.98998 | -0.069551 | 1.525
43 | -0.0052664 | -0.001319 | 0.0052672 | 0.0013191 | 7.2278e-07 | 4.026e-08 | 0.0079156 | 0.0079155 | 0.0079156 | 0.98998 | -0.069551 | 0.99012 | -0.068558 | 2.9317
44 | -0.0035792 | -0.00089558 | 0.00358 | 0.00089527 | 8.6736e-07 | -3.0807e-07 | 0.0053285 | 0.0053283 | 0.0053285 | 0.9994 | -0.0042029 | 0.99965 | -0.002446 | 1.9735
45 | 0.0031896 | 0.00079794 | -0.0031891 | -0.00079821 | 4.8472e-07 | -2.6491e-07 | 0.0047485 | 0.0047486 | 0.0047486 | 0.9994 | -0.0042029 | 0.99924 | -0.0053042 | 1.7588
46 | -0.0079623 | -0.0019936 | 0.007965 | 0.0019942 | 2.6914e-06 | 6.3242e-07 | 0.011852 | 0.011851 | 0.011852 | 0.99965 | -0.002446 | 1 | 0 | 4.3895
47 | 0.0026711 | 0.00066839 | -0.002671 | -0.00066851 | 1.3496e-07 | -1.2718e-07 | 0.0039773 | 0.0039774 | 0.0039774 | 0.99924 | -0.0053042 | 0.99919 | -0.0056702 | 1.4731
48 | 0.14866 | 0.037567 | -0.14844 | -0.037483 | 0.0002198 | 8.4162e-05 | 0.22131 | 0.22131 | 0.22131 | 1 | 0 | 0.99848 | -0.01052 | 40.9839
49 | 0.002671 | 0.00066851 | -0.0026708 | -0.00066867 | 1.6015e-07 | -1.5089e-07 | 0.0039774 | 0.0039774 | 0.0039774 | 0.99919 | -0.0056702 | 0.99913 | -0.0061044 | 1.4731
50 | 0.057838 | 0.014576 | -0.057812 | -0.014566 | 2.5502e-05 | 9.7366e-06 | 0.086223 | 0.086223 | 0.086223 | 0.99848 | -0.01052 | 0.99802 | -0.013671 | 31.9345
51 | 0.090599 | 0.022907 | -0.09052 | -0.022877 | 7.9463e-05 | 3.0471e-05 | 0.13509 | 0.13509 | 0.13509 | 0.99848 | -0.01052 | 0.99757 | -0.016749 | 50.0332
52 | 0.0020407 | 0.00051075 | -0.0020407 | -0.00051077 | 1.0737e-08 | -2.027e-08 | 0.003039 | 0.003039 | 0.003039 | 0.99913 | -0.0061044 | 0.99913 | -0.0061425 | 1.1256
53 | 0.056147 | 0.014149 | -0.05609 | -0.014127 | 5.6883e-05 | 2.1708e-05 | 0.08374 | 0.08374 | 0.08374 | 0.99802 | -0.013671 | 0.99698 | -0.020917 | 31.0149
54 | 0.088471 | 0.022363 | -0.088222 | -0.022268 | 0.00024846 | 9.5264e-05 | 0.13203 | 0.13203 | 0.13203 | 0.99757 | -0.016749 | 0.99468 | -0.036747 | 48.9012
55 | -0.002719 | -0.00068145 | 0.0027191 | 0.00068136 | 1.1623e-07 | -8.9959e-08 | 0.0041516 | 0.0041515 | 0.0041516 | 0.97455 | -0.17906 | 0.97459 | -0.17875 | 1.5376
56 | 0.0032845 | 0.00082284 | -0.0032843 | -0.00082293 | 2.0725e-07 | -8.4852e-08 | 0.0050147 | 0.0050148 | 0.0050148 | 0.97459 | -0.17875 | 0.97453 | -0.17921 | 1.8573
57 | -0.0060037 | -0.0015042 | 0.0060046 | 0.0015043 | 8.8857e-07 | 1.3053e-07 | 0.0091663 | 0.0091662 | 0.0091663 | 0.97459 | -0.17875 | 0.97474 | -0.17768 | 3.3949
58 | 0.0020407 | 0.00051077 | -0.0020404 | -0.00051137 | 3.1887e-07 | -6.0179e-07 | 0.003039 | 0.0030393 | 0.0030393 | 0.99913 | -0.0061425 | 0.99896 | -0.0072727 | 1.1257
59 | -0.04702 | -0.011827 | 0.047108 | 0.01186 | 8.8835e-05 | 3.3796e-05 | 0.070496 | 0.070496 | 0.070496 | 0.99269 | -0.050845 | 0.99462 | -0.037321 | 26.1097
60 | 0.045247 | 0.011382 | -0.045203 | -0.011366 | 4.3357e-05 | 1.6481e-05 | 0.067839 | 0.067839 | 0.067839 | 0.99269 | -0.050845 | 0.99171 | -0.057723 | 25.1255
61 | -0.050967 | -0.012827 | 0.051031 | 0.012852 | 6.4028e-05 | 2.4397e-05 | 0.076268 | 0.076268 | 0.076268 | 0.99462 | -0.037321 | 0.99591 | -0.028334 | 28.2474
62 | 0.043875 | 0.011033 | -0.043855 | -0.011025 | 2.0116e-05 | 7.6408e-06 | 0.065846 | 0.065846 | 0.065846 | 0.99171 | -0.057723 | 0.99124 | -0.061014 | 24.3873
63 | -0.053432 | -0.013454 | 0.053459 | 0.013464 | 2.6789e-05 | 1.0216e-05 | 0.079856 | 0.079856 | 0.079856 | 0.99591 | -0.028334 | 0.99643 | -0.024748 | 29.5763
64 | 0.042526 | 0.010692 | -0.042522 | -0.010691 | 3.6406e-06 | 1.3818e-06 | 0.063851 | 0.063851 | 0.063851 | 0.99124 | -0.061014 | 0.99115 | -0.061628 | 23.6484
65 | -0.05476 | -0.01379 | 0.054789 | 0.013801 | 2.9339e-05 | 1.1192e-05 | 0.081799 | 0.081799 | 0.081799 | 0.99643 | -0.024748 | 0.99698 | -0.020917 | 30.296
66 | 0.041846 | 0.010521 | -0.041808 | -0.010507 | 3.7232e-05 | 1.4125e-05 | 0.062835 | 0.062835 | 0.062835 | 0.99115 | -0.061628 | 0.99024 | -0.06802 | 23.2722
67 | 0.041621 | 0.01046 | -0.041603 | -0.010453 | 1.7661e-05 | 6.6998e-06 | 0.062553 | 0.062553 | 0.062553 | 0.99024 | -0.06802 | 0.98981 | -0.07107 | 23.1679
68 | 0.0024211 | 0.00060121 | -0.0024202 | -0.00060223 | 8.759e-07 | -1.0145e-06 | 0.0036453 | 0.0036458 | 0.0036458 | 0.98774 | -0.085668 | 0.98737 | -0.088324 | 1.3503
69 | 0.086151 | 0.021749 | -0.085777 | -0.021605 | 0.00037374 | 0.00014328 | 0.12893 | 0.12893 | 0.12893 | 0.99468 | -0.036747 | 0.99023 | -0.067768 | 47.7535
70 | 0.007881 | 0.0019749 | -0.0078785 | -0.0019743 | 2.4817e-06 | 6.0105e-07 | 0.011935 | 0.011936 | 0.011936 | 0.98253 | -0.1221 | 0.98221 | -0.12438 | 4.4206
71 | -0.012917 | -0.0032371 | 0.012924 | 0.0032392 | 6.5259e-06 | 2.1637e-06 | 0.019563 | 0.019563 | 0.019563 | 0.98253 | -0.1221 | 0.98304 | -0.11845 | 7.2455
72 | 0.0013236 | 0.00033144 | -0.0013235 | -0.00033171 | 5.8567e-08 | -2.7292e-07 | 0.0020051 | 0.0020052 | 0.0020052 | 0.98221 | -0.12438 | 0.98216 | -0.1247 | 0.74267
73 | -0.014505 | -0.0036354 | 0.014509 | 0.0036369 | 4.456e-06 | 1.526e-06 | 0.021955 | 0.021955 | 0.021955 | 0.98304 | -0.11845 | 0.98335 | -0.11624 | 8.1316
74 | 0.057112 | 0.014352 | -0.057034 | -0.014323 | 7.7583e-05 | 2.9629e-05 | 0.086436 | 0.086436 | 0.086436 | 0.98335 | -0.11624 | 0.98197 | -0.12601 | 32.0133
75 | -0.071621 | -0.017989 | 0.071658 | 0.018003 | 3.6979e-05 | 1.4159e-05 | 0.10839 | 0.10839 | 0.10839 | 0.98335 | -0.11624 | 0.98388 | -0.11252 | 40.1449
76 | 0.055374 | 0.013907 | -0.055349 | -0.013897 | 2.4968e-05 | 9.5311e-06 | 0.083921 | 0.083921 | 0.083921 | 0.98197 | -0.12601 | 0.98152 | -0.12925 | 31.0818
77 | -0.072794 | -0.018288 | 0.07289 | 0.018325 | 9.6389e-05 | 3.6911e-05 | 0.11011 | 0.11011 | 0.11011 | 0.98388 | -0.11252 | 0.98522 | -0.10302 | 40.7812
78 | 0.054333 | 0.013643 | -0.054287 | -0.013625 | 4.6331e-05 | 1.7682e-05 | 0.08238 | 0.08238 | 0.08238 | 0.98152 | -0.12925 | 0.98065 | -0.1354 | 30.5113
79 | -0.07425 | -0.018666 | 0.074305 | 0.018687 | 5.4406e-05 | 2.0837e-05 | 0.11216 | 0.11216 | 0.11216 | 0.98522 | -0.10302 | 0.98596 | -0.097762 | 41.5422
80 | 0.0090245 | 0.0022613 | -0.0090212 | -0.0022604 | 3.3452e-06 | 9.3413e-07 | 0.013771 | 0.013771 | 0.013771 | 0.97512 | -0.175 | 0.97474 | -0.17768 | 5.1005
81 | -0.011259 | -0.0028213 | 0.011266 | 0.0028235 | 6.7926e-06 | 2.1522e-06 | 0.017181 | 0.017181 | 0.017181 | 0.97512 | -0.175 | 0.97572 | -0.17065 | 6.3633
82 | -0.013559 | -0.0033981 | 0.013563 | 0.0033996 | 4.4241e-06 | 1.4944e-06 | 0.020677 | 0.020677 | 0.020677 | 0.97572 | -0.17065 | 0.97605 | -0.16829 | 7.6583
83 | -0.016362 | -0.0041011 | 0.016364 | 0.0041019 | 2.4573e-06 | 8.6599e-07 | 0.024944 | 0.024944 | 0.024944 | 0.97605 | -0.16829 | 0.9762 | -0.1672 | 9.2387
84 | 0.0015821 | 0.0003963 | -0.001582 | -0.00039649 | 6.1319e-08 | -1.8623e-07 | 0.0024156 | 0.0024157 | 0.0024157 | 0.97453 | -0.17921 | 0.97449 | -0.17949 | 0.89469
85 | -0.018021 | -0.0045172 | 0.018035 | 0.0045219 | 1.3184e-05 | 4.7203e-06 | 0.02747 | 0.02747 | 0.02747 | 0.9762 | -0.1672 | 0.97694 | -0.16193 | 10.1741
86 | -0.01901 | -0.0047665 | 0.019023 | 0.0047712 | 1.2969e-05 | 4.6775e-06 | 0.028956 | 0.028956 | 0.028956 | 0.97694 | -0.16193 | 0.97763 | -0.15701 | 10.7246
87 | -0.00030083 | -7.5394e-05 | 0.00030084 | 7.4388e-05 | 1.0151e-08 | -1.0064e-06 | 0.00045368 | 0.00045332 | 0.00045368 | 0.98668 | -0.093314 | 0.98671 | -0.093067 | 0.16803
88 | -0.00030084 | -7.4388e-05 | 0.00030084 | 7.4077e-05 | 3.136e-09 | -3.1125e-07 | 0.00045332 | 0.00045321 | 0.00045332 | 0.98671 | -0.093067 | 0.98672 | -0.092989 | 0.1679
89 | 0.0024202 | 0.00060223 | -0.0024199 | -0.00060251 | 2.4619e-07 | -2.849e-07 | 0.0036458 | 0.0036459 | 0.0036459 | 0.98737 | -0.088324 | 0.98727 | -0.089069 | 1.3503
90 | -0.0052672 | -0.0013191 | 0.0052677 | 0.0013191 | 5.7534e-07 | 3.1996e-08 | 0.0079155 | 0.0079154 | 0.0079155 | 0.99012 | -0.068558 | 0.99023 | -0.067768 | 2.9317
91 | 0.080509 | 0.020286 | -0.080318 | -0.020213 | 0.00019153 | 7.3397e-05 | 0.12102 | 0.12102 | 0.12102 | 0.99023 | -0.067768 | 0.9878 | -0.08481 | 44.8219
92 | 0.080318 | 0.020213 | -0.080173 | -0.020157 | 0.00014494 | 5.5545e-05 | 0.12102 | 0.12102 | 0.12102 | 0.9878 | -0.08481 | 0.98596 | -0.097762 | 44.822
93 | -0.023458 | -0.0058817 | 0.02347 | 0.0058863 | 1.2284e-05 | 4.531e-06 | 0.035705 | 0.035705 | 0.035705 | 0.97763 | -0.15701 | 0.97815 | -0.15323 | 13.2242
94 | 0.0044344 | 0.0011105 | -0.0044338 | -0.0011106 | 6.2603e-07 | -3.5334e-08 | 0.0067492 | 0.0067493 | 0.0067493 | 0.97763 | -0.15701 | 0.97748 | -0.15803 | 2.4997
95 | 0.0036513 | 0.00091445 | -0.0036512 | -0.00091448 | 1.1473e-07 | -3.0475e-08 | 0.0055581 | 0.0055581 | 0.0055581 | 0.97748 | -0.15803 | 0.97745 | -0.15825 | 2.0586
96 | 0.0005837 | 0.0001457 | -0.00058368 | -0.00014622 | 2.0847e-08 | -5.2243e-07 | 0.00088838 | 0.00088857 | 0.00088857 | 0.97745 | -0.15825 | 0.97742 | -0.15851 | 0.3291
97 | -0.02521 | -0.0063222 | 0.025224 | 0.0063274 | 1.3986e-05 | 5.1879e-06 | 0.038351 | 0.038351 | 0.038351 | 0.97815 | -0.15323 | 0.97871 | -0.14923 | 14.2042
98 | -0.026099 | -0.0065467 | 0.026123 | 0.0065558 | 2.4297e-05 | 9.0341e-06 | 0.039682 | 0.039682 | 0.039682 | 0.97871 | -0.14923 | 0.97965 | -0.14252 | 14.6971
99 | 0.025424 | 0.0063758 | -0.025415 | -0.0063723 | 9.2402e-06 | 3.429e-06 | 0.038619 | 0.038619 | 0.038619 | 0.97965 | -0.14252 | 0.97929 | -0.14514 | 14.3033
100 | -0.051547 | -0.012932 | 0.051555 | 0.012934 | 7.6571e-06 | 2.9198e-06 | 0.078301 | 0.078301 | 0.078301 | 0.97965 | -0.14252 | 0.9798 | -0.14145 | 29.0003
101 | -0.01725 | -0.0043236 | 0.017255 | 0.0043256 | 5.8027e-06 | 2.0621e-06 | 0.026236 | 0.026236 | 0.026236 | 0.97834 | -0.15195 | 0.97867 | -0.14952 | 9.7171
102 | 0.015086 | 0.0037814 | -0.01508 | -0.0037792 | 6.4798e-06 | 2.2447e-06 | 0.022946 | 0.022946 | 0.022946 | 0.97834 | -0.15195 | 0.9779 | -0.15505 | 8.4985
103 | -0.022139 | -0.0055497 | 0.022146 | 0.0055519 | 6.1404e-06 | 2.2525e-06 | 0.033662 | 0.033662 | 0.033662 | 0.97867 | -0.14952 | 0.97895 | -0.14752 | 12.4674
104 | 0.014274 | 0.0035772 | -0.014273 | -0.0035767 | 1.3724e-06 | 4.6936e-07 | 0.02172 | 0.02172 | 0.02172 | 0.9779 | -0.15505 | 0.9778 | -0.15574 | 8.0444
105 | -0.023008 | -0.0057681 | 0.023008 | 0.0057681 | 2.0337e-07 | 7.487e-08 | 0.034973 | 0.034973 | 0.034973 | 0.97895 | -0.14752 | 0.97896 | -0.14745 | 12.9529
106 | -0.024628 | -0.0061741 | 0.024636 | 0.0061771 | 7.8752e-06 | 2.9157e-06 | 0.037435 | 0.037435 | 0.037435 | 0.97896 | -0.14745 | 0.97929 | -0.14514 | 13.8648
107 | 0.052559 | 0.013192 | -0.052515 | -0.013175 | 4.4138e-05 | 1.6836e-05 | 0.079758 | 0.079758 | 0.079758 | 0.98065 | -0.1354 | 0.9798 | -0.14145 | 29.5401
108 | -0.00086053 | -0.00021435 | 0.00086058 | 0.00021381 | 4.5882e-08 | -5.4057e-07 | 0.0012973 | 0.0012971 | 0.0012973 | 0.98672 | -0.092989 | 0.98678 | -0.092598 | 0.48046
109 | -0.0016764 | -0.00041826 | 0.0016765 | 0.00041791 | 1.2564e-07 | -3.5446e-07 | 0.0025272 | 0.0025271 | 0.0025272 | 0.98678 | -0.092598 | 0.98685 | -0.092051 | 0.936
110 | -0.0020103 | -0.00050157 | 0.0020111 | 0.00050005 | 8.201e-07 | -1.5143e-06 | 0.0030304 | 0.0030297 | 0.0030304 | 0.98685 | -0.092051 | 0.98727 | -0.089069 | 1.1224

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.15898 | 0.039953

## res_load
| p_mw | q_mvar
0 | 0.0002706 | 6.7818e-05
1 | 0.00031308 | 7.8466e-05
2 | 0.00094124 | 0.0002359
3 | 0.0035496 | 0.00088962
4 | 0.0045324 | 0.0011359
5 | 0.0014536 | 0.00036431
6 | 0.0029645 | 0.00074297
7 | 0.00058175 | 0.0001458
8 | 0.00064857 | 0.00016255
9 | 0.0013309 | 0.00033357
10 | 0.0022734 | 0.00056976
11 | 0.00040111 | 0.00010053
12 | 0.00086337 | 0.00021638
13 | 0.00043841 | 0.00010988
14 | 0.0010392 | 0.00026044
15 | 0.00092435 | 0.00023166
16 | 0.00063358 | 0.00015879
17 | 0.0007399 | 0.00018544
18 | 0.00063317 | 0.00015869
19 | 0.0022581 | 0.00056593
20 | 0.0029429 | 0.00073757
21 | 0.00092956 | 0.00023297
22 | 0.00038627 | 9.6808e-05
23 | 0.00038627 | 9.6808e-05
24 | 0.0014056 | 0.00035228
25 | 0.00086325 | 0.00021635
26 | 0.0047852 | 0.0011993
27 | 0.00058126 | 0.00014568
28 | 0.00065136 | 0.00016325
29 | 0.00041703 | 0.00010452
30 | 0.0013872 | 0.00034767
31 | 0.00038914 | 9.7526e-05
32 | 0.0032227 | 0.00080768
33 | 0.0051658 | 0.0012947
34 | 0.00077854 | 0.00019512
35 | 0.0011588 | 0.00029043
36 | 0.0027386 | 0.00068635
37 | 0.0025271 | 0.00063334
38 | 0.00038959 | 9.7639e-05
39 | 0.0043823 | 0.0010983
40 | 0.00051798 | 0.00012982
41 | 0.0015616 | 0.00039137
42 | 0.00063009 | 0.00015792
43 | 0.0016654 | 0.00041739
44 | 0.0020491 | 0.00051355
45 | 0.002719 | 0.00068145
46 | 0.0017728 | 0.00044432
47 | 0.0038582 | 0.00096696
48 | 0.0013283 | 0.00033289
49 | 0.0024015 | 0.00060187
50 | 0.0013291 | 0.0003331
51 | 0.0013011 | 0.00032609
52 | 0.00067659 | 0.00016957
53 | 0.0013006 | 0.00032597
54 | 0.00018748 | 4.6988e-05
55 | 0.00018748 | 4.6988e-05
56 | 0.00047971 | 0.00012023
57 | 0.0020716 | 0.00051918
58 | 0.0050363 | 0.0012622
59 | 0.0065549 | 0.0016428
60 | 0.0015807 | 0.00039616
61 | 0.0013235 | 0.00033171
62 | 0.0016599 | 0.000416
63 | 0.0011359 | 0.00028469
64 | 0.001016 | 0.00025464
65 | 0.0013604 | 0.00034095
66 | 0.0022345 | 0.00056003
67 | 0.0030166 | 0.00075603
68 | 0.0022927 | 0.00057461
69 | 0.002799 | 0.00070149
70 | 0.0017023 | 0.00042663
71 | 0.001657 | 0.00041528
72 | 0.001582 | 0.00039649
73 | 0.00097586 | 0.00024457
74 | 0.0020404 | 0.00051137
75 | 0.00030083 | 7.5394e-05
76 | 0.0058677 | 0.0014706
77 | 0.00078251 | 0.00019611
78 | 0.0030675 | 0.00076878
79 | 0.0017394 | 0.00043593
80 | 0.00087527 | 0.00021936
81 | 0.0021632 | 0.00054215
82 | 0.004884 | 0.0012241
83 | 0.00080581 | 0.00020196
84 | 0.00086239 | 0.00021613
85 | 0.00082409 | 0.00020654
86 | 0.00162 | 0.000406
87 | 0.00077917 | 0.00019528
88 | 0.001728 | 0.00043309
89 | 0.0009597 | 0.00024052
90 | 0.0005597 | 0.00014027
91 | 0.00081578 | 0.00020445
92 | 0.0003338 | 8.3658e-05
93 | 0.00040883 | 0.00010246

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1