## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1030-4_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1030-4_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1030-4_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1030-4_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1030-4_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1030-4_0_2_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_1030-4_0_2_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_1030-4_0_2_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1030-4_0_2_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1030-4_0_2_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1030-4_0_2_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1030-4_0_2_node_57 | 0.4 | n |  | TRUE
12 | bus_LV_1030-4_0_2_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_1030-4_0_2_node_25 | 0.4 | n |  | TRUE
14 | bus_LV_1030-4_0_2_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_1030-4_0_2_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_1030-4_0_2_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_1030-4_0_2_node_29 | 0.4 | n |  | TRUE
18 | bus_LV_1030-4_0_2_node_56 | 0.4 | n |  | TRUE
19 | bus_LV_1030-4_0_2_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1030-4_0_2_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_1030-4_0_2_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_1030-4_0_2_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_1030-4_0_2_node_54 | 0.4 | n |  | TRUE
24 | bus_LV_1030-4_0_2_node_55 | 0.4 | n |  | TRUE
25 | bus_LV_1030-4_0_2_node_52 | 0.4 | n |  | TRUE
26 | bus_LV_1030-4_0_2_node_46 | 0.4 | n |  | TRUE
27 | bus_LV_1030-4_0_2_node_47 | 0.4 | n |  | TRUE
28 | bus_LV_1030-4_0_2_node_49 | 0.4 | n |  | TRUE
29 | bus_LV_1030-4_0_2_node_50 | 0.4 | n |  | TRUE
30 | bus_LV_1030-4_0_2_node_53 | 0.4 | n |  | TRUE
31 | bus_MV_0_node_7 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1030-4_0_2_load_0 | 0 | 0.0011625 | 0.00029136 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1030-4_0_2_load_2 | 2 | 0.00034893 | 8.7449e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1030-4_0_2_load_15 | 5 | 0.0015017 | 0.00037635 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1030-4_0_2_load_12 | 6 | 0.00096004 | 0.00024061 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1030-4_0_2_load_5 | 7 | 0.0015527 | 0.00038915 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1030-4_0_2_load_6 | 8 | 0.0011554 | 0.00028958 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1030-4_0_2_load_8 | 10 | 0.00090473 | 0.00022675 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1030-4_0_2_load_25 | 13 | 0.0040639 | 0.0010185 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1030-4_0_2_load_26 | 14 | 0.0010494 | 0.00026301 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1030-4_0_2_load_27 | 15 | 0.0041776 | 0.001047 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1030-4_0_2_load_28 | 16 | 0.0017796 | 0.00044601 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1030-4_0_2_load_56 | 18 | 0.003542 | 0.00088771 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1030-4_0_2_load_13 | 19 | 0.00050065 | 0.00012547 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1030-4_0_2_load_9 | 20 | 0.00035682 | 8.9428e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1030-4_0_2_load_10 | 21 | 0.0023133 | 0.00057976 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1030-4_0_2_load_55 | 24 | 0.00099476 | 0.00024931 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1030-4_0_2_load_52 | 25 | 0.0014834 | 0.00037178 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1030-4_0_2_load_46 | 26 | 0.0010384 | 0.00026026 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1030-4_0_2_load_47 | 27 | 0.00038114 | 9.5524e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1030-4_0_2_load_50 | 29 | 0.00020724 | 5.194e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1030-4_0_2_load_53 | 30 | 0.00028597 | 7.1671e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1030-4_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.041245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1030-4_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.040253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1030-4_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.23115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1030-4_0_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.017925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1030-4_0_2_line_4 | NAYY 4x150 SE | 4 | 5 | 0.19984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1030-4_0_2_line_5 | NAYY 4x150 SE | 5 | 6 | 0.038359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1030-4_0_2_line_6 | NAYY 4x150 SE | 6 | 22 | 0.15232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1030-4_0_2_line_7 | NAYY 4x150 SE | 7 | 8 | 0.04899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1030-4_0_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.21292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1030-4_0_2_line_9 | NAYY 4x150 SE | 8 | 10 | 0.058323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1030-4_0_2_line_10 | NAYY 4x150 SE | 9 | 11 | 0.46715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1030-4_0_2_line_11 | NAYY 4x150 SE | 10 | 12 | 0.091644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1030-4_0_2_line_12 | NAYY 4x150 SE | 11 | 18 | 0.024991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1030-4_0_2_line_13 | NAYY 4x150 SE | 12 | 19 | 0.018998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1030-4_0_2_line_14 | NAYY 4x150 SE | 13 | 14 | 0.040051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1030-4_0_2_line_15 | NAYY 4x150 SE | 13 | 15 | 0.0011175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1030-4_0_2_line_16 | NAYY 4x150 SE | 14 | 16 | 0.15271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1030-4_0_2_line_17 | NAYY 4x150 SE | 15 | 17 | 0.02072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1030-4_0_2_line_18 | NAYY 4x150 SE | 16 | 23 | 0.53987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1030-4_0_2_line_19 | NAYY 4x150 SE | 17 | 18 | 0.0070065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1030-4_0_2_line_20 | NAYY 4x150 SE | 19 | 22 | 0.078712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1030-4_0_2_line_21 | NAYY 4x150 SE | 20 | 21 | 0.060866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1030-4_0_2_line_22 | NAYY 4x150 SE | 20 | 22 | 0.12513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1030-4_0_2_line_23 | NAYY 4x150 SE | 23 | 24 | 0.024268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1030-4_0_2_line_24 | NAYY 4x150 SE | 23 | 25 | 0.019354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1030-4_0_2_line_25 | NAYY 4x150 SE | 25 | 30 | 0.030076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1030-4_0_2_line_26 | NAYY 4x150 SE | 26 | 27 | 0.040371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1030-4_0_2_line_27 | NAYY 4x150 SE | 27 | 28 | 0.043746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1030-4_0_2_line_28 | NAYY 4x150 SE | 28 | 29 | 0.015137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1030-4_0_2_line_29 | NAYY 4x150 SE | 29 | 30 | 0.024235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1030-4_0_2_trafo_7 | 0.25 MVA 20/0.4 kV | 31 | 9 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2665859.1958 | 1231999.7847 | 2665857.8517 | 1232002.1714 | 2665855.3936 | 1232003.256 | 2665820.0361 | 1232008.9864
1 | 2665859.1958 | 1231999.7847 | 2665855.9765 | 1231971.8418 | 2665855.7848 | 1231959.7179
2 | 2665861.5886 | 1231729.8665 | 2665860.4663 | 1231863.2643 | 2665859.3013 | 1231868.6216 | 2665855.6455 | 1231874.5961 | 2665854.5161 | 1231879.4757 | 2665855.7848 | 1231959.7179
3 | 2665843.6259 | 1231729.1338 | 2665861.5886 | 1231729.8665
4 | 2665843.6259 | 1231729.1338 | 2665830.3847 | 1231732.1781 | 2665785.5517 | 1231739.7537 | 2665761.4598 | 1231739.9429 | 2665738.5696 | 1231736.2318 | 2665726.1013 | 1231732.4026 | 2665715.7382 | 1231727.2069 | 2665708.1593 | 1231720.8857 | 2665690.5286 | 1231702.4454 | 2665679.9766 | 1231693.0894 | 2665663.642 | 1231683.4471 | 2665663.2564 | 1231683.2878
5 | 2665663.2564 | 1231683.2878 | 2665633.2006 | 1231670.8695 | 2665627.5538 | 1231669.3838
6 | 2665478.0913 | 1231641.685 | 2665491.5271 | 1231641.5995 | 2665604.793 | 1231663.3955 | 2665627.5538 | 1231669.3838
7 | 2665240.7723 | 1231624.8375 | 2665284.1597 | 1231647.5881
8 | 2665043.3187 | 1231546.6851 | 2665054.0182 | 1231547.5138 | 2665196.4121 | 1231608.1573 | 2665237.5141 | 1231623.129 | 2665240.7723 | 1231624.8375
9 | 2665335.8121 | 1231674.6726 | 2665284.1597 | 1231647.5881
10 | 2665043.3187 | 1231546.6851 | 2664576.2198 | 1231539.9685
11 | 2665417.7527 | 1231715.603 | 2665395.4202 | 1231705.9288 | 2665335.8121 | 1231674.6726
12 | 2664576.2198 | 1231539.9685 | 2664572.0722 | 1231542.5252 | 2664557.0528 | 1231555.911
13 | 2665417.7527 | 1231715.603 | 2665427.9763 | 1231699.5903
14 | 2664537.9669 | 1231577.4518 | 2664516.9406 | 1231603.0666 | 2664512.6356 | 1231608.4735
15 | 2664537.9669 | 1231577.4518 | 2664538.6759 | 1231576.588
16 | 2664512.6356 | 1231608.4735 | 2664507.1897 | 1231615.3134 | 2664501.4459 | 1231628.1817 | 2664497.1559 | 1231649.4492 | 2664490.0308 | 1231673.7657 | 2664448.4713 | 1231745.4295
17 | 2664551.8222 | 1231560.5728 | 2664538.6759 | 1231576.588
18 | 2664872.1805 | 1232079.989 | 2664448.4713 | 1231745.4295
19 | 2664551.8222 | 1231560.5728 | 2664557.0528 | 1231555.911
20 | 2665478.0913 | 1231641.685 | 2665465.9981 | 1231646.3994 | 2665458.751 | 1231652.5459 | 2665452.1599 | 1231661.7127 | 2665427.9763 | 1231699.5903
21 | 2665565.3147 | 1231554.0444 | 2665581.5937 | 1231538.7354 | 2665591.6031 | 1231523.1799 | 2665600.2089 | 1231509.9106 | 2665602.2548 | 1231506.2361
22 | 2665478.0913 | 1231641.685 | 2665480.7826 | 1231632.4974 | 2665488.2201 | 1231622.8174 | 2665508.3774 | 1231603.8046 | 2665547.8684 | 1231570.4511 | 2665565.3147 | 1231554.0444
23 | 2664872.1805 | 1232079.989 | 2664863.1014 | 1232092.4426 | 2664861.0616 | 1232101.0603
24 | 2664872.1805 | 1232079.989 | 2664885.1381 | 1232083.377 | 2664889.5031 | 1232087.436
25 | 2664889.5031 | 1232087.436 | 2664905.8508 | 1232102.638 | 2664907.7983 | 1232110.1419
26 | 2664964.7511 | 1232138.7812 | 2664935.9118 | 1232150.6422 | 2664926.7956 | 1232151.7875
27 | 2664884.8207 | 1232141.5786 | 2664919.7906 | 1232152.6675 | 2664926.7956 | 1232151.7875
28 | 2664884.8207 | 1232141.5786 | 2664895.2434 | 1232130.6011
29 | 2664907.7983 | 1232110.1419 | 2664907.7983 | 1232110.1419 | 2664900.3258 | 1232125.2481 | 2664895.2434 | 1232130.6011

## bus_geodata
| x | y | coords
0 | 2665820.0361 | 1232008.9864
1 | 2665859.1958 | 1231999.7847
2 | 2665855.7848 | 1231959.7179
3 | 2665861.5886 | 1231729.8665
4 | 2665843.6259 | 1231729.1338
5 | 2665663.2564 | 1231683.2878
6 | 2665627.5538 | 1231669.3838
7 | 2665240.7723 | 1231624.8375
8 | 2665284.1597 | 1231647.5881
9 | 2665043.3187 | 1231546.6851
10 | 2665335.8121 | 1231674.6726
11 | 2664576.2198 | 1231539.9685
12 | 2665417.7527 | 1231715.603
13 | 2664537.9669 | 1231577.4518
14 | 2664512.6356 | 1231608.4735
15 | 2664538.6759 | 1231576.588
16 | 2664448.4713 | 1231745.4295
17 | 2664551.8222 | 1231560.5728
18 | 2664557.0528 | 1231555.911
19 | 2665427.9763 | 1231699.5903
20 | 2665565.3147 | 1231554.0444
21 | 2665602.2548 | 1231506.2361
22 | 2665478.0913 | 1231641.685
23 | 2664872.1805 | 1232079.989
24 | 2664861.0616 | 1232101.0603
25 | 2664889.5031 | 1232087.436
26 | 2664964.7511 | 1232138.7812
27 | 2664926.7956 | 1232151.7875
28 | 2664884.8207 | 1232141.5786
29 | 2664895.2434 | 1232130.6011
30 | 2664907.7983 | 1232110.1419
31 | 2665043.3187 | 1231546.6851

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99137 | -0.061413 | 0.0011625 | 0.00029136
1 | 0.99143 | -0.060925 | 0 | 0
2 | 0.9915 | -0.060448 | 0.00034893 | 8.7449e-05
3 | 0.992 | -0.056858 | 0 | 0
4 | 0.99204 | -0.056578 | 0 | 0
5 | 0.99248 | -0.053432 | 0.0015017 | 0.00037635
6 | 0.99264 | -0.05224 | 0.00096004 | 0.00024061
7 | 0.99672 | -0.023204 | 0.0015527 | 0.00038915
8 | 0.99607 | -0.027793 | 0.0011554 | 0.00028958
9 | 1 | 0 | -0.030916 | -0.0075586
10 | 0.9954 | -0.032582 | 0.00090473 | 0.00022675
11 | 0.98715 | -0.090298 | 0 | 0
12 | 0.99446 | -0.039276 | 0 | 0
13 | 0.98582 | -0.099744 | 0.0040639 | 0.0010185
14 | 0.9854 | -0.10275 | 0.0010494 | 0.00026301
15 | 0.98584 | -0.099613 | 0.0041776 | 0.001047
16 | 0.98404 | -0.11257 | 0.0017796 | 0.00044601
17 | 0.98631 | -0.096306 | 0 | 0
18 | 0.98646 | -0.095189 | 0.003542 | 0.00088771
19 | 0.99426 | -0.040665 | 0.00050065 | 0.00012547
20 | 0.99303 | -0.049415 | 0.00035682 | 8.9428e-05
21 | 0.99283 | -0.050842 | 0.0023133 | 0.00057976
22 | 0.99351 | -0.04602 | 0 | 0
23 | 0.98059 | -0.13733 | 0 | 0
24 | 0.98056 | -0.13758 | 0.00099476 | 0.00024931
25 | 0.9805 | -0.13802 | 0.0014834 | 0.00037178
26 | 0.98017 | -0.14034 | 0.0010384 | 0.00026026
27 | 0.98023 | -0.1399 | 0.00038114 | 9.5524e-05
28 | 0.98032 | -0.13926 | 0 | 0
29 | 0.98035 | -0.13903 | 0.00020724 | 5.194e-05
30 | 0.98041 | -0.13862 | 0.00028597 | 7.1671e-05
31 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0011625 | -0.00029136 | 0.0011626 | 0.00029086 | 7.8354e-08 | -5.017e-07 | 0.0017449 | 0.0017447 | 0.0017449 | 0.99137 | -0.061413 | 0.99143 | -0.060925 | 0.64627
1 | -0.0011626 | -0.00029086 | 0.0011627 | 0.00029037 | 7.6454e-08 | -4.8972e-07 | 0.0017447 | 0.0017446 | 0.0017447 | 0.99143 | -0.060925 | 0.9915 | -0.060448 | 0.6462
2 | -0.0015116 | -0.00037782 | 0.0015124 | 0.00037512 | 7.4173e-07 | -2.6974e-06 | 0.0022682 | 0.0022672 | 0.0022682 | 0.9915 | -0.060448 | 0.992 | -0.056858 | 0.84008
3 | -0.0015124 | -0.00037512 | 0.0015124 | 0.00037491 | 5.749e-08 | -2.0932e-07 | 0.0022672 | 0.0022671 | 0.0022672 | 0.992 | -0.056858 | 0.99204 | -0.056578 | 0.83969
4 | -0.0015124 | -0.00037491 | 0.0015131 | 0.00037257 | 6.4067e-07 | -2.3349e-06 | 0.0022671 | 0.0022662 | 0.0022671 | 0.99204 | -0.056578 | 0.99248 | -0.053432 | 0.83966
5 | -0.0030147 | -0.00074893 | 0.0030152 | 0.00074862 | 4.8849e-07 | -3.079e-07 | 0.0045176 | 0.0045174 | 0.0045176 | 0.99248 | -0.053432 | 0.99264 | -0.05224 | 1.6732
6 | -0.0039752 | -0.00098923 | 0.0039786 | 0.00098855 | 3.3719e-06 | -6.7382e-07 | 0.0059566 | 0.0059559 | 0.0059566 | 0.99264 | -0.05224 | 0.99351 | -0.04602 | 2.2061
7 | 0.0092351 | 0.0023031 | -0.0092293 | -0.0023015 | 5.8077e-06 | 1.5956e-06 | 0.013783 | 0.013783 | 0.013783 | 0.99672 | -0.023204 | 0.99607 | -0.027793 | 5.105
8 | -0.010788 | -0.0026923 | 0.010822 | 0.0027027 | 3.4443e-05 | 1.0463e-05 | 0.016101 | 0.0161 | 0.016101 | 0.99672 | -0.023204 | 1 | 0 | 5.9635
9 | 0.0080739 | 0.0020119 | -0.0080686 | -0.0020107 | 5.291e-06 | 1.2764e-06 | 0.012057 | 0.012058 | 0.012058 | 0.99607 | -0.027793 | 0.9954 | -0.032582 | 4.4658
10 | 0.019294 | 0.0048558 | -0.019053 | -0.0047694 | 0.0002404 | 8.641e-05 | 0.028716 | 0.028718 | 0.028718 | 1 | 0 | 0.98715 | -0.090298 | 10.6365
11 | 0.0071638 | 0.0017839 | -0.0071573 | -0.0017826 | 6.5538e-06 | 1.3306e-06 | 0.010705 | 0.010706 | 0.010706 | 0.9954 | -0.032582 | 0.99446 | -0.039276 | 3.965
12 | 0.019053 | 0.0047694 | -0.01904 | -0.0047647 | 1.2861e-05 | 4.6275e-06 | 0.028718 | 0.028719 | 0.028719 | 0.98715 | -0.090298 | 0.98646 | -0.095189 | 10.6365
13 | 0.0071573 | 0.0017826 | -0.0071559 | -0.0017823 | 1.3587e-06 | 2.7613e-07 | 0.010706 | 0.010706 | 0.010706 | 0.99446 | -0.039276 | 0.99426 | -0.040665 | 3.9651
14 | 0.0072471 | 0.0018082 | -0.0072441 | -0.0018075 | 2.989e-06 | 6.3918e-07 | 0.010936 | 0.010936 | 0.010936 | 0.98582 | -0.099744 | 0.9854 | -0.10275 | 4.0504
15 | -0.011311 | -0.0028267 | 0.011311 | 0.0028267 | 2.0318e-07 | 6.39e-08 | 0.01707 | 0.01707 | 0.01707 | 0.98582 | -0.099744 | 0.98584 | -0.099613 | 6.3223
16 | 0.0061947 | 0.0015445 | -0.0061864 | -0.0015432 | 8.334e-06 | 1.2627e-06 | 0.0093515 | 0.0093522 | 0.0093522 | 0.9854 | -0.10275 | 0.98404 | -0.11257 | 3.4638
17 | -0.015489 | -0.0038737 | 0.015496 | 0.0038762 | 7.0648e-06 | 2.4529e-06 | 0.023376 | 0.023376 | 0.023376 | 0.98584 | -0.099613 | 0.98631 | -0.096306 | 8.6577
18 | 0.0044067 | 0.0010972 | -0.0043918 | -0.0010983 | 1.4953e-05 | -1.0833e-06 | 0.0066611 | 0.0066636 | 0.0066636 | 0.98404 | -0.11257 | 0.98059 | -0.13733 | 2.468
19 | -0.015496 | -0.0038762 | 0.015498 | 0.003877 | 2.389e-06 | 8.2941e-07 | 0.023376 | 0.023376 | 0.023376 | 0.98631 | -0.096306 | 0.98646 | -0.095189 | 8.6577
20 | 0.0066553 | 0.0016568 | -0.0066504 | -0.001656 | 4.8691e-06 | 8.5267e-07 | 0.0099564 | 0.0099568 | 0.0099568 | 0.99426 | -0.040665 | 0.99351 | -0.04602 | 3.6877
21 | 0.0023137 | 0.00057915 | -0.0023133 | -0.00057976 | 4.565e-07 | -6.1169e-07 | 0.0034668 | 0.003467 | 0.003467 | 0.99303 | -0.049415 | 0.99283 | -0.050842 | 1.2841
22 | -0.0026706 | -0.00066858 | 0.0026718 | 0.00066744 | 1.25e-06 | -1.1388e-06 | 0.0040015 | 0.0040009 | 0.0040015 | 0.99303 | -0.049415 | 0.99351 | -0.04602 | 1.482
23 | 0.00099479 | 0.00024902 | -0.00099476 | -0.00024931 | 3.4505e-08 | -2.9285e-07 | 0.0015095 | 0.0015096 | 0.0015096 | 0.98059 | -0.13733 | 0.98056 | -0.13758 | 0.5591
24 | 0.003397 | 0.0008493 | -0.0033967 | -0.00084942 | 3.2082e-07 | -1.2073e-07 | 0.0051541 | 0.0051542 | 0.0051542 | 0.98059 | -0.13733 | 0.9805 | -0.13802 | 1.909
25 | 0.0019133 | 0.00047764 | -0.0019131 | -0.00047796 | 1.5816e-07 | -3.1847e-07 | 0.0029029 | 0.0029031 | 0.0029031 | 0.9805 | -0.13802 | 0.98041 | -0.13862 | 1.0752
26 | -0.0010384 | -0.00026026 | 0.0010385 | 0.00025977 | 6.26e-08 | -4.848e-07 | 0.0015765 | 0.0015763 | 0.0015765 | 0.98017 | -0.14034 | 0.98023 | -0.1399 | 0.58388
27 | -0.0014196 | -0.0003553 | 0.0014198 | 0.00035479 | 1.2674e-07 | -5.0275e-07 | 0.0021549 | 0.0021547 | 0.0021549 | 0.98023 | -0.1399 | 0.98032 | -0.13926 | 0.7981
28 | -0.0014198 | -0.00035479 | 0.0014198 | 0.00035462 | 4.3851e-08 | -1.7399e-07 | 0.0021547 | 0.0021546 | 0.0021547 | 0.98032 | -0.13926 | 0.98035 | -0.13903 | 0.79803
29 | -0.0016271 | -0.00040656 | 0.0016271 | 0.00040629 | 9.2194e-08 | -2.7013e-07 | 0.0024692 | 0.0024691 | 0.0024692 | 0.98035 | -0.13903 | 0.98041 | -0.13862 | 0.91451

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.030916 | 0.0075586

## res_load
| p_mw | q_mvar
0 | 0.0011625 | 0.00029136
1 | 0.00034893 | 8.7449e-05
2 | 0.0015017 | 0.00037635
3 | 0.00096004 | 0.00024061
4 | 0.0015527 | 0.00038915
5 | 0.0011554 | 0.00028958
6 | 0.00090473 | 0.00022675
7 | 0.0040639 | 0.0010185
8 | 0.0010494 | 0.00026301
9 | 0.0041776 | 0.001047
10 | 0.0017796 | 0.00044601
11 | 0.003542 | 0.00088771
12 | 0.00050065 | 0.00012547
13 | 0.00035682 | 8.9428e-05
14 | 0.0023133 | 0.00057976
15 | 0.00099476 | 0.00024931
16 | 0.0014834 | 0.00037178
17 | 0.0010384 | 0.00026026
18 | 0.00038114 | 9.5524e-05
19 | 0.00020724 | 5.194e-05
20 | 0.00028597 | 7.1671e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1