## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1031-11_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1031-11_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1031-11_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1031-11_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1031-11_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1031-11_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1031-11_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1031-11_0_4_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_1031-11_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1031-11_0_4_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_1031-11_0_4_node_33 | 0.4 | n |  | TRUE
11 | bus_LV_1031-11_0_4_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_1031-11_0_4_node_32 | 0.4 | n |  | TRUE
13 | bus_LV_1031-11_0_4_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1031-11_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1031-11_0_4_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_1031-11_0_4_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_1031-11_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1031-11_0_4_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_1031-11_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1031-11_0_4_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1031-11_0_4_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1031-11_0_4_node_30 | 0.4 | n |  | TRUE
23 | bus_LV_1031-11_0_4_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_1031-11_0_4_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_1031-11_0_4_node_31 | 0.4 | n |  | TRUE
26 | bus_LV_1031-11_0_4_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1031-11_0_4_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1031-11_0_4_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_1031-11_0_4_node_29 | 0.4 | n |  | TRUE
30 | bus_MV_353_1_node_297 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1031-11_0_4_load_0 | 0 | 0.00192 | 0.00048119 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1031-11_0_4_load_1 | 1 | 0.0026845 | 0.00067281 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1031-11_0_4_load_2 | 2 | 0.0051641 | 0.0012942 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1031-11_0_4_load_3 | 3 | 0.0064626 | 0.0016197 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1031-11_0_4_load_4 | 4 | 0.0027846 | 0.00069788 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1031-11_0_4_load_7 | 8 | 0.0063273 | 0.0015858 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1031-11_0_4_load_33 | 10 | 0.073557 | 0.018435 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1031-11_0_4_load_32 | 12 | 0.0062267 | 0.0015605 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1031-11_0_4_load_28 | 15 | 0.012229 | 0.003065 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1031-11_0_4_load_27 | 16 | 0.0077641 | 0.0019459 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1031-11_0_4_load_20 | 20 | 0.0069053 | 0.0017306 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1031-11_0_4_load_17 | 21 | 0.0048032 | 0.0012038 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1031-11_0_4_load_30 | 22 | 0.0035019 | 0.00087766 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1031-11_0_4_load_26 | 23 | 0.012985 | 0.0032543 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1031-11_0_4_load_25 | 24 | 0.0077187 | 0.0019345 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1031-11_0_4_load_31 | 25 | 0.02003 | 0.0050199 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1031-11_0_4_load_18 | 26 | 0.013911 | 0.0034865 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1031-11_0_4_load_29 | 29 | 0.0041189 | 0.0010323 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1031-11_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0034154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1031-11_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.012366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1031-11_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.024056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1031-11_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.014125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1031-11_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.017781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1031-11_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.00502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1031-11_0_4_line_6 | NAYY 4x150 SE | 5 | 7 | 0.018266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1031-11_0_4_line_7 | NAYY 4x150 SE | 6 | 8 | 0.026224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1031-11_0_4_line_8 | NAYY 4x150 SE | 7 | 22 | 0.016011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1031-11_0_4_line_9 | NAYY 4x150 SE | 7 | 23 | 0.034243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1031-11_0_4_line_10 | NAYY 4x150 SE | 8 | 16 | 0.005954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1031-11_0_4_line_11 | NAYY 4x150 SE | 9 | 10 | 0.019737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1031-11_0_4_line_12 | NAYY 4x150 SE | 9 | 11 | 0.024767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1031-11_0_4_line_13 | NAYY 4x150 SE | 11 | 12 | 0.005258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1031-11_0_4_line_14 | NAYY 4x150 SE | 11 | 13 | 0.011944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1031-11_0_4_line_15 | NAYY 4x150 SE | 13 | 24 | 0.054852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1031-11_0_4_line_16 | NAYY 4x150 SE | 14 | 15 | 0.030075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1031-11_0_4_line_17 | NAYY 4x150 SE | 14 | 16 | 0.018237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1031-11_0_4_line_18 | NAYY 4x150 SE | 15 | 17 | 0.019844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1031-11_0_4_line_19 | NAYY 4x150 SE | 17 | 18 | 0.018055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1031-11_0_4_line_20 | NAYY 4x150 SE | 18 | 25 | 0.014568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1031-11_0_4_line_21 | NAYY 4x150 SE | 19 | 20 | 0.019722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1031-11_0_4_line_22 | NAYY 4x150 SE | 19 | 21 | 0.024405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1031-11_0_4_line_23 | NAYY 4x150 SE | 21 | 26 | 0.026879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1031-11_0_4_line_24 | NAYY 4x150 SE | 23 | 27 | 0.020199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1031-11_0_4_line_25 | NAYY 4x150 SE | 24 | 27 | 0.039986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1031-11_0_4_line_26 | NAYY 4x150 SE | 26 | 27 | 0.017703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1031-11_0_4_line_27 | NAYY 4x150 SE | 27 | 28 | 0.00711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1031-11_0_4_line_28 | NAYY 4x150 SE | 28 | 29 | 0.0043836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1031-11_0_4_trafo_19 | 0.25 MVA 20/0.4 kV | 30 | 27 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2664638.1563 | 1224520.101 | 2664638.7007 | 1224516.7293
1 | 2664636.1855 | 1224532.3087 | 2664638.1563 | 1224520.101
2 | 2664642.5348 | 1224492.9803 | 2664638.7007 | 1224516.7293
3 | 2664636.1855 | 1224532.3087 | 2664633.9343 | 1224546.2531
4 | 2664645.3687 | 1224475.4265 | 2664642.5348 | 1224492.9803
5 | 2664633.1342 | 1224551.2089 | 2664633.9343 | 1224546.2531
6 | 2664638.6752 | 1224465.503 | 2664640.934 | 1224467.6623 | 2664647.0113 | 1224466.6054 | 2664645.3687 | 1224475.4265
7 | 2664633.1342 | 1224551.2089 | 2664628.3409 | 1224551.3348 | 2664608.7054 | 1224559.9164
8 | 2664638.6752 | 1224465.503 | 2664625.6382 | 1224474.7975
9 | 2664638.6752 | 1224465.503 | 2664633.677 | 1224460.7457 | 2664606.8407 | 1224455.5051
10 | 2664608.7054 | 1224559.9164 | 2664603.2497 | 1224562.3008
11 | 2664578.4982 | 1224358.9597 | 2664574.3233 | 1224378.249
12 | 2664578.4982 | 1224358.9597 | 2664579.7989 | 1224352.9922 | 2664597.9975 | 1224357.1144
13 | 2664597.9975 | 1224357.1144 | 2664597.2662 | 1224362.3209
14 | 2664597.9975 | 1224357.1144 | 2664609.7238 | 1224359.5543
15 | 2664609.7238 | 1224359.5543 | 2664603.323 | 1224385.5126 | 2664596.5906 | 1224412.8108
16 | 2664586.5392 | 1224569.604 | 2664573.8066 | 1224542.3569
17 | 2664586.5392 | 1224569.604 | 2664603.2497 | 1224562.3008
18 | 2664565.4056 | 1224524.3792 | 2664573.8066 | 1224542.3569
19 | 2664580.0185 | 1224513.7197 | 2664576.5942 | 1224516.2509 | 2664566.4756 | 1224523.6014 | 2664565.4056 | 1224524.3792
20 | 2664580.0185 | 1224513.7197 | 2664583.1154 | 1224511.3184 | 2664591.5298 | 1224504.7914
21 | 2664522.922 | 1224456.5975 | 2664535.0544 | 1224472.1461
22 | 2664522.922 | 1224456.5975 | 2664539.8853 | 1224443.8509 | 2664543.0293 | 1224444.3701
23 | 2664543.0293 | 1224444.3701 | 2664569.5494 | 1224448.7494
24 | 2664587.0159 | 1224451.6336 | 2664606.8407 | 1224455.5051
25 | 2664587.0159 | 1224451.6336 | 2664596.5906 | 1224412.8108
26 | 2664587.0159 | 1224451.6336 | 2664569.5494 | 1224448.7494
27 | 2664587.0159 | 1224451.6336 | 2664585.3864 | 1224458.5537
28 | 2664585.3864 | 1224458.5537 | 2664584.3815 | 1224462.8206

## bus_geodata
| x | y | coords
0 | 2664638.1563 | 1224520.101
1 | 2664638.7007 | 1224516.7293
2 | 2664636.1855 | 1224532.3087
3 | 2664642.5348 | 1224492.9803
4 | 2664633.9343 | 1224546.2531
5 | 2664645.3687 | 1224475.4265
6 | 2664633.1342 | 1224551.2089
7 | 2664638.6752 | 1224465.5031
8 | 2664608.7054 | 1224559.9164
9 | 2664578.4982 | 1224358.9597
10 | 2664574.3233 | 1224378.249
11 | 2664597.9975 | 1224357.1144
12 | 2664597.2662 | 1224362.3209
13 | 2664609.7238 | 1224359.5543
14 | 2664586.5392 | 1224569.604
15 | 2664573.8066 | 1224542.3569
16 | 2664603.2497 | 1224562.3008
17 | 2664565.4056 | 1224524.3792
18 | 2664580.0185 | 1224513.7197
19 | 2664522.922 | 1224456.5975
20 | 2664535.0544 | 1224472.1461
21 | 2664543.0293 | 1224444.3701
22 | 2664625.6382 | 1224474.7975
23 | 2664606.8407 | 1224455.5051
24 | 2664596.5906 | 1224412.8108
25 | 2664591.5298 | 1224504.7914
26 | 2664569.5494 | 1224448.7494
27 | 2664587.0159 | 1224451.6336
28 | 2664585.3864 | 1224458.5537
29 | 2664584.3815 | 1224462.8206
30 | 2664585.3864 | 1224458.5537

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98845 | -0.080568 | 0.00192 | 0.00048119
1 | 0.98873 | -0.078607 | 0.0026845 | 0.00067281
2 | 0.98747 | -0.087436 | 0.0051641 | 0.0012942
3 | 0.99078 | -0.064166 | 0.0064626 | 0.0016197
4 | 0.98647 | -0.094549 | 0.0027846 | 0.00069788
5 | 0.99247 | -0.052366 | 0 | 0
6 | 0.98613 | -0.096937 | 0 | 0
7 | 0.9942 | -0.040285 | 0 | 0
8 | 0.98436 | -0.10944 | 0.0063273 | 0.0015858
9 | 0.98456 | -0.10797 | 0 | 0
10 | 0.98245 | -0.12295 | 0.073557 | 0.018435
11 | 0.9872 | -0.089259 | 0 | 0
12 | 0.98715 | -0.089595 | 0.0062267 | 0.0015605
13 | 0.98858 | -0.079514 | 0 | 0
14 | 0.98316 | -0.11796 | 0 | 0
15 | 0.98175 | -0.128 | 0.012229 | 0.003065
16 | 0.98402 | -0.11189 | 0.0077641 | 0.0019459
17 | 0.98118 | -0.13212 | 0 | 0
18 | 0.98065 | -0.13587 | 0 | 0
19 | 0.99866 | -0.0093656 | 0 | 0
20 | 0.99847 | -0.010729 | 0.0069053 | 0.0017306
21 | 0.9989 | -0.0076788 | 0.0048032 | 0.0012038
22 | 0.99411 | -0.040852 | 0.0035019 | 0.00087766
23 | 0.99761 | -0.016546 | 0.012985 | 0.0032543
24 | 0.99493 | -0.035103 | 0.0077187 | 0.0019345
25 | 0.98023 | -0.1389 | 0.02003 | 0.0050199
26 | 0.99935 | -0.0045309 | 0.013911 | 0.0034865
27 | 1 | 0 | -0.2024 | -0.050855
28 | 0.99996 | -0.00029235 | 0 | 0
29 | 0.99993 | -0.00047258 | 0.0041189 | 0.0010323
30 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.056532 | -0.014208 | 0.056548 | 0.014214 | 1.5441e-05 | 5.895e-06 | 0.085119 | 0.085119 | 0.085119 | 0.98845 | -0.080568 | 0.98873 | -0.078607 | 31.5254
1 | 0.054613 | 0.013727 | -0.05456 | -0.013707 | 5.2173e-05 | 1.9908e-05 | 0.082228 | 0.082228 | 0.082228 | 0.98845 | -0.080568 | 0.98747 | -0.087436 | 30.4549
2 | -0.059232 | -0.014887 | 0.059352 | 0.014933 | 0.00011933 | 4.5586e-05 | 0.089159 | 0.089159 | 0.089159 | 0.98873 | -0.078607 | 0.99078 | -0.064166 | 33.0218
3 | 0.049396 | 0.012413 | -0.049347 | -0.012394 | 4.885e-05 | 1.8608e-05 | 0.074447 | 0.074447 | 0.074447 | 0.98747 | -0.087436 | 0.98647 | -0.094549 | 27.5728
4 | -0.065814 | -0.016552 | 0.065923 | 0.016594 | 0.00010845 | 4.1482e-05 | 0.098865 | 0.098864 | 0.098865 | 0.99078 | -0.064166 | 0.99247 | -0.052366 | 36.6165
5 | 0.046563 | 0.011696 | -0.046547 | -0.011691 | 1.5457e-05 | 5.8811e-06 | 0.070246 | 0.070246 | 0.070246 | 0.98647 | -0.094549 | 0.98613 | -0.096937 | 26.0171
6 | -0.065923 | -0.016594 | 0.066034 | 0.016636 | 0.00011141 | 4.2612e-05 | 0.098864 | 0.098864 | 0.098864 | 0.99247 | -0.052366 | 0.9942 | -0.040285 | 36.6165
7 | 0.046547 | 0.011691 | -0.046467 | -0.01166 | 8.0748e-05 | 3.0723e-05 | 0.070246 | 0.070246 | 0.070246 | 0.98613 | -0.096937 | 0.98436 | -0.10944 | 26.0172
8 | 0.0035022 | 0.00087756 | -0.0035019 | -0.00087766 | 2.745e-07 | -1.0203e-07 | 0.0052417 | 0.0052417 | 0.0052417 | 0.9942 | -0.040285 | 0.99411 | -0.040852 | 1.9414
9 | -0.069536 | -0.017514 | 0.069768 | 0.017603 | 0.00023159 | 8.8626e-05 | 0.10411 | 0.10411 | 0.10411 | 0.9942 | -0.040285 | 0.99761 | -0.016546 | 38.5578
10 | 0.040139 | 0.010074 | -0.040126 | -0.010069 | 1.3681e-05 | 5.1861e-06 | 0.060682 | 0.060682 | 0.060682 | 0.98436 | -0.10944 | 0.98402 | -0.11189 | 22.4747
11 | 0.07371 | 0.018494 | -0.073557 | -0.018435 | 0.00015286 | 5.8543e-05 | 0.11141 | 0.11141 | 0.11141 | 0.98456 | -0.10797 | 0.98245 | -0.12295 | 41.2624
12 | -0.07371 | -0.018494 | 0.073901 | 0.018567 | 0.00019182 | 7.3462e-05 | 0.11141 | 0.11141 | 0.11141 | 0.98456 | -0.10797 | 0.9872 | -0.089259 | 41.2624
13 | 0.0062269 | 0.0015606 | -0.0062267 | -0.0015605 | 2.8904e-07 | 4.3946e-08 | 0.0093859 | 0.0093859 | 0.0093859 | 0.9872 | -0.089259 | 0.98715 | -0.089595 | 3.4763
14 | -0.080128 | -0.020128 | 0.080237 | 0.020169 | 0.00010875 | 4.1674e-05 | 0.12079 | 0.12079 | 0.12079 | 0.9872 | -0.089259 | 0.98858 | -0.079514 | 44.7386
15 | -0.080237 | -0.020169 | 0.080736 | 0.020361 | 0.00049942 | 0.00019138 | 0.12079 | 0.12079 | 0.12079 | 0.98858 | -0.079514 | 0.99493 | -0.035103 | 44.7386
16 | 0.032334 | 0.0081128 | -0.032289 | -0.0080958 | 4.4951e-05 | 1.6908e-05 | 0.048941 | 0.048941 | 0.048941 | 0.98316 | -0.11796 | 0.98175 | -0.128 | 18.1264
17 | -0.032334 | -0.0081128 | 0.032361 | 0.008123 | 2.7257e-05 | 1.0252e-05 | 0.048941 | 0.048941 | 0.048941 | 0.98316 | -0.11796 | 0.98402 | -0.11189 | 18.1263
18 | 0.02006 | 0.0050309 | -0.020049 | -0.0050267 | 1.1448e-05 | 4.1522e-06 | 0.030406 | 0.030406 | 0.030406 | 0.98175 | -0.128 | 0.98118 | -0.13212 | 11.2613
19 | 0.020049 | 0.0050267 | -0.020038 | -0.005023 | 1.0416e-05 | 3.7782e-06 | 0.030406 | 0.030406 | 0.030406 | 0.98118 | -0.13212 | 0.98065 | -0.13587 | 11.2614
20 | 0.020038 | 0.005023 | -0.02003 | -0.0050199 | 8.4042e-06 | 3.0487e-06 | 0.030406 | 0.030406 | 0.030406 | 0.98065 | -0.13587 | 0.98023 | -0.1389 | 11.2614
21 | 0.0069066 | 0.0017309 | -0.0069053 | -0.0017306 | 1.3033e-06 | 2.4326e-07 | 0.010291 | 0.010291 | 0.010291 | 0.99866 | -0.0093656 | 0.99847 | -0.010729 | 3.8114
22 | -0.0069066 | -0.0017309 | 0.0069082 | 0.0017312 | 1.6127e-06 | 3.0088e-07 | 0.010291 | 0.010291 | 0.010291 | 0.99866 | -0.0093656 | 0.9989 | -0.0076788 | 3.8114
23 | -0.011711 | -0.0029349 | 0.011716 | 0.0029366 | 5.1048e-06 | 1.6113e-06 | 0.017446 | 0.017446 | 0.017446 | 0.9989 | -0.0076788 | 0.99935 | -0.0045309 | 6.4614
24 | -0.082753 | -0.020857 | 0.082945 | 0.02093 | 0.00019216 | 7.3645e-05 | 0.12347 | 0.12347 | 0.12347 | 0.99761 | -0.016546 | 1 | 0 | 45.731
25 | -0.088455 | -0.022295 | 0.088892 | 0.022463 | 0.00043698 | 0.00016755 | 0.13234 | 0.13234 | 0.13234 | 0.99493 | -0.035103 | 1 | 0 | 49.0141
26 | -0.025628 | -0.0064231 | 0.025644 | 0.006429 | 1.6085e-05 | 5.9546e-06 | 0.038159 | 0.038159 | 0.038159 | 0.99935 | -0.0045309 | 1 | 0 | 14.133
27 | 0.0041192 | 0.0010323 | -0.004119 | -0.0010323 | 1.6668e-07 | -2.9166e-08 | 0.0061294 | 0.0061294 | 0.0061294 | 1 | 0 | 0.99996 | -0.00029235 | 2.2702
28 | 0.004119 | 0.0010323 | -0.0041189 | -0.0010323 | 1.0277e-07 | -1.7978e-08 | 0.0061294 | 0.0061294 | 0.0061294 | 0.99996 | -0.00029235 | 0.99993 | -0.00047258 | 2.2702

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.2024 | 0.050855

## res_load
| p_mw | q_mvar
0 | 0.00192 | 0.00048119
1 | 0.0026845 | 0.00067281
2 | 0.0051641 | 0.0012942
3 | 0.0064626 | 0.0016197
4 | 0.0027846 | 0.00069788
5 | 0.0063273 | 0.0015858
6 | 0.073557 | 0.018435
7 | 0.0062267 | 0.0015605
8 | 0.012229 | 0.003065
9 | 0.0077641 | 0.0019459
10 | 0.0069053 | 0.0017306
11 | 0.0048032 | 0.0012038
12 | 0.0035019 | 0.00087766
13 | 0.012985 | 0.0032543
14 | 0.0077187 | 0.0019345
15 | 0.02003 | 0.0050199
16 | 0.013911 | 0.0034865
17 | 0.0041189 | 0.0010323

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1