## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1031-13_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1031-13_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1031-13_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1031-13_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1031-13_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1031-13_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1031-13_0_4_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_1031-13_0_4_node_33 | 0.4 | n |  | TRUE
8 | bus_LV_1031-13_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1031-13_0_4_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_1031-13_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1031-13_0_4_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_1031-13_0_4_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_1031-13_0_4_node_27 | 0.4 | n |  | TRUE
14 | bus_LV_1031-13_0_4_node_31 | 0.4 | n |  | TRUE
15 | bus_LV_1031-13_0_4_node_30 | 0.4 | n |  | TRUE
16 | bus_LV_1031-13_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1031-13_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1031-13_0_4_node_36 | 0.4 | n |  | TRUE
19 | bus_LV_1031-13_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1031-13_0_4_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_1031-13_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1031-13_0_4_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_1031-13_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1031-13_0_4_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_1031-13_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1031-13_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1031-13_0_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_1031-13_0_4_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_1031-13_0_4_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_1031-13_0_4_node_35 | 0.4 | n |  | TRUE
31 | bus_LV_1031-13_0_4_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_1031-13_0_4_node_32 | 0.4 | n |  | TRUE
33 | bus_MV_353_1_node_238 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1031-13_0_4_load_0 | 0 | 0.00049578 | 0.00012425 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1031-13_0_4_load_1 | 1 | 0.0010912 | 0.00027348 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1031-13_0_4_load_33 | 7 | 0.011408 | 0.0028592 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1031-13_0_4_load_6 | 8 | 0.0027169 | 0.00068092 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1031-13_0_4_load_13 | 9 | 0.016655 | 0.0041741 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1031-13_0_4_load_10 | 10 | 0.0052685 | 0.0013204 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1031-13_0_4_load_27 | 13 | 0.015938 | 0.0039944 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1031-13_0_4_load_30 | 15 | 0.0017724 | 0.00044421 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1031-13_0_4_load_36 | 18 | 0.026256 | 0.0065805 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1031-13_0_4_load_11 | 19 | 0.0016486 | 0.00041319 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1031-13_0_4_load_34 | 20 | 0.0087916 | 0.0022034 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1031-13_0_4_load_28 | 22 | 0.0021345 | 0.00053495 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1031-13_0_4_load_15 | 23 | 0.088409 | 0.022157 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1031-13_0_4_load_26 | 24 | 0.00044249 | 0.0001109 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1031-13_0_4_load_21 | 25 | 0.00031566 | 7.9112e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1031-13_0_4_load_23 | 27 | 0.00027514 | 6.8956e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1031-13_0_4_load_25 | 29 | 0.00047161 | 0.0001182 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1031-13_0_4_load_35 | 30 | 0.0041917 | 0.0010505 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1031-13_0_4_load_29 | 31 | 0.00060904 | 0.00015264 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1031-13_0_4_load_32 | 32 | 0.0036064 | 0.00090386 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1031-13_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.028834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1031-13_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.029781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1031-13_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.036395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1031-13_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.028566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1031-13_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.092822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1031-13_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.042295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1031-13_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.01998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1031-13_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.068601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1031-13_0_4_line_8 | NAYY 4x150 SE | 6 | 9 | 0.083481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1031-13_0_4_line_9 | NAYY 4x150 SE | 6 | 10 | 0.023288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1031-13_0_4_line_10 | NAYY 4x150 SE | 7 | 14 | 0.039353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1031-13_0_4_line_11 | NAYY 4x150 SE | 8 | 16 | 0.035235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1031-13_0_4_line_12 | NAYY 4x150 SE | 10 | 19 | 0.04417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1031-13_0_4_line_13 | NAYY 4x150 SE | 11 | 12 | 0.026898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1031-13_0_4_line_14 | NAYY 4x150 SE | 11 | 13 | 0.042609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1031-13_0_4_line_15 | NAYY 4x150 SE | 12 | 20 | 0.035875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1031-13_0_4_line_16 | NAYY 4x150 SE | 12 | 21 | 0.027337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1031-13_0_4_line_17 | NAYY 4x150 SE | 13 | 22 | 0.045232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1031-13_0_4_line_18 | NAYY 4x150 SE | 14 | 15 | 0.012571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1031-13_0_4_line_19 | NAYY 4x150 SE | 14 | 32 | 0.008907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1031-13_0_4_line_20 | NAYY 4x150 SE | 16 | 17 | 0.07564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1031-13_0_4_line_21 | NAYY 4x150 SE | 17 | 18 | 0.040409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1031-13_0_4_line_22 | NAYY 4x150 SE | 20 | 30 | 0.06729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1031-13_0_4_line_23 | NAYY 4x150 SE | 21 | 23 | 0.039876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1031-13_0_4_line_24 | NAYY 4x150 SE | 22 | 31 | 0.001242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_1031-13_0_4_line_25 | NAYY 4x150 SE | 23 | 24 | 0.10953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1031-13_0_4_line_26 | NAYY 4x150 SE | 24 | 28 | 0.029725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1031-13_0_4_line_27 | NAYY 4x150 SE | 25 | 26 | 0.01765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1031-13_0_4_line_28 | NAYY 4x150 SE | 26 | 27 | 0.022512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1031-13_0_4_line_29 | NAYY 4x150 SE | 27 | 28 | 0.0020469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1031-13_0_4_line_30 | NAYY 4x150 SE | 28 | 29 | 0.021824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1031-13_0_4_line_31 | NAYY 4x150 SE | 31 | 32 | 0.019464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1031-13_0_4_trafo_17 | 0.25 MVA 20/0.4 kV | 33 | 12 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2664245.4074 | 1224202.8366 | 2664236.6631 | 1224230.3129
1 | 2664254.4388 | 1224174.4583 | 2664245.4074 | 1224202.8366
2 | 2664225.6258 | 1224264.9943 | 2664236.6631 | 1224230.3129
3 | 2664254.4388 | 1224174.4583 | 2664228.2676 | 1224162.8352
4 | 2664152.9964 | 1224300.523 | 2664156.9688 | 1224298.4867 | 2664209.0553 | 1224296.1577 | 2664211.9197 | 1224293.5091 | 2664218.7228 | 1224271.5796 | 2664225.6258 | 1224264.9943
5 | 2664196.2959 | 1224162.4235 | 2664199.9343 | 1224151.3001 | 2664228.2676 | 1224162.8352
6 | 2664228.2676 | 1224162.8352 | 2664231.0985 | 1224154.8718 | 2664231.3054 | 1224143.3458
7 | 2664152.9964 | 1224300.523 | 2664148.4185 | 1224297.5273 | 2664102.4364 | 1224289.2602 | 2664089.211 | 1224279.5449
8 | 2664196.2959 | 1224162.4235 | 2664199.4737 | 1224166.5827 | 2664195.1807 | 1224180.7566 | 2664185.9467 | 1224183.4143 | 2664174.47 | 1224180.989 | 2664150.6506 | 1224170.648 | 2664134.7487 | 1224167.9417
9 | 2664196.2959 | 1224162.4235 | 2664174.9385 | 1224153.1406
10 | 2664234.807 | 1224104.235 | 2664231.6307 | 1224125.2252 | 2664231.3054 | 1224143.3458
11 | 2664054.4544 | 1224273.7562 | 2664089.211 | 1224279.5449
12 | 2664141.125 | 1224152.4286 | 2664145.9228 | 1224140.7558 | 2664155.6386 | 1224144.7519 | 2664174.9385 | 1224153.1406
13 | 2664101.3535 | 1224107.5101 | 2664125.8377 | 1224118.8032
14 | 2664125.8377 | 1224118.8032 | 2664130.16 | 1224108.9434 | 2664153.8031 | 1224099.7811 | 2664160.2897 | 1224099.7044
15 | 2664101.3535 | 1224107.5101 | 2664114.985 | 1224074.3256
16 | 2664076.4537 | 1224096.0682 | 2664091.0987 | 1224102.8523 | 2664101.3535 | 1224107.5101
17 | 2664160.2897 | 1224099.7044 | 2664197.0682 | 1224099.2693 | 2664205.4467 | 1224100.3717
18 | 2664234.807 | 1224104.235 | 2664247.1057 | 1224106.8373
19 | 2664234.807 | 1224104.235 | 2664225.9761 | 1224103.073
20 | 2664054.4544 | 1224273.7562 | 2664052.3579 | 1224266.3511 | 2664046.1523 | 1224262.4152 | 2664013.2095 | 1224255.7678 | 2664004.9985 | 1224254.2675 | 2664009.9612 | 1224236.2982
21 | 2664009.9612 | 1224236.2982 | 2664022.9947 | 1224239.2069 | 2664031.7074 | 1224213.5933
22 | 2664114.985 | 1224074.3256 | 2664132.9142 | 1224030.6786 | 2664134.273 | 1224024.9118 | 2664136.6909 | 1224010.94
23 | 2664076.4537 | 1224096.0682 | 2664070.0528 | 1224093.342 | 2664055.7568 | 1224087.2399 | 2664039.7729 | 1224080.4276
24 | 2664206.678 | 1224100.5337 | 2664205.4467 | 1224100.3717
25 | 2664039.7729 | 1224080.4276 | 2663982.889 | 1223986.8308
26 | 2663954.7537 | 1223977.2396 | 2663982.889 | 1223986.8308
27 | 2663931.467 | 1223969.4402 | 2663914.6717 | 1223964.0137
28 | 2663931.467 | 1223969.4402 | 2663939.3261 | 1223971.9706 | 2663952.8167 | 1223976.5781
29 | 2663954.7537 | 1223977.2396 | 2663952.8167 | 1223976.5781
30 | 2663954.7537 | 1223977.2396 | 2663946.6696 | 1223997.5109
31 | 2664206.678 | 1224100.5337 | 2664225.9761 | 1224103.073

## bus_geodata
| x | y | coords
0 | 2664245.4074 | 1224202.8366
1 | 2664236.6631 | 1224230.3129
2 | 2664254.4388 | 1224174.4583
3 | 2664225.6258 | 1224264.9943
4 | 2664228.2676 | 1224162.8352
5 | 2664152.9964 | 1224300.523
6 | 2664196.2959 | 1224162.4235
7 | 2664231.3054 | 1224143.3458
8 | 2664089.211 | 1224279.5449
9 | 2664134.7487 | 1224167.9417
10 | 2664174.9385 | 1224153.1406
11 | 2664125.8377 | 1224118.8032
12 | 2664101.3535 | 1224107.5101
13 | 2664160.2897 | 1224099.7044
14 | 2664234.807 | 1224104.235
15 | 2664247.1057 | 1224106.8373
16 | 2664054.4544 | 1224273.7562
17 | 2664009.9612 | 1224236.2982
18 | 2664031.7074 | 1224213.5933
19 | 2664141.125 | 1224152.4286
20 | 2664114.985 | 1224074.3256
21 | 2664076.4537 | 1224096.0682
22 | 2664205.4467 | 1224100.3717
23 | 2664039.7729 | 1224080.4276
24 | 2663982.889 | 1223986.8308
25 | 2663914.6717 | 1223964.0137
26 | 2663931.467 | 1223969.4402
27 | 2663952.8167 | 1223976.5781
28 | 2663954.7537 | 1223977.2396
29 | 2663946.6696 | 1223997.5109
30 | 2664136.6909 | 1224010.94
31 | 2664206.678 | 1224100.5337
32 | 2664225.9761 | 1224103.073
33 | 2664125.8377 | 1224118.8032

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98629 | -0.095502 | 0.00049578 | 0.00012425
1 | 0.98501 | -0.10442 | 0.0010912 | 0.00027348
2 | 0.98762 | -0.086166 | 0 | 0
3 | 0.98347 | -0.11529 | 0 | 0
4 | 0.9889 | -0.077233 | 0 | 0
5 | 0.97952 | -0.14318 | 0 | 0
6 | 0.98746 | -0.08743 | 0 | 0
7 | 0.98969 | -0.071713 | 0.011408 | 0.0028592
8 | 0.9766 | -0.16393 | 0.0027169 | 0.00068092
9 | 0.98545 | -0.10169 | 0.016655 | 0.0041741
10 | 0.98723 | -0.08908 | 0.0052685 | 0.0013204
11 | 0.99825 | -0.012061 | 0 | 0
12 | 1 | 0 | -0.1955 | -0.049072
13 | 0.99549 | -0.031251 | 0.015938 | 0.0039944
14 | 0.99156 | -0.058584 | 0 | 0
15 | 0.99153 | -0.05881 | 0.0017724 | 0.00044421
16 | 0.97524 | -0.17363 | 0 | 0
17 | 0.97233 | -0.19454 | 0 | 0
18 | 0.97077 | -0.20576 | 0.026256 | 0.0065805
19 | 0.98712 | -0.089827 | 0.0016486 | 0.00041319
20 | 0.99934 | -0.0046547 | 0.0087916 | 0.0022034
21 | 0.99647 | -0.024625 | 0 | 0
22 | 0.99307 | -0.048089 | 0.0021345 | 0.00053495
23 | 0.99131 | -0.060859 | 0.088409 | 0.022157
24 | 0.99107 | -0.062549 | 0.00044249 | 0.0001109
25 | 0.99101 | -0.063014 | 0.00031566 | 7.9112e-05
26 | 0.99102 | -0.062958 | 0 | 0
27 | 0.99103 | -0.062885 | 0.00027514 | 6.8956e-05
28 | 0.99103 | -0.062872 | 0 | 0
29 | 0.99101 | -0.062977 | 0.00047161 | 0.0001182
30 | 0.99893 | -0.0074768 | 0.0041917 | 0.0010505
31 | 0.993 | -0.048539 | 0.00060904 | 0.00015264
32 | 0.992 | -0.055539 | 0.0036064 | 0.00090386
33 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.030499 | 0.0076971 | -0.030461 | -0.0076829 | 3.8126e-05 | 1.4297e-05 | 0.046033 | 0.046033 | 0.046033 | 0.98629 | -0.095502 | 0.98501 | -0.10442 | 17.0492
1 | -0.030995 | -0.0078214 | 0.031035 | 0.0078367 | 4.0668e-05 | 1.5261e-05 | 0.046781 | 0.046781 | 0.046781 | 0.98629 | -0.095502 | 0.98762 | -0.086166 | 17.3262
2 | 0.029369 | 0.0074094 | -0.029325 | -0.0073926 | 4.474e-05 | 1.6745e-05 | 0.044384 | 0.044385 | 0.044385 | 0.98501 | -0.10442 | 0.98347 | -0.11529 | 16.4388
3 | -0.031035 | -0.0078367 | 0.031074 | 0.0078513 | 3.9009e-05 | 1.4637e-05 | 0.046781 | 0.04678 | 0.046781 | 0.98762 | -0.086166 | 0.9889 | -0.077233 | 17.3262
4 | 0.029325 | 0.0073926 | -0.029211 | -0.0073499 | 0.00011411 | 4.2713e-05 | 0.044385 | 0.044385 | 0.044385 | 0.98347 | -0.11529 | 0.97952 | -0.14318 | 16.4389
5 | 0.02364 | 0.0059314 | -0.023606 | -0.0059191 | 3.3399e-05 | 1.2304e-05 | 0.035574 | 0.035574 | 0.035574 | 0.9889 | -0.077233 | 0.98746 | -0.08743 | 13.1755
6 | -0.054714 | -0.013783 | 0.054756 | 0.013798 | 4.2278e-05 | 1.5748e-05 | 0.082354 | 0.082354 | 0.082354 | 0.9889 | -0.077233 | 0.98969 | -0.071713 | 15.2508
7 | 0.029211 | 0.0073499 | -0.029126 | -0.0073183 | 8.4331e-05 | 3.1574e-05 | 0.044385 | 0.044385 | 0.044385 | 0.97952 | -0.14318 | 0.9766 | -0.16393 | 16.439
8 | 0.016688 | 0.0041857 | -0.016655 | -0.0041741 | 3.2945e-05 | 1.1605e-05 | 0.025148 | 0.025148 | 0.025148 | 0.98746 | -0.08743 | 0.98545 | -0.10169 | 9.3142
9 | 0.0069189 | 0.0017334 | -0.0069173 | -0.0017331 | 1.5796e-06 | 3.097e-07 | 0.010426 | 0.010426 | 0.010426 | 0.98746 | -0.08743 | 0.98723 | -0.08908 | 3.8615
10 | -0.066165 | -0.016658 | 0.066286 | 0.016703 | 0.00012157 | 4.5745e-05 | 0.099506 | 0.099506 | 0.099506 | 0.98969 | -0.071713 | 0.99156 | -0.058584 | 18.4271
11 | 0.026409 | 0.0066374 | -0.026374 | -0.0066242 | 3.5613e-05 | 1.3257e-05 | 0.040246 | 0.040246 | 0.040246 | 0.9766 | -0.16393 | 0.97524 | -0.17363 | 14.9059
12 | 0.0016488 | 0.00041269 | -0.0016486 | -0.00041319 | 1.7022e-07 | -4.9924e-07 | 0.002485 | 0.0024852 | 0.0024852 | 0.98723 | -0.08908 | 0.98712 | -0.089827 | 0.92044
13 | -0.09087 | -0.022932 | 0.091025 | 0.02299 | 0.0001541 | 5.8565e-05 | 0.13551 | 0.13551 | 0.13551 | 0.99825 | -0.012061 | 1 | 0 | 25.0942
14 | 0.09087 | 0.022932 | -0.090626 | -0.022839 | 0.00024411 | 9.2779e-05 | 0.13551 | 0.13551 | 0.13551 | 0.99825 | -0.012061 | 0.99549 | -0.031251 | 25.0943
15 | 0.012993 | 0.0032564 | -0.012985 | -0.0032537 | 8.3682e-06 | 2.7482e-06 | 0.019334 | 0.019334 | 0.019334 | 1 | 0 | 0.99934 | -0.0046547 | 7.1609
16 | 0.090678 | 0.022825 | -0.090367 | -0.022706 | 0.00031073 | 0.00011915 | 0.13497 | 0.13497 | 0.13497 | 1 | 0 | 0.99647 | -0.024625 | 49.9871
17 | 0.074688 | 0.018845 | -0.074512 | -0.018778 | 0.00017603 | 6.6532e-05 | 0.11169 | 0.11169 | 0.11169 | 0.99549 | -0.031251 | 0.99307 | -0.048089 | 20.6826
18 | 0.0017725 | 0.00044407 | -0.0017724 | -0.00044421 | 5.5498e-08 | -1.408e-07 | 0.0026598 | 0.0026599 | 0.0026599 | 0.99156 | -0.058584 | 0.99153 | -0.05881 | 0.98515
19 | -0.068059 | -0.017147 | 0.068088 | 0.017158 | 2.9007e-05 | 1.0927e-05 | 0.10217 | 0.10217 | 0.10217 | 0.99156 | -0.058584 | 0.992 | -0.055539 | 18.9196
20 | 0.026374 | 0.0066242 | -0.026297 | -0.0065957 | 7.6451e-05 | 2.8463e-05 | 0.040246 | 0.040246 | 0.040246 | 0.97524 | -0.17363 | 0.97233 | -0.19454 | 14.906
21 | 0.026297 | 0.0065957 | -0.026256 | -0.0065805 | 4.0843e-05 | 1.5208e-05 | 0.040246 | 0.040246 | 0.040246 | 0.97233 | -0.19454 | 0.97077 | -0.20576 | 14.9061
22 | 0.0041933 | 0.0010503 | -0.0041917 | -0.0010505 | 1.6369e-06 | -2.5168e-07 | 0.0062436 | 0.0062439 | 0.0062439 | 0.99934 | -0.0046547 | 0.99893 | -0.0074768 | 2.3126
23 | 0.090367 | 0.022706 | -0.089914 | -0.022532 | 0.00045325 | 0.00017381 | 0.13497 | 0.13497 | 0.13497 | 0.99647 | -0.024625 | 0.99131 | -0.060859 | 49.9872
24 | 0.072378 | 0.018243 | -0.072373 | -0.018241 | 4.5607e-06 | 1.722e-06 | 0.10849 | 0.10849 | 0.10849 | 0.99307 | -0.048089 | 0.993 | -0.048539 | 20.0904
25 | 0.0015053 | 0.0003747 | -0.001505 | -0.00037598 | 3.4874e-07 | -1.2776e-06 | 0.0022587 | 0.0022592 | 0.0022592 | 0.99131 | -0.060859 | 0.99107 | -0.062549 | 0.83672
26 | 0.0010625 | 0.00026508 | -0.0010624 | -0.00026545 | 4.7179e-08 | -3.6488e-07 | 0.0015948 | 0.0015949 | 0.0015949 | 0.99107 | -0.062549 | 0.99103 | -0.062872 | 0.59071
27 | -0.00031566 | -7.9112e-05 | 0.00031566 | 7.8886e-05 | 2.4738e-09 | -2.2646e-07 | 0.00047397 | 0.00047389 | 0.00047397 | 0.99101 | -0.063014 | 0.99102 | -0.062958 | 0.17554
28 | -0.00031566 | -7.8886e-05 | 0.00031567 | 7.8597e-05 | 3.154e-09 | -2.8885e-07 | 0.00047389 | 0.00047379 | 0.00047389 | 0.99102 | -0.062958 | 0.99103 | -0.062885 | 0.17552
29 | -0.00059081 | -0.00014755 | 0.00059081 | 0.00014753 | 1.0047e-09 | -2.5988e-08 | 0.00088691 | 0.0008869 | 0.00088691 | 0.99103 | -0.062885 | 0.99103 | -0.062872 | 0.32848
30 | 0.00047162 | 0.00011792 | -0.00047161 | -0.0001182 | 6.8277e-09 | -2.7857e-07 | 0.00070803 | 0.00070813 | 0.00070813 | 0.99103 | -0.062872 | 0.99101 | -0.062977 | 0.26227
31 | 0.071764 | 0.018089 | -0.071694 | -0.018062 | 7.0278e-05 | 2.6527e-05 | 0.10758 | 0.10758 | 0.10758 | 0.993 | -0.048539 | 0.992 | -0.055539 | 19.9214

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.1955 | 0.049072

## res_load
| p_mw | q_mvar
0 | 0.00049578 | 0.00012425
1 | 0.0010912 | 0.00027348
2 | 0.011408 | 0.0028592
3 | 0.0027169 | 0.00068092
4 | 0.016655 | 0.0041741
5 | 0.0052685 | 0.0013204
6 | 0.015938 | 0.0039944
7 | 0.0017724 | 0.00044421
8 | 0.026256 | 0.0065805
9 | 0.0016486 | 0.00041319
10 | 0.0087916 | 0.0022034
11 | 0.0021345 | 0.00053495
12 | 0.088409 | 0.022157
13 | 0.00044249 | 0.0001109
14 | 0.00031566 | 7.9112e-05
15 | 0.00027514 | 6.8956e-05
16 | 0.00047161 | 0.0001182
17 | 0.0041917 | 0.0010505
18 | 0.00060904 | 0.00015264
19 | 0.0036064 | 0.00090386

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1