## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1031-20_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1031-20_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1031-20_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1031-20_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1031-20_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1031-20_0_3_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_1031-20_0_3_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_1031-20_0_3_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_1031-20_0_3_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_1031-20_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1031-20_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1031-20_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1031-20_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1031-20_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1031-20_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1031-20_0_3_node_25 | 0.4 | n |  | TRUE
16 | bus_LV_1031-20_0_3_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_1031-20_0_3_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_1031-20_0_3_node_33 | 0.4 | n |  | TRUE
19 | bus_LV_1031-20_0_3_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1031-20_0_3_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1031-20_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1031-20_0_3_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1031-20_0_3_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_1031-20_0_3_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_1031-20_0_3_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_1031-20_0_3_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1031-20_0_3_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1031-20_0_3_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1031-20_0_3_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_1031-20_0_3_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_1031-20_0_3_node_31 | 0.4 | n |  | TRUE
32 | bus_MV_353_1_node_45 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1031-20_0_3_load_0 | 0 | 0.0093863 | 0.0023524 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1031-20_0_3_load_1 | 1 | 0.02953 | 0.0074008 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1031-20_0_3_load_4 | 4 | 0.0065455 | 0.0016405 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1031-20_0_3_load_16 | 5 | 0.029435 | 0.0073771 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1031-20_0_3_load_20 | 6 | 0.0053352 | 0.0013371 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1031-20_0_3_load_17 | 7 | 0.0104 | 0.0026064 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1031-20_0_3_load_19 | 8 | 0.0058536 | 0.001467 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1031-20_0_3_load_5 | 9 | 0.0083245 | 0.0020863 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1031-20_0_3_load_6 | 10 | 0.0074901 | 0.0018772 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1031-20_0_3_load_8 | 12 | 0.030332 | 0.007602 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1031-20_0_3_load_9 | 13 | 0.0037078 | 0.00092927 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1031-20_0_3_load_10 | 14 | 0.010256 | 0.0025704 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1031-20_0_3_load_25 | 15 | 0.0058158 | 0.0014576 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1031-20_0_3_load_24 | 17 | 0.0058337 | 0.0014621 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1031-20_0_3_load_33 | 18 | 0.0063593 | 0.0015938 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1031-20_0_3_load_11 | 19 | 0.0055628 | 0.0013942 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1031-20_0_3_load_12 | 20 | 0.0040687 | 0.0010197 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1031-20_0_3_load_13 | 21 | 0.0034751 | 0.00087094 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1031-20_0_3_load_26 | 24 | 0.0087935 | 0.0022039 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1031-20_0_3_load_28 | 25 | 0.0036423 | 0.00091285 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1031-20_0_3_load_23 | 26 | 0.0034559 | 0.00086612 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1031-20_0_3_load_22 | 28 | 0.0058182 | 0.0014582 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1031-20_0_3_load_30 | 30 | 0.0053104 | 0.0013309 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1031-20_0_3_load_31 | 31 | 0.0036641 | 0.00091831 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1031-20_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.014531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1031-20_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.042382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1031-20_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.027467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1031-20_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.011809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1031-20_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.063009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1031-20_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0063992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1031-20_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.037259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1031-20_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.029967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1031-20_0_3_line_8 | NAYY 4x150 SE | 8 | 27 | 0.0021505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1031-20_0_3_line_9 | NAYY 4x150 SE | 9 | 10 | 0.017141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1031-20_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.02202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1031-20_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.028483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1031-20_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.003962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1031-20_0_3_line_13 | NAYY 4x150 SE | 11 | 14 | 0.022817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1031-20_0_3_line_14 | NAYY 4x150 SE | 13 | 15 | 0.023881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1031-20_0_3_line_15 | NAYY 4x150 SE | 14 | 16 | 0.010722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1031-20_0_3_line_16 | NAYY 4x150 SE | 15 | 17 | 0.010739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1031-20_0_3_line_17 | NAYY 4x150 SE | 16 | 18 | 0.018364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1031-20_0_3_line_18 | NAYY 4x150 SE | 17 | 28 | 0.0040503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1031-20_0_3_line_19 | NAYY 4x150 SE | 19 | 20 | 0.017306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1031-20_0_3_line_20 | NAYY 4x150 SE | 19 | 21 | 0.0076435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1031-20_0_3_line_21 | NAYY 4x150 SE | 21 | 22 | 0.011433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1031-20_0_3_line_22 | NAYY 4x150 SE | 22 | 23 | 0.028801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1031-20_0_3_line_23 | NAYY 4x150 SE | 22 | 24 | 0.0083215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1031-20_0_3_line_24 | NAYY 4x150 SE | 23 | 25 | 0.017354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1031-20_0_3_line_25 | NAYY 4x150 SE | 24 | 26 | 0.042772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1031-20_0_3_line_26 | NAYY 4x150 SE | 25 | 29 | 0.026043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1031-20_0_3_line_27 | NAYY 4x150 SE | 26 | 27 | 0.010663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1031-20_0_3_line_28 | NAYY 4x150 SE | 27 | 28 | 0.018233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_1031-20_0_3_line_29 | NAYY 4x150 SE | 29 | 30 | 0.028532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1031-20_0_3_line_30 | NAYY 4x150 SE | 29 | 31 | 0.0046995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1031-20_0_3_trafo_22 | 0.25 MVA 20/0.4 kV | 32 | 28 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2664329.4948 | 1225001.5892 | 2664343.5219 | 1225005.3846
1 | 2664288.6167 | 1224990.4052 | 2664294.1338 | 1224992.0213 | 2664329.4948 | 1225001.5892
2 | 2664370.1811 | 1225011.2887 | 2664365.9111 | 1225011.4426 | 2664343.5219 | 1225005.3846
3 | 2664288.6167 | 1224990.4052 | 2664284.8133 | 1225001.5851
4 | 2664370.1811 | 1225011.2887 | 2664385.3139 | 1225015.4995 | 2664378.6824 | 1225062.334
5 | 2664284.8133 | 1225001.5851 | 2664282.7523 | 1225007.6432
6 | 2664372.7006 | 1225099.1012 | 2664376.0462 | 1225080.9523 | 2664378.6824 | 1225062.334
7 | 2664273.1007 | 1225036.0137 | 2664282.7523 | 1225007.6432
8 | 2664272.4081 | 1225038.0496 | 2664273.1007 | 1225036.0137
9 | 2664285.4724 | 1225103.1013 | 2664302.179 | 1225106.9358
10 | 2664264.0104 | 1225098.1753 | 2664285.4724 | 1225103.1013
11 | 2664302.179 | 1225106.9358 | 2664309.3034 | 1225108.571 | 2664330.3304 | 1225106.0876
12 | 2664264.0104 | 1225098.1753 | 2664264.0638 | 1225094.2136
13 | 2664264.0104 | 1225098.1753 | 2664263.7388 | 1225117.7071 | 2664263.1245 | 1225120.9325
14 | 2664266.1323 | 1225070.4267 | 2664264.0864 | 1225092.5392 | 2664264.0638 | 1225094.2136
15 | 2664261.1186 | 1225131.4654 | 2664263.1245 | 1225120.9325
16 | 2664266.1323 | 1225070.4267 | 2664266.7645 | 1225063.594 | 2664267.6008 | 1225059.8084
17 | 2664261.1186 | 1225131.4654 | 2664254.4925 | 1225148.5919
18 | 2664268.4746 | 1225055.8534 | 2664267.6008 | 1225059.8084
19 | 2664198.6897 | 1225069.7908 | 2664204.5427 | 1225053.5041
20 | 2664207.1277 | 1225046.3111 | 2664204.5427 | 1225053.5041
21 | 2664210.9942 | 1225035.552 | 2664207.1277 | 1225046.3111
22 | 2664183.3492 | 1225027.3598 | 2664205.2279 | 1225033.1439 | 2664210.9942 | 1225035.552
23 | 2664210.9942 | 1225035.552 | 2664219.2409 | 1225034.4387
24 | 2664183.3492 | 1225027.3598 | 2664190.2727 | 1225011.4465
25 | 2664261.8181 | 1225036.8008 | 2664249.3668 | 1225035.3325 | 2664224.9494 | 1225033.668 | 2664219.2409 | 1225034.4387
26 | 2664200.6627 | 1224987.5654 | 2664190.2727 | 1225011.4465
27 | 2664272.4081 | 1225038.0496 | 2664261.8181 | 1225036.8008
28 | 2664272.4081 | 1225038.0496 | 2664268.4746 | 1225055.8534
29 | 2664200.6627 | 1224987.5654 | 2664212.049 | 1224961.4041
30 | 2664200.6627 | 1224987.5654 | 2664203.3047 | 1224991.452

## bus_geodata
| x | y | coords
0 | 2664329.4948 | 1225001.5892
1 | 2664343.5219 | 1225005.3846
2 | 2664288.6167 | 1224990.4052
3 | 2664370.1811 | 1225011.2887
4 | 2664284.8133 | 1225001.5851
5 | 2664378.6824 | 1225062.334
6 | 2664282.7523 | 1225007.6432
7 | 2664372.7006 | 1225099.1012
8 | 2664273.1007 | 1225036.0137
9 | 2664285.4724 | 1225103.1013
10 | 2664302.179 | 1225106.9358
11 | 2664264.0104 | 1225098.1753
12 | 2664330.3304 | 1225106.0876
13 | 2664264.0638 | 1225094.2136
14 | 2664263.1245 | 1225120.9325
15 | 2664266.1323 | 1225070.4267
16 | 2664261.1186 | 1225131.4654
17 | 2664267.6008 | 1225059.8084
18 | 2664254.4925 | 1225148.5919
19 | 2664204.5427 | 1225053.5041
20 | 2664198.6897 | 1225069.7908
21 | 2664207.1277 | 1225046.3111
22 | 2664210.9942 | 1225035.552
23 | 2664183.3492 | 1225027.3598
24 | 2664219.2409 | 1225034.4387
25 | 2664190.2727 | 1225011.4465
26 | 2664261.8181 | 1225036.8008
27 | 2664272.4081 | 1225038.0496
28 | 2664268.4746 | 1225055.8534
29 | 2664200.6627 | 1224987.5654
30 | 2664212.049 | 1224961.4041
31 | 2664203.3047 | 1224991.452
32 | 2664272.4081 | 1225038.0496

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98702 | -0.090646 | 0.0093863 | 0.0023524
1 | 0.98556 | -0.10099 | 0.02953 | 0.0074008
2 | 0.99186 | -0.056614 | 0 | 0
3 | 0.98397 | -0.11225 | 0 | 0
4 | 0.99321 | -0.04719 | 0.0065455 | 0.0016405
5 | 0.98032 | -0.13823 | 0.029435 | 0.0073771
6 | 0.994 | -0.041671 | 0.0053352 | 0.0013371
7 | 0.97975 | -0.14225 | 0.0104 | 0.0026064
8 | 0.99793 | -0.014339 | 0.0058536 | 0.001467
9 | 0.99434 | -0.039603 | 0.0083245 | 0.0020863
10 | 0.99341 | -0.046154 | 0.0074901 | 0.0018772
11 | 0.9958 | -0.029359 | 0 | 0
12 | 0.99217 | -0.054902 | 0.030332 | 0.007602
13 | 0.99616 | -0.026857 | 0.0037078 | 0.00092927
14 | 0.99526 | -0.033178 | 0.010256 | 0.0025704
15 | 0.99843 | -0.010925 | 0.0058158 | 0.0014576
16 | 0.99516 | -0.033865 | 0 | 0
17 | 0.99955 | -0.0031599 | 0.0058337 | 0.0014621
18 | 0.99499 | -0.035042 | 0.0063593 | 0.0015938
19 | 0.99491 | -0.035572 | 0.0055628 | 0.0013942
20 | 0.99481 | -0.036282 | 0.0040687 | 0.0010197
21 | 0.99501 | -0.03483 | 0.0034751 | 0.00087094
22 | 0.99523 | -0.033319 | 0 | 0
23 | 0.99471 | -0.036985 | 0 | 0
24 | 0.99554 | -0.031162 | 0.0087935 | 0.0022039
25 | 0.99439 | -0.039196 | 0.0036423 | 0.00091285
26 | 0.99765 | -0.016319 | 0.0034559 | 0.00086612
27 | 0.99823 | -0.012259 | 0 | 0
28 | 1 | 0 | -0.2154 | -0.054046
29 | 0.99406 | -0.041557 | 0 | 0
30 | 0.99384 | -0.043088 | 0.0053104 | 0.0013309
31 | 0.99403 | -0.041731 | 0.0036641 | 0.00091831
32 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.069676 | 0.017503 | -0.069576 | -0.017464 | 0.00010008 | 3.8307e-05 | 0.10506 | 0.10506 | 0.10506 | 0.98702 | -0.090646 | 0.98556 | -0.10099 | 38.9102
1 | -0.079063 | -0.019855 | 0.079439 | 0.019999 | 0.00037581 | 0.000144 | 0.11921 | 0.11921 | 0.11921 | 0.98702 | -0.090646 | 0.99186 | -0.056614 | 44.1512
2 | 0.040047 | 0.010063 | -0.039984 | -0.01004 | 6.2679e-05 | 2.3758e-05 | 0.060473 | 0.060473 | 0.060473 | 0.98556 | -0.10099 | 0.98397 | -0.11225 | 22.3974
3 | -0.079439 | -0.019999 | 0.079543 | 0.020039 | 0.00010472 | 4.0123e-05 | 0.11921 | 0.11921 | 0.11921 | 0.99186 | -0.056614 | 0.99321 | -0.04719 | 44.1511
4 | 0.039984 | 0.01004 | -0.03984 | -0.0099852 | 0.00014379 | 5.4505e-05 | 0.060473 | 0.060473 | 0.060473 | 0.98397 | -0.11225 | 0.98032 | -0.13823 | 22.3975
5 | -0.086089 | -0.02168 | 0.086155 | 0.021705 | 6.6464e-05 | 2.548e-05 | 0.12901 | 0.12901 | 0.12901 | 0.99321 | -0.04719 | 0.994 | -0.041671 | 47.7831
6 | 0.010405 | 0.0026081 | -0.0104 | -0.0026064 | 5.7998e-06 | 1.7612e-06 | 0.015794 | 0.015794 | 0.015794 | 0.98032 | -0.13823 | 0.97975 | -0.14225 | 5.8498
7 | -0.09149 | -0.023042 | 0.091841 | 0.023177 | 0.00035098 | 0.0001346 | 0.137 | 0.137 | 0.137 | 0.994 | -0.041671 | 0.99793 | -0.014339 | 50.7411
8 | -0.097695 | -0.024644 | 0.097723 | 0.024655 | 2.8498e-05 | 1.0933e-05 | 0.14573 | 0.14573 | 0.14573 | 0.99793 | -0.014339 | 0.99823 | -0.012259 | 53.9738
9 | 0.037894 | 0.009506 | -0.037859 | -0.009493 | 3.4399e-05 | 1.3008e-05 | 0.05671 | 0.056711 | 0.056711 | 0.99434 | -0.039603 | 0.99341 | -0.046154 | 21.0039
10 | -0.046218 | -0.011592 | 0.046284 | 0.011617 | 6.5738e-05 | 2.4998e-05 | 0.069168 | 0.069168 | 0.069168 | 0.99434 | -0.039603 | 0.9958 | -0.029359 | 25.6178
11 | 0.030369 | 0.0076158 | -0.030332 | -0.007602 | 3.6781e-05 | 1.3778e-05 | 0.045491 | 0.045491 | 0.045491 | 0.99341 | -0.046154 | 0.99217 | -0.054902 | 16.8486
12 | -0.06291 | -0.015785 | 0.062931 | 0.015793 | 2.1851e-05 | 8.3526e-06 | 0.094012 | 0.094012 | 0.094012 | 0.9958 | -0.029359 | 0.99616 | -0.026857 | 34.8192
13 | 0.016626 | 0.0041675 | -0.016617 | -0.0041644 | 8.7879e-06 | 3.0833e-06 | 0.024844 | 0.024844 | 0.024844 | 0.9958 | -0.029359 | 0.99526 | -0.033178 | 9.2015
14 | -0.066639 | -0.016722 | 0.066787 | 0.016779 | 0.00014768 | 5.649e-05 | 0.09955 | 0.09955 | 0.09955 | 0.99616 | -0.026857 | 0.99843 | -0.010925 | 36.8705
15 | 0.0063609 | 0.001594 | -0.0063603 | -0.0015939 | 6.0514e-07 | 9.3421e-08 | 0.0095102 | 0.0095103 | 0.0095103 | 0.99526 | -0.033178 | 0.99516 | -0.033865 | 3.5223
16 | -0.072603 | -0.018237 | 0.072681 | 0.018267 | 7.8476e-05 | 3.0043e-05 | 0.10822 | 0.10822 | 0.10822 | 0.99843 | -0.010925 | 0.99955 | -0.0031599 | 40.0807
17 | 0.0063603 | 0.0015939 | -0.0063593 | -0.0015938 | 1.0364e-06 | 1.6007e-07 | 0.0095103 | 0.0095103 | 0.0095103 | 0.99516 | -0.033865 | 0.99499 | -0.035042 | 3.5223
18 | -0.078515 | -0.019729 | 0.078549 | 0.019742 | 3.454e-05 | 1.3232e-05 | 0.1169 | 0.1169 | 0.1169 | 0.99955 | -0.0031599 | 1 | 0 | 43.2972
19 | 0.0040691 | 0.0010196 | -0.0040687 | -0.0010197 | 3.9998e-07 | -7.0881e-08 | 0.0060858 | 0.0060859 | 0.0060859 | 0.99491 | -0.035572 | 0.99481 | -0.036282 | 2.254
20 | -0.009632 | -0.0024138 | 0.0096329 | 0.0024141 | 9.898e-07 | 2.8142e-07 | 0.014406 | 0.014406 | 0.014406 | 0.99491 | -0.035572 | 0.99501 | -0.03483 | 5.3355
21 | -0.013108 | -0.003285 | 0.013111 | 0.0032859 | 2.7413e-06 | 9.0583e-07 | 0.019603 | 0.019603 | 0.019603 | 0.99501 | -0.03483 | 0.99523 | -0.033319 | 7.2602
22 | 0.012631 | 0.0031663 | -0.012625 | -0.0031642 | 6.4101e-06 | 2.0914e-06 | 0.018886 | 0.018886 | 0.018886 | 0.99523 | -0.033319 | 0.99471 | -0.036985 | 6.9948
23 | -0.025742 | -0.0064522 | 0.02575 | 0.0064551 | 7.6921e-06 | 2.8504e-06 | 0.038488 | 0.038488 | 0.038488 | 0.99523 | -0.033319 | 0.99554 | -0.031162 | 14.255
24 | 0.012625 | 0.0031642 | -0.012621 | -0.0031629 | 3.8625e-06 | 1.2604e-06 | 0.018886 | 0.018886 | 0.018886 | 0.99471 | -0.036985 | 0.99439 | -0.039196 | 6.9948
25 | -0.034543 | -0.0086589 | 0.034614 | 0.0086857 | 7.115e-05 | 2.6808e-05 | 0.051632 | 0.051632 | 0.051632 | 0.99554 | -0.031162 | 0.99765 | -0.016319 | 19.1229
26 | 0.0089787 | 0.0022501 | -0.0089758 | -0.0022493 | 2.9336e-06 | 7.9058e-07 | 0.013436 | 0.013436 | 0.013436 | 0.99439 | -0.039196 | 0.99406 | -0.041557 | 4.9762
27 | -0.03807 | -0.0095518 | 0.038092 | 0.00956 | 2.1457e-05 | 8.1133e-06 | 0.056786 | 0.056786 | 0.056786 | 0.99765 | -0.016319 | 0.99823 | -0.012259 | 21.0319
28 | -0.13582 | -0.034215 | 0.13605 | 0.034304 | 0.00023331 | 8.9257e-05 | 0.20252 | 0.20252 | 0.20252 | 0.99823 | -0.012259 | 1 | 0 | 37.5028
29 | 0.0053116 | 0.001331 | -0.0053104 | -0.0013309 | 1.1255e-06 | 6.3084e-08 | 0.0079508 | 0.007951 | 0.007951 | 0.99406 | -0.041557 | 0.99384 | -0.043088 | 2.9448
30 | 0.0036642 | 0.00091829 | -0.0036641 | -0.00091831 | 8.8223e-08 | -2.699e-08 | 0.005485 | 0.005485 | 0.005485 | 0.99406 | -0.041557 | 0.99403 | -0.041731 | 2.0315

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22122 | 0.055504

## res_load
| p_mw | q_mvar
0 | 0.0093863 | 0.0023524
1 | 0.02953 | 0.0074008
2 | 0.0065455 | 0.0016405
3 | 0.029435 | 0.0073771
4 | 0.0053352 | 0.0013371
5 | 0.0104 | 0.0026064
6 | 0.0058536 | 0.001467
7 | 0.0083245 | 0.0020863
8 | 0.0074901 | 0.0018772
9 | 0.030332 | 0.007602
10 | 0.0037078 | 0.00092927
11 | 0.010256 | 0.0025704
12 | 0.0058158 | 0.0014576
13 | 0.0058337 | 0.0014621
14 | 0.0063593 | 0.0015938
15 | 0.0055628 | 0.0013942
16 | 0.0040687 | 0.0010197
17 | 0.0034751 | 0.00087094
18 | 0.0087935 | 0.0022039
19 | 0.0036423 | 0.00091285
20 | 0.0034559 | 0.00086612
21 | 0.0058182 | 0.0014582
22 | 0.0053104 | 0.0013309
23 | 0.0036641 | 0.00091831

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1