## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1031-25_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1031-25_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1031-25_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1031-25_0_3_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_1031-25_0_3_node_29 | 0.4 | n |  | TRUE
5 | bus_LV_1031-25_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1031-25_0_3_node_37 | 0.4 | n |  | TRUE
7 | bus_LV_1031-25_0_3_node_30 | 0.4 | n |  | TRUE
8 | bus_LV_1031-25_0_3_node_17 | 0.4 | n |  | TRUE
9 | bus_LV_1031-25_0_3_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_1031-25_0_3_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1031-25_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1031-25_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1031-25_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1031-25_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1031-25_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1031-25_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1031-25_0_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1031-25_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_1031-25_0_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1031-25_0_3_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_1031-25_0_3_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_1031-25_0_3_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_1031-25_0_3_node_67 | 0.4 | n |  | TRUE
24 | bus_LV_1031-25_0_3_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_1031-25_0_3_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_1031-25_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1031-25_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_1031-25_0_3_node_46 | 0.4 | n |  | TRUE
29 | bus_LV_1031-25_0_3_node_38 | 0.4 | n |  | TRUE
30 | bus_LV_1031-25_0_3_node_65 | 0.4 | n |  | TRUE
31 | bus_LV_1031-25_0_3_node_61 | 0.4 | n |  | TRUE
32 | bus_LV_1031-25_0_3_node_36 | 0.4 | n |  | TRUE
33 | bus_LV_1031-25_0_3_node_45 | 0.4 | n |  | TRUE
34 | bus_LV_1031-25_0_3_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_1031-25_0_3_node_66 | 0.4 | n |  | TRUE
36 | bus_LV_1031-25_0_3_node_64 | 0.4 | n |  | TRUE
37 | bus_LV_1031-25_0_3_node_25 | 0.4 | n |  | TRUE
38 | bus_LV_1031-25_0_3_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_1031-25_0_3_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_1031-25_0_3_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_1031-25_0_3_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_1031-25_0_3_node_31 | 0.4 | n |  | TRUE
43 | bus_LV_1031-25_0_3_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_1031-25_0_3_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_1031-25_0_3_node_43 | 0.4 | n |  | TRUE
46 | bus_LV_1031-25_0_3_node_39 | 0.4 | n |  | TRUE
47 | bus_LV_1031-25_0_3_node_47 | 0.4 | n |  | TRUE
48 | bus_LV_1031-25_0_3_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_1031-25_0_3_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_1031-25_0_3_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_1031-25_0_3_node_48 | 0.4 | n |  | TRUE
52 | bus_LV_1031-25_0_3_node_49 | 0.4 | n |  | TRUE
53 | bus_LV_1031-25_0_3_node_59 | 0.4 | n |  | TRUE
54 | bus_LV_1031-25_0_3_node_50 | 0.4 | n |  | TRUE
55 | bus_LV_1031-25_0_3_node_60 | 0.4 | n |  | TRUE
56 | bus_LV_1031-25_0_3_node_62 | 0.4 | n |  | TRUE
57 | bus_LV_1031-25_0_3_node_58 | 0.4 | n |  | TRUE
58 | bus_LV_1031-25_0_3_node_51 | 0.4 | n |  | TRUE
59 | bus_LV_1031-25_0_3_node_52 | 0.4 | n |  | TRUE
60 | bus_LV_1031-25_0_3_node_54 | 0.4 | n |  | TRUE
61 | bus_LV_1031-25_0_3_node_56 | 0.4 | n |  | TRUE
62 | bus_LV_1031-25_0_3_node_55 | 0.4 | n |  | TRUE
63 | bus_LV_1031-25_0_3_node_57 | 0.4 | n |  | TRUE
64 | bus_LV_1031-25_0_3_node_63 | 0.4 | n |  | TRUE
65 | bus_MV_353_1_node_80 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1031-25_0_3_load_0 | 0 | 0.015404 | 0.0038606 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1031-25_0_3_load_5 | 3 | 0.0061453 | 0.0015402 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1031-25_0_3_load_29 | 4 | 0.0024103 | 0.00060409 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1031-25_0_3_load_6 | 5 | 0.011064 | 0.0027729 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1031-25_0_3_load_37 | 6 | 0.0065346 | 0.0016377 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1031-25_0_3_load_30 | 7 | 0.0024109 | 0.00060424 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1031-25_0_3_load_17 | 8 | 0.0026801 | 0.00067169 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1031-25_0_3_load_18 | 9 | 0.0026793 | 0.00067149 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1031-25_0_3_load_7 | 10 | 0.002376 | 0.00059549 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1031-25_0_3_load_8 | 11 | 0.0049236 | 0.001234 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1031-25_0_3_load_11 | 14 | 0.0030636 | 0.00076782 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1031-25_0_3_load_12 | 15 | 0.003066 | 0.0007684 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1031-25_0_3_load_13 | 16 | 0.0057847 | 0.0014498 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1031-25_0_3_load_14 | 17 | 0.0032099 | 0.00080449 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1031-25_0_3_load_15 | 18 | 0.0023803 | 0.00059656 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1031-25_0_3_load_16 | 19 | 0.0030666 | 0.00076856 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1031-25_0_3_load_28 | 20 | 0.002674 | 0.00067017 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1031-25_0_3_load_24 | 21 | 0.0032807 | 0.00082221 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1031-25_0_3_load_67 | 23 | 0.0026831 | 0.00067244 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1031-25_0_3_load_19 | 26 | 0.0026823 | 0.00067225 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1031-25_0_3_load_20 | 27 | 0.0026785 | 0.00067131 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1031-25_0_3_load_46 | 28 | 0.0035537 | 0.00089063 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1031-25_0_3_load_38 | 29 | 0.011909 | 0.0029846 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1031-25_0_3_load_61 | 31 | 0.0039041 | 0.00097847 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1031-25_0_3_load_45 | 33 | 0.0029862 | 0.0007484 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1031-25_0_3_load_26 | 34 | 0.0034165 | 0.00085625 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1031-25_0_3_load_66 | 35 | 0.0071141 | 0.001783 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1031-25_0_3_load_64 | 36 | 0.0042789 | 0.0010724 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1031-25_0_3_load_27 | 38 | 0.0065118 | 0.001632 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1031-25_0_3_load_34 | 41 | 0.014119 | 0.0035384 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1031-25_0_3_load_31 | 42 | 0.0024135 | 0.00060488 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1031-25_0_3_load_35 | 43 | 0.0024124 | 0.0006046 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1031-25_0_3_load_43 | 45 | 0.0085506 | 0.002143 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1031-25_0_3_load_39 | 46 | 0.0049761 | 0.0012471 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1031-25_0_3_load_40 | 48 | 0.0021515 | 0.00053921 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1031-25_0_3_load_42 | 49 | 0.0035225 | 0.00088282 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1031-25_0_3_load_44 | 50 | 0.00211 | 0.0005288 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1031-25_0_3_load_48 | 51 | 0.0046109 | 0.0011556 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1031-25_0_3_load_49 | 52 | 0.0043993 | 0.0011026 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1031-25_0_3_load_50 | 54 | 0.0047891 | 0.0012003 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1031-25_0_3_load_62 | 56 | 0.0066143 | 0.0016577 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1031-25_0_3_load_58 | 57 | 0.0098043 | 0.0024572 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1031-25_0_3_load_51 | 58 | 0.0035467 | 0.0008889 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1031-25_0_3_load_52 | 59 | 0.003545 | 0.00088846 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1031-25_0_3_load_54 | 60 | 0.003545 | 0.00088846 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1031-25_0_3_load_56 | 61 | 0.0035468 | 0.0008889 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1031-25_0_3_load_55 | 62 | 0.0038961 | 0.00097645 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1031-25_0_3_load_57 | 63 | 0.0039023 | 0.00097801 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1031-25_0_3_load_63 | 64 | 0.0038989 | 0.00097716 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1031-25_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.079423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1031-25_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.037271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1031-25_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.084408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1031-25_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.010597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1031-25_0_3_line_4 | NAYY 4x150 SE | 4 | 7 | 0.0054775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1031-25_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.01044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1031-25_0_3_line_6 | NAYY 4x150 SE | 6 | 8 | 0.059152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1031-25_0_3_line_7 | NAYY 4x150 SE | 7 | 42 | 0.0054807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1031-25_0_3_line_8 | NAYY 4x150 SE | 8 | 9 | 0.0076993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1031-25_0_3_line_9 | NAYY 4x150 SE | 9 | 26 | 0.0077021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1031-25_0_3_line_10 | NAYY 4x150 SE | 10 | 11 | 0.00062404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1031-25_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.013336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_1031-25_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.0054227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1031-25_0_3_line_13 | NAYY 4x150 SE | 12 | 14 | 0.010351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1031-25_0_3_line_14 | NAYY 4x150 SE | 12 | 15 | 0.014876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1031-25_0_3_line_15 | NAYY 4x150 SE | 13 | 16 | 0.0055927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1031-25_0_3_line_16 | NAYY 4x150 SE | 13 | 17 | 0.0097497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1031-25_0_3_line_17 | NAYY 4x150 SE | 14 | 18 | 0.00086875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1031-25_0_3_line_18 | NAYY 4x150 SE | 15 | 19 | 0.0085259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1031-25_0_3_line_19 | NAYY 4x150 SE | 16 | 20 | 0.0028129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1031-25_0_3_line_20 | NAYY 4x150 SE | 17 | 21 | 0.00015418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1031-25_0_3_line_21 | NAYY 4x150 SE | 18 | 22 | 0.020761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_1031-25_0_3_line_22 | NAYY 4x150 SE | 20 | 23 | 0.0077006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1031-25_0_3_line_23 | NAYY 4x150 SE | 22 | 24 | 0.012122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_1031-25_0_3_line_24 | NAYY 4x150 SE | 22 | 25 | 0.030701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1031-25_0_3_line_25 | NAYY 4x150 SE | 23 | 27 | 0.0077021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1031-25_0_3_line_26 | NAYY 4x150 SE | 24 | 28 | 0.020946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_1031-25_0_3_line_27 | NAYY 4x150 SE | 25 | 29 | 0.014052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1031-25_0_3_line_28 | NAYY 4x150 SE | 25 | 30 | 0.069776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1031-25_0_3_line_29 | NAYY 4x150 SE | 26 | 27 | 0.007704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1031-25_0_3_line_30 | NAYY 4x150 SE | 28 | 31 | 0.00083231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_1031-25_0_3_line_31 | NAYY 4x150 SE | 30 | 35 | 0.017401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1031-25_0_3_line_32 | NAYY 4x150 SE | 30 | 36 | 0.031988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1031-25_0_3_line_33 | NAYY 4x150 SE | 31 | 53 | 0.0092893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
34 | LV_1031-25_0_3_line_34 | NAYY 4x150 SE | 32 | 33 | 0.0054007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_1031-25_0_3_line_35 | NAYY 4x150 SE | 32 | 34 | 0.022782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1031-25_0_3_line_36 | NAYY 4x150 SE | 33 | 47 | 0.030591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
37 | LV_1031-25_0_3_line_37 | NAYY 4x150 SE | 34 | 37 | 0.015378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1031-25_0_3_line_38 | NAYY 4x150 SE | 37 | 38 | 0.010938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1031-25_0_3_line_39 | NAYY 4x150 SE | 38 | 39 | 0.018419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1031-25_0_3_line_40 | NAYY 4x150 SE | 39 | 40 | 0.00439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1031-25_0_3_line_41 | NAYY 4x150 SE | 39 | 41 | 0.03152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1031-25_0_3_line_42 | NAYY 4x150 SE | 40 | 43 | 0.01842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1031-25_0_3_line_43 | NAYY 4x150 SE | 40 | 42 | 0.020498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1031-25_0_3_line_44 | NAYY 4x150 SE | 43 | 44 | 0.051498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1031-25_0_3_line_45 | NAYY 4x150 SE | 44 | 45 | 0.012729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1031-25_0_3_line_46 | NAYY 4x150 SE | 44 | 46 | 0.0073345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1031-25_0_3_line_47 | NAYY 4x150 SE | 45 | 50 | 0.030131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1031-25_0_3_line_48 | NAYY 4x150 SE | 46 | 48 | 0.014019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1031-25_0_3_line_49 | NAYY 4x150 SE | 47 | 51 | 0.00068985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1031-25_0_3_line_50 | NAYY 4x150 SE | 47 | 52 | 0.023668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
51 | LV_1031-25_0_3_line_51 | NAYY 4x150 SE | 48 | 49 | 0.026069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1031-25_0_3_line_52 | NAYY 4x150 SE | 52 | 54 | 5.6137e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_1031-25_0_3_line_53 | NAYY 4x150 SE | 53 | 57 | 0.013826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_1031-25_0_3_line_54 | NAYY 4x150 SE | 53 | 63 | 0.013544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1031-25_0_3_line_55 | NAYY 4x150 SE | 54 | 55 | 0.010473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
56 | LV_1031-25_0_3_line_56 | NAYY 4x150 SE | 55 | 56 | 0.0050463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1031-25_0_3_line_57 | NAYY 4x150 SE | 55 | 57 | 0.0065721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
58 | LV_1031-25_0_3_line_58 | NAYY 4x150 SE | 56 | 64 | 0.0011362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1031-25_0_3_line_59 | NAYY 4x150 SE | 58 | 59 | 0.0075874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1031-25_0_3_line_60 | NAYY 4x150 SE | 59 | 60 | 0.0075865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1031-25_0_3_line_61 | NAYY 4x150 SE | 60 | 61 | 0.0075874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1031-25_0_3_line_62 | NAYY 4x150 SE | 61 | 64 | 0.0079616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1031-25_0_3_line_63 | NAYY 4x150 SE | 62 | 63 | 0.0082832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1031-25_0_3_trafo_8 | 0.25 MVA 20/0.4 kV | 65 | 11 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2664827.0179 | 1223875.3504 | 2664857.0231 | 1223883.7825 | 2664860.3719 | 1223888.2219 | 2664861.1777 | 1223907.5208 | 2664881.6484 | 1223918.8141
1 | 2664827.0179 | 1223875.3504 | 2664834.6798 | 1223838.8772
2 | 2664834.6798 | 1223838.8772 | 2664842.3468 | 1223840.9175 | 2664916.4144 | 1223859.9532
3 | 2664916.4144 | 1223859.9532 | 2664926.6779 | 1223862.591
4 | 2664931.9831 | 1223863.9544 | 2664926.6779 | 1223862.591
5 | 2664923.3885 | 1224006.2396 | 2664913.1006 | 1224004.4623
6 | 2664962.7878 | 1223962.1185 | 2664923.3885 | 1224006.2396
7 | 2664937.2912 | 1223865.3186 | 2664931.9831 | 1223863.9544
8 | 2664962.7878 | 1223962.1185 | 2664964.6929 | 1223954.6587
9 | 2664966.5987 | 1223947.1961 | 2664964.6929 | 1223954.6587
10 | 2664983.6898 | 1223924.7896 | 2664983.5354 | 1223925.3943
11 | 2664980.2359 | 1223938.3162 | 2664983.5354 | 1223925.3943
12 | 2664978.4342 | 1223923.4537 | 2664983.6898 | 1223924.7896
13 | 2664980.2359 | 1223938.3162 | 2664990.2503 | 1223940.9337
14 | 2664980.2359 | 1223938.3162 | 2664976.5548 | 1223952.7293
15 | 2664978.4342 | 1223923.4537 | 2664973.0122 | 1223922.0825
16 | 2664978.4342 | 1223923.4537 | 2664980.8474 | 1223914.0073
17 | 2664990.2503 | 1223940.9337 | 2664991.0908 | 1223941.1534
18 | 2664974.445 | 1223960.99 | 2664976.5548 | 1223952.7293
19 | 2664973.0122 | 1223922.0825 | 2664972.3162 | 1223924.808
20 | 2664980.8474 | 1223914.0073 | 2664980.8855 | 1223913.858
21 | 2665011.1771 | 1223946.4035 | 2664991.0908 | 1223941.1534
22 | 2664972.3162 | 1223924.808 | 2664970.4107 | 1223932.2691
23 | 2665011.1771 | 1223946.4035 | 2665014.323 | 1223934.697
24 | 2665011.1771 | 1223946.4035 | 2665005.1308 | 1223976.5012
25 | 2664970.4107 | 1223932.2691 | 2664968.5049 | 1223939.7317
26 | 2665014.323 | 1223934.697 | 2665034.5927 | 1223939.9783
27 | 2665005.1308 | 1223976.5012 | 2664991.0785 | 1223976.4864
28 | 2665005.1308 | 1223976.5012 | 2665015.8353 | 1224045.4511
29 | 2664968.5049 | 1223939.7317 | 2664966.5987 | 1223947.1961
30 | 2665035.3981 | 1223940.1882 | 2665034.5927 | 1223939.9783
31 | 2665015.8353 | 1224045.4511 | 2665033.1215 | 1224043.456
32 | 2665015.8353 | 1224045.4511 | 2664984.0284 | 1224048.8501
33 | 2665044.3873 | 1223942.5303 | 2665035.3981 | 1223940.1882
34 | 2665027.089 | 1223887.1504 | 2665032.2773 | 1223888.6502
35 | 2665027.089 | 1223887.1504 | 2665004.932 | 1223881.8504
36 | 2665061.6646 | 1223897.1456 | 2665032.2773 | 1223888.6502
37 | 2664989.976 | 1223878.2729 | 2665004.932 | 1223881.8504
38 | 2664989.976 | 1223878.2729 | 2664979.3381 | 1223875.7293
39 | 2664961.4245 | 1223871.4459 | 2664979.3381 | 1223875.7293
40 | 2664961.4245 | 1223871.4459 | 2664957.1437 | 1223870.4208
41 | 2664961.4245 | 1223871.4459 | 2664955.0937 | 1223897.0599 | 2664950.063 | 1223895.9599
42 | 2664957.1437 | 1223870.4208 | 2664961.8774 | 1223855.663 | 2664962.9565 | 1223852.948
43 | 2664957.1437 | 1223870.4208 | 2664937.2912 | 1223865.3186
44 | 2664996.0944 | 1223815.1882 | 2664978.8111 | 1223827.8188 | 2664967.6941 | 1223841.0282 | 2664962.9565 | 1223852.948
45 | 2664996.0944 | 1223815.1882 | 2664984.4909 | 1223810.4474 | 2664984.2997 | 1223810.4115
46 | 2664996.0944 | 1223815.1882 | 2665002.1391 | 1223817.1888 | 2665003.0859 | 1223817.3873
47 | 2664984.2997 | 1223810.4115 | 2664954.6862 | 1223804.8504
48 | 2665003.0859 | 1223817.3873 | 2665016.807 | 1223820.2637
49 | 2665062.3438 | 1223897.2659 | 2665061.6646 | 1223897.1456
50 | 2665061.6646 | 1223897.1456 | 2665056.1856 | 1223920.1707
51 | 2665042.3216 | 1223825.6123 | 2665016.807 | 1223820.2637
52 | 2665056.1726 | 1223920.2253 | 2665056.1856 | 1223920.1707
53 | 2665044.3873 | 1223942.5303 | 2665047.3255 | 1223929.0204
54 | 2665044.3873 | 1223942.5303 | 2665041.5099 | 1223955.7656
55 | 2665053.7482 | 1223930.4137 | 2665056.1726 | 1223920.2253
56 | 2665053.7482 | 1223930.4137 | 2665058.6807 | 1223931.4794
57 | 2665053.7482 | 1223930.4137 | 2665047.3255 | 1223929.0204
58 | 2665058.6807 | 1223931.4794 | 2665058.4393 | 1223932.5896
59 | 2665051.9116 | 1223962.6111 | 2665053.5237 | 1223955.1969
60 | 2665055.1356 | 1223947.7836 | 2665053.5237 | 1223955.1969
61 | 2665056.7477 | 1223940.3695 | 2665055.1356 | 1223947.7836
62 | 2665058.4393 | 1223932.5896 | 2665056.7477 | 1223940.3695
63 | 2665039.7502 | 1223963.8597 | 2665041.5099 | 1223955.7656

## bus_geodata
| x | y | coords
0 | 2664881.6484 | 1223918.8141
1 | 2664827.0179 | 1223875.3504
2 | 2664834.6798 | 1223838.8772
3 | 2664916.4144 | 1223859.9532
4 | 2664926.6779 | 1223862.591
5 | 2664913.1006 | 1224004.4623
6 | 2664923.3885 | 1224006.2396
7 | 2664931.9831 | 1223863.9544
8 | 2664962.7878 | 1223962.1185
9 | 2664964.6929 | 1223954.6587
10 | 2664983.5354 | 1223925.3943
11 | 2664983.6898 | 1223924.7896
12 | 2664980.2359 | 1223938.3162
13 | 2664978.4342 | 1223923.4537
14 | 2664990.2503 | 1223940.9337
15 | 2664976.5548 | 1223952.7293
16 | 2664973.0122 | 1223922.0825
17 | 2664980.8474 | 1223914.0073
18 | 2664991.0908 | 1223941.1534
19 | 2664974.445 | 1223960.99
20 | 2664972.3162 | 1223924.808
21 | 2664980.8855 | 1223913.858
22 | 2665011.1771 | 1223946.4035
23 | 2664970.4107 | 1223932.2691
24 | 2665014.323 | 1223934.697
25 | 2665005.1308 | 1223976.5012
26 | 2664966.5987 | 1223947.1961
27 | 2664968.5049 | 1223939.7317
28 | 2665034.5927 | 1223939.9783
29 | 2664991.0785 | 1223976.4864
30 | 2665015.8353 | 1224045.4511
31 | 2665035.3981 | 1223940.1882
32 | 2665027.089 | 1223887.1504
33 | 2665032.2773 | 1223888.6502
34 | 2665004.932 | 1223881.8504
35 | 2665033.1215 | 1224043.456
36 | 2664984.0284 | 1224048.8501
37 | 2664989.976 | 1223878.2729
38 | 2664979.3381 | 1223875.7293
39 | 2664961.4245 | 1223871.4459
40 | 2664957.1437 | 1223870.4208
41 | 2664950.063 | 1223895.9599
42 | 2664937.2912 | 1223865.3186
43 | 2664962.9565 | 1223852.948
44 | 2664996.0944 | 1223815.1882
45 | 2664984.2997 | 1223810.4115
46 | 2665003.0859 | 1223817.3873
47 | 2665061.6646 | 1223897.1456
48 | 2665016.807 | 1223820.2637
49 | 2665042.3216 | 1223825.6123
50 | 2664954.6862 | 1223804.8504
51 | 2665062.3438 | 1223897.2659
52 | 2665056.1856 | 1223920.1707
53 | 2665044.3873 | 1223942.5303
54 | 2665056.1726 | 1223920.2253
55 | 2665053.7482 | 1223930.4137
56 | 2665058.6807 | 1223931.4794
57 | 2665047.3255 | 1223929.0204
58 | 2665051.9116 | 1223962.6111
59 | 2665053.5237 | 1223955.1969
60 | 2665055.1356 | 1223947.7836
61 | 2665056.7477 | 1223940.3695
62 | 2665039.7502 | 1223963.8597
63 | 2665041.5099 | 1223955.7656
64 | 2665058.4393 | 1223932.5896
65 | 2664978.4342 | 1223923.4537

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97009 | -0.21088 | 0.015404 | 0.0038606
1 | 0.97189 | -0.19793 | 0 | 0
2 | 0.97273 | -0.19187 | 0 | 0
3 | 0.97464 | -0.17817 | 0.0061453 | 0.0015402
4 | 0.97498 | -0.17577 | 0.0024103 | 0.00060409
5 | 0.99613 | -0.027143 | 0.011064 | 0.0027729
6 | 0.99629 | -0.025982 | 0.0065346 | 0.0016377
7 | 0.97517 | -0.17439 | 0.0024109 | 0.00060424
8 | 0.99778 | -0.015528 | 0.0026801 | 0.00067169
9 | 0.998 | -0.013963 | 0.0026793 | 0.00067149
10 | 0.99992 | -0.000562 | 0.002376 | 0.00059549
11 | 1 | 0 | -0.23013 | -0.057864
12 | 0.9982 | -0.012436 | 0 | 0
13 | 0.99964 | -0.0024885 | 0 | 0
14 | 0.99691 | -0.02136 | 0.0030636 | 0.00076782
15 | 0.99807 | -0.01335 | 0.003066 | 0.0007684
16 | 0.99933 | -0.0046939 | 0.0057847 | 0.0014498
17 | 0.99955 | -0.0031206 | 0.0032099 | 0.00080449
18 | 0.9968 | -0.022097 | 0.0023803 | 0.00059656
19 | 0.99803 | -0.013612 | 0.0030666 | 0.00076856
20 | 0.99919 | -0.005641 | 0.002674 | 0.00067017
21 | 0.99955 | -0.0031256 | 0.0032807 | 0.00082221
22 | 0.99429 | -0.039501 | 0 | 0
23 | 0.99885 | -0.0080291 | 0.0026831 | 0.00067244
24 | 0.99303 | -0.048272 | 0 | 0
25 | 0.99327 | -0.046735 | 0 | 0
26 | 0.99826 | -0.012191 | 0.0026823 | 0.00067225
27 | 0.99854 | -0.010212 | 0.0026785 | 0.00067131
28 | 0.99086 | -0.063481 | 0.0035537 | 0.00089063
29 | 0.99303 | -0.048428 | 0.011909 | 0.0029846
30 | 0.99213 | -0.054792 | 0 | 0
31 | 0.99077 | -0.064072 | 0.0039041 | 0.00097847
32 | 0.98375 | -0.11337 | 0 | 0
33 | 0.98405 | -0.11124 | 0.0029862 | 0.0007484
34 | 0.9812 | -0.13142 | 0.0034165 | 0.00085625
35 | 0.99195 | -0.056047 | 0.0071141 | 0.001783
36 | 0.99193 | -0.05618 | 0.0042789 | 0.0010724
37 | 0.97955 | -0.1431 | 0 | 0
38 | 0.97838 | -0.15144 | 0.0065118 | 0.001632
39 | 0.97659 | -0.16427 | 0 | 0
40 | 0.97625 | -0.16668 | 0 | 0
41 | 0.97594 | -0.16893 | 0.014119 | 0.0035384
42 | 0.97538 | -0.17287 | 0.0024135 | 0.00060488
43 | 0.97561 | -0.17126 | 0.0024124 | 0.0006046
44 | 0.974 | -0.18279 | 0 | 0
45 | 0.9738 | -0.18422 | 0.0085506 | 0.002143
46 | 0.97389 | -0.18362 | 0.0049761 | 0.0012471
47 | 0.98583 | -0.098718 | 0 | 0
48 | 0.97377 | -0.18445 | 0.0021515 | 0.00053921
49 | 0.97364 | -0.18542 | 0.0035225 | 0.00088282
50 | 0.97371 | -0.18489 | 0.00211 | 0.0005288
51 | 0.98583 | -0.098751 | 0.0046109 | 0.0011556
52 | 0.98729 | -0.0885 | 0.0043993 | 0.0011026
53 | 0.98985 | -0.070487 | 0 | 0
54 | 0.98729 | -0.088474 | 0.0047891 | 0.0012003
55 | 0.988 | -0.08347 | 0 | 0
56 | 0.98782 | -0.084745 | 0.0066143 | 0.0016577
57 | 0.98857 | -0.079505 | 0.0098043 | 0.0024572
58 | 0.9874 | -0.087763 | 0.0035467 | 0.0008889
59 | 0.98744 | -0.087487 | 0.003545 | 0.00088846
60 | 0.98752 | -0.086937 | 0.003545 | 0.00088846
61 | 0.98763 | -0.086111 | 0.0035468 | 0.0008889
62 | 0.98966 | -0.071892 | 0.0038961 | 0.00097645
63 | 0.9897 | -0.071563 | 0.0039023 | 0.00097801
64 | 0.98779 | -0.084955 | 0.0038989 | 0.00097716
65 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.015404 | -0.0038606 | 0.015432 | 0.0038702 | 2.7668e-05 | 9.6591e-06 | 0.023628 | 0.023628 | 0.023628 | 0.97009 | -0.21088 | 0.97189 | -0.19793 | 8.7511
1 | -0.015432 | -0.0038702 | 0.015445 | 0.0038748 | 1.2983e-05 | 4.5314e-06 | 0.023628 | 0.023627 | 0.023628 | 0.97189 | -0.19793 | 0.97273 | -0.19187 | 8.751
2 | -0.015445 | -0.0038748 | 0.015474 | 0.003885 | 2.9403e-05 | 1.0259e-05 | 0.023627 | 0.023627 | 0.023627 | 0.97273 | -0.19187 | 0.97464 | -0.17817 | 8.7509
3 | -0.021619 | -0.0054252 | 0.021627 | 0.0054278 | 7.2051e-06 | 2.6391e-06 | 0.033009 | 0.033009 | 0.033009 | 0.97464 | -0.17817 | 0.97498 | -0.17577 | 12.2257
4 | -0.024037 | -0.0060319 | 0.024041 | 0.0060336 | 4.6006e-06 | 1.7011e-06 | 0.036688 | 0.036688 | 0.036688 | 0.97498 | -0.17577 | 0.97517 | -0.17439 | 13.5881
5 | -0.011064 | -0.0027729 | 0.011066 | 0.0027734 | 1.7795e-06 | 5.4849e-07 | 0.016527 | 0.016527 | 0.016527 | 0.99613 | -0.027143 | 0.99629 | -0.025982 | 6.1212
6 | -0.0176 | -0.0044111 | 0.017626 | 0.0044202 | 2.5505e-05 | 9.0383e-06 | 0.026287 | 0.026287 | 0.026287 | 0.99629 | -0.025982 | 0.99778 | -0.015528 | 9.7359
7 | -0.026452 | -0.0066379 | 0.026458 | 0.0066399 | 5.5727e-06 | 2.075e-06 | 0.040367 | 0.040367 | 0.040367 | 0.97517 | -0.17439 | 0.97538 | -0.17287 | 14.9507
8 | -0.020306 | -0.0050919 | 0.02031 | 0.0050935 | 4.406e-06 | 1.594e-06 | 0.030284 | 0.030284 | 0.030284 | 0.99778 | -0.015528 | 0.998 | -0.013963 | 11.2161
9 | -0.022989 | -0.0057649 | 0.022995 | 0.005767 | 5.6472e-06 | 2.0713e-06 | 0.034278 | 0.034278 | 0.034278 | 0.998 | -0.013963 | 0.99826 | -0.012191 | 12.6957
10 | -0.18327 | -0.046307 | 0.18328 | 0.046313 | 1.4496e-05 | 5.5589e-06 | 0.27286 | 0.27286 | 0.27286 | 0.99992 | -0.000562 | 1 | 0 | 50.529
11 | 0.18089 | 0.045712 | -0.18059 | -0.045596 | 0.00030181 | 0.00011573 | 0.26932 | 0.26932 | 0.26932 | 0.99992 | -0.000562 | 0.9982 | -0.012436 | 49.8742
12 | 0.046047 | 0.011552 | -0.046031 | -0.011546 | 1.5888e-05 | 6.0398e-06 | 0.068523 | 0.068523 | 0.068523 | 1 | 0 | 0.99964 | -0.0024885 | 25.3789
13 | 0.17445 | 0.044059 | -0.17424 | -0.043975 | 0.00021861 | 8.381e-05 | 0.26018 | 0.26018 | 0.26018 | 0.9982 | -0.012436 | 0.99691 | -0.02136 | 48.1811
14 | 0.0061334 | 0.001537 | -0.0061327 | -0.0015369 | 7.7598e-07 | 1.0402e-07 | 0.0091431 | 0.0091431 | 0.0091431 | 0.9982 | -0.012436 | 0.99807 | -0.01335 | 3.3863
15 | 0.03954 | 0.0099189 | -0.039528 | -0.0099143 | 1.2091e-05 | 4.577e-06 | 0.058861 | 0.058861 | 0.058861 | 0.99964 | -0.0024885 | 0.99933 | -0.0046939 | 21.8003
16 | 0.0064912 | 0.0016268 | -0.0064906 | -0.0016267 | 5.68e-07 | 9.0653e-08 | 0.0096624 | 0.0096624 | 0.0096624 | 0.99964 | -0.0024885 | 0.99955 | -0.0031206 | 3.5787
17 | 0.17117 | 0.043207 | -0.17115 | -0.0432 | 1.7709e-05 | 6.7884e-06 | 0.25561 | 0.25561 | 0.25561 | 0.99691 | -0.02136 | 0.9968 | -0.022097 | 47.3343
18 | 0.0030667 | 0.00076849 | -0.0030666 | -0.00076856 | 1.1121e-07 | -6.8643e-08 | 0.0045721 | 0.0045721 | 0.0045721 | 0.99807 | -0.01335 | 0.99803 | -0.013612 | 1.6934
19 | 0.033743 | 0.0084645 | -0.033739 | -0.0084629 | 4.4316e-06 | 1.6676e-06 | 0.050247 | 0.050247 | 0.050247 | 0.99933 | -0.0046939 | 0.99919 | -0.005641 | 18.6101
20 | 0.0032807 | 0.00082221 | -0.0032807 | -0.00082221 | 2.2947e-09 | -1.1383e-09 | 0.0048838 | 0.0048838 | 0.0048838 | 0.99955 | -0.0031206 | 0.99955 | -0.0031256 | 1.8088
21 | 0.16877 | 0.042604 | -0.16836 | -0.042446 | 0.00041151 | 0.00015773 | 0.25205 | 0.25205 | 0.25205 | 0.9968 | -0.022097 | 0.99429 | -0.039501 | 46.6763
22 | 0.031065 | 0.0077927 | -0.031055 | -0.0077888 | 1.0285e-05 | 3.855e-06 | 0.046265 | 0.046265 | 0.046265 | 0.99919 | -0.005641 | 0.99885 | -0.0080291 | 17.1352
23 | 0.14502 | 0.036593 | -0.14484 | -0.036524 | 0.00017829 | 6.8258e-05 | 0.21712 | 0.21712 | 0.21712 | 0.99429 | -0.039501 | 0.99303 | -0.048272 | 40.2069
24 | 0.023343 | 0.0058536 | -0.023319 | -0.005845 | 2.338e-05 | 8.5947e-06 | 0.034935 | 0.034935 | 0.034935 | 0.99429 | -0.039501 | 0.99327 | -0.046735 | 12.9388
25 | 0.028372 | 0.0071164 | -0.028363 | -0.0071132 | 8.5865e-06 | 3.2017e-06 | 0.042268 | 0.042268 | 0.042268 | 0.99885 | -0.0080291 | 0.99854 | -0.010212 | 15.6548
26 | 0.14484 | 0.036524 | -0.14453 | -0.036406 | 0.00030807 | 0.00011795 | 0.21712 | 0.21712 | 0.21712 | 0.99303 | -0.048272 | 0.99086 | -0.063481 | 40.207
27 | 0.011911 | 0.0029855 | -0.011909 | -0.0029846 | 2.7922e-06 | 8.9208e-07 | 0.017845 | 0.017845 | 0.017845 | 0.99327 | -0.046735 | 0.99303 | -0.048428 | 6.6091
28 | 0.011408 | 0.0028595 | -0.011395 | -0.0028555 | 1.2717e-05 | 3.9892e-06 | 0.01709 | 0.017091 | 0.017091 | 0.99327 | -0.046735 | 0.99213 | -0.054792 | 6.3299
29 | -0.025677 | -0.0064393 | 0.025684 | 0.0064419 | 7.0431e-06 | 2.6082e-06 | 0.038277 | 0.038276 | 0.038277 | 0.99826 | -0.012191 | 0.99854 | -0.010212 | 14.1765
30 | 0.14098 | 0.035516 | -0.14097 | -0.035511 | 1.1647e-05 | 4.4582e-06 | 0.21178 | 0.21178 | 0.21178 | 0.99086 | -0.063481 | 0.99077 | -0.064072 | 39.2187
31 | 0.0071154 | 0.0017832 | -0.0071141 | -0.001783 | 1.2366e-06 | 2.5096e-07 | 0.010672 | 0.010672 | 0.010672 | 0.99213 | -0.054792 | 0.99195 | -0.056047 | 3.9526
32 | 0.0042798 | 0.0010723 | -0.0042789 | -0.0010724 | 8.2241e-07 | -9.6683e-08 | 0.0064188 | 0.0064189 | 0.0064189 | 0.99213 | -0.054792 | 0.99193 | -0.05618 | 2.3774
33 | 0.13706 | 0.034533 | -0.13694 | -0.034486 | 0.00012289 | 4.7027e-05 | 0.20592 | 0.20592 | 0.20592 | 0.99077 | -0.064072 | 0.98985 | -0.070487 | 38.1329
34 | -0.077265 | -0.019453 | 0.077288 | 0.019462 | 2.3028e-05 | 8.7197e-06 | 0.1169 | 0.1169 | 0.1169 | 0.98375 | -0.11337 | 0.98405 | -0.11124 | 21.6486
35 | 0.077265 | 0.019453 | -0.077071 | -0.019379 | 0.00019428 | 7.4435e-05 | 0.1169 | 0.1169 | 0.1169 | 0.98375 | -0.11337 | 0.9812 | -0.13142 | 43.2973
36 | -0.080274 | -0.020211 | 0.080415 | 0.020264 | 0.0001407 | 5.3338e-05 | 0.12142 | 0.12142 | 0.12142 | 0.98405 | -0.11124 | 0.98583 | -0.098718 | 22.4848
37 | 0.073654 | 0.018523 | -0.073535 | -0.018477 | 0.00011977 | 4.5872e-05 | 0.11172 | 0.11172 | 0.11172 | 0.9812 | -0.13142 | 0.97955 | -0.1431 | 41.3784
38 | 0.073535 | 0.018477 | -0.073449 | -0.018444 | 8.519e-05 | 3.2628e-05 | 0.11172 | 0.11172 | 0.11172 | 0.97955 | -0.1431 | 0.97838 | -0.15144 | 41.3784
39 | 0.066938 | 0.016812 | -0.066818 | -0.016767 | 0.00011915 | 4.5596e-05 | 0.10182 | 0.10182 | 0.10182 | 0.97838 | -0.15144 | 0.97659 | -0.16427 | 37.7104
40 | 0.052691 | 0.013225 | -0.052673 | -0.013218 | 1.766e-05 | 6.7374e-06 | 0.080292 | 0.080292 | 0.080292 | 0.97659 | -0.16427 | 0.97625 | -0.16668 | 29.7376
41 | 0.014128 | 0.0035416 | -0.014119 | -0.0035384 | 9.1143e-06 | 3.1114e-06 | 0.021527 | 0.021527 | 0.021527 | 0.97659 | -0.16427 | 0.97594 | -0.16893 | 7.9728
42 | 0.023777 | 0.0059642 | -0.023762 | -0.0059587 | 1.5098e-05 | 5.5768e-06 | 0.036243 | 0.036243 | 0.036243 | 0.97625 | -0.16668 | 0.97561 | -0.17126 | 13.4233
43 | 0.028896 | 0.0072541 | -0.028871 | -0.0072448 | 2.4817e-05 | 9.2891e-06 | 0.044049 | 0.044049 | 0.044049 | 0.97625 | -0.16668 | 0.97538 | -0.17287 | 16.3143
44 | 0.021349 | 0.0053541 | -0.021315 | -0.0053416 | 3.4076e-05 | 1.2464e-05 | 0.032564 | 0.032564 | 0.032564 | 0.97561 | -0.17126 | 0.974 | -0.18279 | 12.0607
45 | 0.010663 | 0.0026721 | -0.010661 | -0.0026715 | 2.1078e-06 | 6.5228e-07 | 0.01629 | 0.01629 | 0.01629 | 0.974 | -0.18279 | 0.9738 | -0.18422 | 6.0333
46 | 0.010652 | 0.0026695 | -0.010651 | -0.0026691 | 1.2121e-06 | 3.7492e-07 | 0.016274 | 0.016274 | 0.016274 | 0.974 | -0.18279 | 0.97389 | -0.18362 | 6.0274
47 | 0.0021101 | 0.0005285 | -0.00211 | -0.0005288 | 1.9547e-07 | -2.9964e-07 | 0.0032243 | 0.0032244 | 0.0032244 | 0.9738 | -0.18422 | 0.97371 | -0.18489 | 1.1942
48 | 0.0056751 | 0.001422 | -0.0056744 | -0.0014219 | 6.5773e-07 | 7.855e-08 | 0.0086709 | 0.008671 | 0.008671 | 0.97389 | -0.18362 | 0.97377 | -0.18445 | 3.2115
49 | 0.0046109 | 0.0011556 | -0.0046109 | -0.0011556 | 2.0851e-08 | -7.7629e-10 | 0.0069597 | 0.0069597 | 0.0069597 | 0.98583 | -0.098718 | 0.98583 | -0.098751 | 2.5777
50 | -0.085026 | -0.021419 | 0.085148 | 0.021466 | 0.0001217 | 4.6204e-05 | 0.12838 | 0.12838 | 0.12838 | 0.98583 | -0.098718 | 0.98729 | -0.0885 | 23.7736
51 | 0.003523 | 0.00088268 | -0.0035225 | -0.00088282 | 4.7144e-07 | -1.4294e-07 | 0.0053834 | 0.0053835 | 0.0053835 | 0.97377 | -0.18445 | 0.97364 | -0.18542 | 1.9939
52 | -0.089547 | -0.022568 | 0.089547 | 0.022568 | 3.1924e-07 | 1.2135e-07 | 0.13501 | 0.13501 | 0.13501 | 0.98729 | -0.0885 | 0.98729 | -0.088474 | 25.0014
53 | 0.12914 | 0.032531 | -0.12898 | -0.032469 | 0.00016267 | 6.221e-05 | 0.19419 | 0.19419 | 0.19419 | 0.98985 | -0.070487 | 0.98857 | -0.079505 | 35.9616
54 | 0.0077997 | 0.0019547 | -0.0077986 | -0.0019544 | 1.1619e-06 | 2.7281e-07 | 0.011725 | 0.011725 | 0.011725 | 0.98985 | -0.070487 | 0.9897 | -0.071563 | 4.3426
55 | -0.094336 | -0.023769 | 0.094402 | 0.023794 | 6.6096e-05 | 2.5154e-05 | 0.14223 | 0.14223 | 0.14223 | 0.98729 | -0.088474 | 0.988 | -0.08347 | 26.3381
56 | 0.024706 | 0.0061926 | -0.024701 | -0.006191 | 4.3597e-06 | 1.6122e-06 | 0.037209 | 0.037209 | 0.037209 | 0.988 | -0.08347 | 0.98782 | -0.084745 | 13.7812
57 | -0.11911 | -0.029986 | 0.11917 | 0.030012 | 6.602e-05 | 2.5224e-05 | 0.17943 | 0.17943 | 0.17943 | 0.988 | -0.08347 | 0.98857 | -0.079505 | 33.2287
58 | 0.018087 | 0.0045333 | -0.018087 | -0.0045331 | 5.2629e-07 | 1.8788e-07 | 0.027246 | 0.027246 | 0.027246 | 0.98782 | -0.084745 | 0.98779 | -0.084955 | 10.091
59 | -0.0035467 | -0.0008889 | 0.0035469 | 0.00088885 | 1.3526e-07 | -4.503e-08 | 0.005345 | 0.0053449 | 0.005345 | 0.9874 | -0.087763 | 0.98744 | -0.087487 | 1.9796
60 | -0.0070919 | -0.0017773 | 0.0070924 | 0.0017774 | 5.4068e-07 | 1.109e-07 | 0.010687 | 0.010687 | 0.010687 | 0.98744 | -0.087487 | 0.98752 | -0.086937 | 3.9582
61 | -0.010637 | -0.0026659 | 0.010639 | 0.0026663 | 1.2164e-06 | 3.7076e-07 | 0.016029 | 0.016029 | 0.016029 | 0.98752 | -0.086937 | 0.98763 | -0.086111 | 5.9366
62 | -0.014185 | -0.0035552 | 0.014188 | 0.0035559 | 2.2693e-06 | 7.7091e-07 | 0.021372 | 0.021372 | 0.021372 | 0.98763 | -0.086111 | 0.98779 | -0.084955 | 7.9157
63 | -0.0038961 | -0.00097645 | 0.0038963 | 0.00097641 | 1.7737e-07 | -3.8218e-08 | 0.005858 | 0.005858 | 0.005858 | 0.98966 | -0.071892 | 0.9897 | -0.071563 | 2.1696

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23505 | 0.059098

## res_load
| p_mw | q_mvar
0 | 0.015404 | 0.0038606
1 | 0.0061453 | 0.0015402
2 | 0.0024103 | 0.00060409
3 | 0.011064 | 0.0027729
4 | 0.0065346 | 0.0016377
5 | 0.0024109 | 0.00060424
6 | 0.0026801 | 0.00067169
7 | 0.0026793 | 0.00067149
8 | 0.002376 | 0.00059549
9 | 0.0049236 | 0.001234
10 | 0.0030636 | 0.00076782
11 | 0.003066 | 0.0007684
12 | 0.0057847 | 0.0014498
13 | 0.0032099 | 0.00080449
14 | 0.0023803 | 0.00059656
15 | 0.0030666 | 0.00076856
16 | 0.002674 | 0.00067017
17 | 0.0032807 | 0.00082221
18 | 0.0026831 | 0.00067244
19 | 0.0026823 | 0.00067225
20 | 0.0026785 | 0.00067131
21 | 0.0035537 | 0.00089063
22 | 0.011909 | 0.0029846
23 | 0.0039041 | 0.00097847
24 | 0.0029862 | 0.0007484
25 | 0.0034165 | 0.00085625
26 | 0.0071141 | 0.001783
27 | 0.0042789 | 0.0010724
28 | 0.0065118 | 0.001632
29 | 0.014119 | 0.0035384
30 | 0.0024135 | 0.00060488
31 | 0.0024124 | 0.0006046
32 | 0.0085506 | 0.002143
33 | 0.0049761 | 0.0012471
34 | 0.0021515 | 0.00053921
35 | 0.0035225 | 0.00088282
36 | 0.00211 | 0.0005288
37 | 0.0046109 | 0.0011556
38 | 0.0043993 | 0.0011026
39 | 0.0047891 | 0.0012003
40 | 0.0066143 | 0.0016577
41 | 0.0098043 | 0.0024572
42 | 0.0035467 | 0.0008889
43 | 0.003545 | 0.00088846
44 | 0.003545 | 0.00088846
45 | 0.0035468 | 0.0008889
46 | 0.0038961 | 0.00097645
47 | 0.0039023 | 0.00097801
48 | 0.0038989 | 0.00097716

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1