## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1031-32_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1031-32_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1031-32_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1031-32_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1031-32_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1031-32_0_2_node_46 | 0.4 | n |  | TRUE
6 | bus_LV_1031-32_0_2_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_1031-32_0_2_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_1031-32_0_2_node_44 | 0.4 | n |  | TRUE
9 | bus_LV_1031-32_0_2_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_1031-32_0_2_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_1031-32_0_2_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_1031-32_0_2_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_1031-32_0_2_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1031-32_0_2_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1031-32_0_2_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1031-32_0_2_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1031-32_0_2_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1031-32_0_2_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1031-32_0_2_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1031-32_0_2_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1031-32_0_2_node_32 | 0.4 | n |  | TRUE
22 | bus_LV_1031-32_0_2_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1031-32_0_2_node_60 | 0.4 | n |  | TRUE
24 | bus_LV_1031-32_0_2_node_51 | 0.4 | n |  | TRUE
25 | bus_LV_1031-32_0_2_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_1031-32_0_2_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1031-32_0_2_node_58 | 0.4 | n |  | TRUE
28 | bus_LV_1031-32_0_2_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_1031-32_0_2_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_1031-32_0_2_node_56 | 0.4 | n |  | TRUE
31 | bus_LV_1031-32_0_2_node_50 | 0.4 | n |  | TRUE
32 | bus_LV_1031-32_0_2_node_59 | 0.4 | n |  | TRUE
33 | bus_LV_1031-32_0_2_node_57 | 0.4 | n |  | TRUE
34 | bus_LV_1031-32_0_2_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_1031-32_0_2_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_1031-32_0_2_node_63 | 0.4 | n |  | TRUE
37 | bus_LV_1031-32_0_2_node_62 | 0.4 | n |  | TRUE
38 | bus_LV_1031-32_0_2_node_45 | 0.4 | n |  | TRUE
39 | bus_LV_1031-32_0_2_node_47 | 0.4 | n |  | TRUE
40 | bus_LV_1031-32_0_2_node_48 | 0.4 | n |  | TRUE
41 | bus_LV_1031-32_0_2_node_49 | 0.4 | n |  | TRUE
42 | bus_LV_1031-32_0_2_node_52 | 0.4 | n |  | TRUE
43 | bus_LV_1031-32_0_2_node_65 | 0.4 | n |  | TRUE
44 | bus_LV_1031-32_0_2_node_64 | 0.4 | n |  | TRUE
45 | bus_LV_1031-32_0_2_node_54 | 0.4 | n |  | TRUE
46 | bus_LV_1031-32_0_2_node_53 | 0.4 | n |  | TRUE
47 | bus_LV_1031-32_0_2_node_55 | 0.4 | n |  | TRUE
48 | bus_MV_353_1_node_99 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1031-32_0_2_load_0 | 0 | 0.001062 | 0.00026617 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1031-32_0_2_load_1 | 1 | 0.00072681 | 0.00018216 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1031-32_0_2_load_2 | 2 | 0.00055221 | 0.0001384 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1031-32_0_2_load_3 | 3 | 0.00066238 | 0.00016601 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1031-32_0_2_load_46 | 5 | 0.00090372 | 0.00022649 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1031-32_0_2_load_14 | 7 | 0.0011018 | 0.00027613 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1031-32_0_2_load_44 | 8 | 0.00071233 | 0.00017853 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1031-32_0_2_load_18 | 10 | 0.0026721 | 0.0006697 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1031-32_0_2_load_15 | 11 | 0.0016288 | 0.00040821 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1031-32_0_2_load_5 | 12 | 0.001739 | 0.00043583 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1031-32_0_2_load_6 | 13 | 0.0027527 | 0.00068989 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1031-32_0_2_load_7 | 14 | 0.0021029 | 0.00052704 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1031-32_0_2_load_8 | 15 | 0.0022821 | 0.00057196 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1031-32_0_2_load_9 | 16 | 0.0012348 | 0.00030946 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1031-32_0_2_load_13 | 17 | 0.0053383 | 0.0013379 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1031-32_0_2_load_10 | 18 | 0.0025762 | 0.00064566 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1031-32_0_2_load_11 | 19 | 0.0026308 | 0.00065935 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1031-32_0_2_load_12 | 20 | 0.0013893 | 0.00034819 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1031-32_0_2_load_32 | 21 | 0.0015895 | 0.00039837 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1031-32_0_2_load_16 | 22 | 0.0015128 | 0.00037915 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1031-32_0_2_load_60 | 23 | 0.0046472 | 0.0011647 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1031-32_0_2_load_33 | 25 | 0.0011536 | 0.00028912 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1031-32_0_2_load_23 | 26 | 0.0033484 | 0.00083919 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1031-32_0_2_load_35 | 29 | 0.0023059 | 0.0005779 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1031-32_0_2_load_56 | 30 | 0.00099262 | 0.00024877 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1031-32_0_2_load_59 | 32 | 0.0025454 | 0.00063794 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1031-32_0_2_load_57 | 33 | 0.0027373 | 0.00068603 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1031-32_0_2_load_36 | 34 | 0.0023869 | 0.00059821 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1031-32_0_2_load_34 | 35 | 0.0013138 | 0.00032926 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1031-32_0_2_load_63 | 36 | 0.00096871 | 0.00024278 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1031-32_0_2_load_62 | 37 | 0.0037257 | 0.00093374 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1031-32_0_2_load_45 | 38 | 0.00087795 | 0.00022003 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1031-32_0_2_load_47 | 39 | 0.0011584 | 0.00029031 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1031-32_0_2_load_48 | 40 | 0.0014642 | 0.00036698 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1031-32_0_2_load_49 | 41 | 0.0011733 | 0.00029405 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1031-32_0_2_load_52 | 42 | 0.00063163 | 0.0001583 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1031-32_0_2_load_65 | 43 | 0.0020752 | 0.00052009 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1031-32_0_2_load_64 | 44 | 0.0070328 | 0.0017626 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1031-32_0_2_load_54 | 45 | 0.0016947 | 0.00042474 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1031-32_0_2_load_53 | 46 | 0.002192 | 0.00054937 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1031-32_0_2_load_55 | 47 | 0.0059299 | 0.0014862 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1031-32_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0043469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1031-32_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0086335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1031-32_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0069112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1031-32_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.014387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1031-32_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0038687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1031-32_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.05147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1031-32_0_2_line_6 | NAYY 4x150 SE | 4 | 7 | 0.021134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1031-32_0_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.0030148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1031-32_0_2_line_8 | NAYY 4x150 SE | 6 | 9 | 0.009551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1031-32_0_2_line_9 | NAYY 4x150 SE | 6 | 10 | 0.010883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1031-32_0_2_line_10 | NAYY 4x150 SE | 7 | 11 | 0.024048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1031-32_0_2_line_11 | NAYY 4x150 SE | 8 | 38 | 0.0047371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1031-32_0_2_line_12 | NAYY 4x150 SE | 9 | 21 | 0.03824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1031-32_0_2_line_13 | NAYY 4x150 SE | 9 | 20 | 0.024068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1031-32_0_2_line_14 | NAYY 4x150 SE | 10 | 16 | 0.0085564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1031-32_0_2_line_15 | NAYY 4x150 SE | 11 | 22 | 0.020593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1031-32_0_2_line_16 | NAYY 4x150 SE | 12 | 13 | 0.022323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1031-32_0_2_line_17 | NAYY 4x150 SE | 12 | 14 | 0.0026324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1031-32_0_2_line_18 | NAYY 4x150 SE | 13 | 15 | 0.0090793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1031-32_0_2_line_19 | NAYY 4x150 SE | 14 | 16 | 0.014931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1031-32_0_2_line_20 | NAYY 4x150 SE | 15 | 17 | 0.0068398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1031-32_0_2_line_21 | NAYY 4x150 SE | 18 | 19 | 0.013369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1031-32_0_2_line_22 | NAYY 4x150 SE | 19 | 20 | 0.024512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1031-32_0_2_line_23 | NAYY 4x150 SE | 21 | 25 | 0.027075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1031-32_0_2_line_24 | NAYY 4x150 SE | 22 | 23 | 0.028639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1031-32_0_2_line_25 | NAYY 4x150 SE | 23 | 24 | 0.024133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1031-32_0_2_line_26 | NAYY 4x150 SE | 24 | 30 | 0.012222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1031-32_0_2_line_27 | NAYY 4x150 SE | 24 | 31 | 0.046619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1031-32_0_2_line_28 | NAYY 4x150 SE | 25 | 35 | 0.021689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1031-32_0_2_line_29 | NAYY 4x150 SE | 26 | 27 | 0.029654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1031-32_0_2_line_30 | NAYY 4x150 SE | 26 | 28 | 0.076174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1031-32_0_2_line_31 | NAYY 4x150 SE | 27 | 32 | 0.018127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1031-32_0_2_line_32 | NAYY 4x150 SE | 27 | 33 | 0.055066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1031-32_0_2_line_33 | NAYY 4x150 SE | 28 | 29 | 0.03332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1031-32_0_2_line_34 | NAYY 4x150 SE | 29 | 34 | 0.010019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1031-32_0_2_line_35 | NAYY 4x150 SE | 30 | 45 | 0.013871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1031-32_0_2_line_36 | NAYY 4x150 SE | 31 | 42 | 0.1284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1031-32_0_2_line_37 | NAYY 4x150 SE | 31 | 40 | 0.026377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1031-32_0_2_line_38 | NAYY 4x150 SE | 33 | 35 | 0.023392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1031-32_0_2_line_39 | NAYY 4x150 SE | 36 | 37 | 0.0038071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1031-32_0_2_line_40 | NAYY 4x150 SE | 37 | 44 | 0.015653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1031-32_0_2_line_41 | NAYY 4x150 SE | 39 | 40 | 0.025106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1031-32_0_2_line_42 | NAYY 4x150 SE | 39 | 41 | 0.028693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1031-32_0_2_line_43 | NAYY 4x150 SE | 42 | 43 | 0.076264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1031-32_0_2_line_44 | NAYY 4x150 SE | 42 | 44 | 0.21926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1031-32_0_2_line_45 | NAYY 4x150 SE | 45 | 46 | 0.00040159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1031-32_0_2_line_46 | NAYY 4x150 SE | 46 | 47 | 0.019886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1031-32_0_2_trafo_15 | 0.25 MVA 20/0.4 kV | 48 | 11 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2665187.5819 | 1223770.8086 | 2665190.8744 | 1223767.9705
1 | 2665187.5819 | 1223770.8086 | 2665181.0424 | 1223776.4454
2 | 2665196.1094 | 1223763.4582 | 2665190.8744 | 1223767.9705
3 | 2665170.1453 | 1223785.8383 | 2665181.0424 | 1223776.4454
4 | 2665196.1094 | 1223763.4582 | 2665199.0397 | 1223760.9324
5 | 2665170.1453 | 1223785.8383 | 2665182.6708 | 1223804.7096 | 2665186.2865 | 1223813.844 | 2665189.2306 | 1223821.2921 | 2665192.8488 | 1223825.3454 | 2665198.3263 | 1223826.5061
6 | 2665170.1453 | 1223785.8383 | 2665153.2141 | 1223773.1893
7 | 2665201.3232 | 1223758.964 | 2665199.0397 | 1223760.9324
8 | 2665191.2115 | 1223832.899 | 2665198.3263 | 1223826.5061
9 | 2665198.3263 | 1223826.5061 | 2665203.2213 | 1223825.459 | 2665208.6572 | 1223823.2247
10 | 2665129.9012 | 1223767.2877 | 2665153.2141 | 1223773.1893 | 2665153.2141 | 1223773.1893
11 | 2665201.3232 | 1223758.964 | 2665204.9114 | 1223755.8712
12 | 2665191.2115 | 1223832.899 | 2665180.8888 | 1223822.0123 | 2665175.6245 | 1223818.697 | 2665168.425 | 1223816.2167 | 2665159.1101 | 1223814.9441
13 | 2665191.2115 | 1223832.899 | 2665206.7732 | 1223851.2599
14 | 2665216.5712 | 1223819.9719 | 2665208.6572 | 1223823.2247
15 | 2665129.9012 | 1223767.2877 | 2665123.7894 | 1223765.7405 | 2665109.7883 | 1223762.8917
16 | 2665232.2524 | 1223812.358 | 2665236.1136 | 1223809.1532 | 2665247.793 | 1223796.3832
17 | 2665232.2524 | 1223812.358 | 2665230.2268 | 1223814.0392
18 | 2665253.9362 | 1223789.6978 | 2665252.4233 | 1223791.3205 | 2665247.793 | 1223796.3832
19 | 2665230.2268 | 1223814.0392 | 2665229.4633 | 1223814.6728 | 2665216.5712 | 1223819.9719
20 | 2665258.6004 | 1223784.6951 | 2665253.9362 | 1223789.6978
21 | 2665234.2609 | 1223875.0974 | 2665230.1408 | 1223875.3191 | 2665224.7191 | 1223871.8464 | 2665222.804 | 1223869.7974
22 | 2665206.7732 | 1223851.2599 | 2665219.375 | 1223866.1286 | 2665222.804 | 1223869.7974
23 | 2665132.2844 | 1223811.2792 | 2665159.1101 | 1223814.9441
24 | 2665081.7244 | 1223757.1815 | 2665109.7883 | 1223762.8917
25 | 2665058.2032 | 1223751.7925 | 2665075.9171 | 1223755.9999 | 2665081.7244 | 1223757.1815
26 | 2665058.2032 | 1223751.7925 | 2665049.2805 | 1223749.4602 | 2665046.3878 | 1223748.6676
27 | 2665081.4703 | 1223711.4098 | 2665076.4099 | 1223719.2484 | 2665067.9484 | 1223732.9981 | 2665058.2032 | 1223751.7925
28 | 2665110.8183 | 1223808.1814 | 2665119.1476 | 1223809.4844 | 2665132.2844 | 1223811.2792
29 | 2665033.4449 | 1223795.4278 | 2665038.0648 | 1223824.72
30 | 2665038.0648 | 1223824.72 | 2665061.6646 | 1223897.1456
31 | 2665051.0037 | 1223795.086 | 2665041.2372 | 1223792.9446 | 2665033.4449 | 1223795.4278
32 | 2665033.4449 | 1223795.4278 | 2665039.533 | 1223796.9286 | 2665050.3219 | 1223799.1812 | 2665067.799 | 1223801.4513 | 2665087.7074 | 1223804.5658
33 | 2665061.6646 | 1223897.1456 | 2665073.2366 | 1223899.1955 | 2665088.4786 | 1223900.5741 | 2665094.7241 | 1223900.1018
34 | 2665094.7241 | 1223900.1018 | 2665104.7143 | 1223899.3463
35 | 2665046.3878 | 1223748.6676 | 2665033.0094 | 1223745.0017
36 | 2665081.4703 | 1223711.4098 | 2665089.6323 | 1223700.7811 | 2665094.1206 | 1223694.6373 | 2665097.2365 | 1223691.247 | 2665099.8184 | 1223688.8403 | 2665101.9825 | 1223687.8856 | 2665106.4107 | 1223687.2336 | 2665112.3318 | 1223688.0544 | 2665123.2353 | 1223690.2528 | 2665129.9715 | 1223690.7379 | 2665137.8908 | 1223689.8351 | 2665152.362 | 1223684.779 | 2665159.7138 | 1223682.369 | 2665167.2268 | 1223681.1727 | 2665174.5596 | 1223680.508 | 2665189.3673 | 1223682.1156 | 2665196.8458 | 1223683.7497
37 | 2665081.4703 | 1223711.4098 | 2665094.8877 | 1223714.6363 | 2665107.1761 | 1223717.3169
38 | 2665110.8183 | 1223808.1814 | 2665087.7074 | 1223804.5658
39 | 2665094.4285 | 1223474.1325 | 2665091.4526 | 1223471.7579
40 | 2665106.6634 | 1223483.8952 | 2665094.4285 | 1223474.1325
41 | 2665131.715 | 1223722.6226 | 2665121.4491 | 1223720.4304 | 2665107.1761 | 1223717.3169
42 | 2665131.715 | 1223722.6226 | 2665156.0767 | 1223727.825 | 2665159.7904 | 1223728.5418
43 | 2665196.8458 | 1223683.7497 | 2665211.1702 | 1223686.8796 | 2665238.4255 | 1223693.0153 | 2665250.8339 | 1223696.2867 | 2665260.4894 | 1223696.1035 | 2665269.1088 | 1223694.2857 | 2665271.2875 | 1223693.364
44 | 2665196.8458 | 1223683.7497 | 2665106.6634 | 1223483.8952
45 | 2665032.6221 | 1223744.8956 | 2665033.0094 | 1223745.0017
46 | 2665013.4434 | 1223739.6404 | 2665032.6221 | 1223744.8956

## bus_geodata
| x | y | coords
0 | 2665187.5819 | 1223770.8086
1 | 2665190.8744 | 1223767.9705
2 | 2665181.0424 | 1223776.4454
3 | 2665196.1094 | 1223763.4582
4 | 2665170.1453 | 1223785.8383
5 | 2665199.0397 | 1223760.9324
6 | 2665198.3263 | 1223826.5061
7 | 2665153.2141 | 1223773.1893
8 | 2665201.3232 | 1223758.964
9 | 2665191.2115 | 1223832.899
10 | 2665208.6572 | 1223823.2247
11 | 2665129.9012 | 1223767.2877
12 | 2665232.2524 | 1223812.358
13 | 2665247.793 | 1223796.3832
14 | 2665230.2268 | 1223814.0392
15 | 2665253.9362 | 1223789.6978
16 | 2665216.5712 | 1223819.9719
17 | 2665258.6004 | 1223784.6951
18 | 2665234.2609 | 1223875.0974
19 | 2665222.804 | 1223869.7974
20 | 2665206.7732 | 1223851.2599
21 | 2665159.1101 | 1223814.9441
22 | 2665109.7883 | 1223762.8917
23 | 2665081.7244 | 1223757.1815
24 | 2665058.2032 | 1223751.7925
25 | 2665132.2844 | 1223811.2792
26 | 2665038.0648 | 1223824.72
27 | 2665033.4449 | 1223795.4278
28 | 2665061.6646 | 1223897.1456
29 | 2665094.7241 | 1223900.1018
30 | 2665046.3878 | 1223748.6676
31 | 2665081.4703 | 1223711.4098
32 | 2665051.0037 | 1223795.086
33 | 2665087.7074 | 1223804.5658
34 | 2665104.7143 | 1223899.3463
35 | 2665110.8183 | 1223808.1814
36 | 2665091.4526 | 1223471.7579
37 | 2665094.4285 | 1223474.1325
38 | 2665204.9114 | 1223755.8712
39 | 2665131.715 | 1223722.6226
40 | 2665107.1761 | 1223717.3169
41 | 2665159.7904 | 1223728.5418
42 | 2665196.8458 | 1223683.7497
43 | 2665271.2875 | 1223693.364
44 | 2665106.6634 | 1223483.8952
45 | 2665033.0094 | 1223745.0017
46 | 2665032.6221 | 1223744.8956
47 | 2665013.4434 | 1223739.6404
48 | 2665170.1453 | 1223785.8383

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9967 | -0.023046 | 0.001062 | 0.00026617
1 | 0.99667 | -0.023215 | 0.00072681 | 0.00018216
2 | 0.99676 | -0.022617 | 0.00055221 | 0.0001384
3 | 0.99664 | -0.023435 | 0.00066238 | 0.00016601
4 | 0.99687 | -0.021822 | 0 | 0
5 | 0.99663 | -0.023532 | 0.00090372 | 0.00022649
6 | 0.99376 | -0.043677 | 0 | 0
7 | 0.99832 | -0.011722 | 0.0011018 | 0.00027613
8 | 0.99662 | -0.02358 | 0.00071233 | 0.00017853
9 | 0.99343 | -0.045996 | 0 | 0
10 | 0.99348 | -0.045671 | 0.0026721 | 0.0006697
11 | 1 | 0 | -0.085273 | -0.021231
12 | 0.99294 | -0.04948 | 0.001739 | 0.00043583
13 | 0.9926 | -0.051825 | 0.0027527 | 0.00068989
14 | 0.99298 | -0.049157 | 0.0021029 | 0.00052704
15 | 0.9925 | -0.052526 | 0.0022821 | 0.00057196
16 | 0.99329 | -0.047009 | 0.0012348 | 0.00030946
17 | 0.99245 | -0.052896 | 0.0053383 | 0.0013379
18 | 0.99297 | -0.049244 | 0.0025762 | 0.00064566
19 | 0.99302 | -0.048895 | 0.0026308 | 0.00065935
20 | 0.9932 | -0.047603 | 0.0013893 | 0.00034819
21 | 0.99247 | -0.052735 | 0.0015895 | 0.00039837
22 | 0.99896 | -0.0072552 | 0.0015128 | 0.00037915
23 | 0.99758 | -0.016935 | 0.0046472 | 0.0011647
24 | 0.99657 | -0.023985 | 0 | 0
25 | 0.99186 | -0.057077 | 0.0011536 | 0.00028912
26 | 0.98977 | -0.071849 | 0.0033484 | 0.00083919
27 | 0.99011 | -0.069417 | 0 | 0
28 | 0.98925 | -0.075499 | 0 | 0
29 | 0.98903 | -0.077095 | 0.0023059 | 0.0005779
30 | 0.99638 | -0.025314 | 0.00099262 | 0.00024877
31 | 0.99535 | -0.032561 | 0 | 0
32 | 0.99005 | -0.069887 | 0.0025454 | 0.00063794
33 | 0.99095 | -0.063476 | 0.0027373 | 0.00068603
34 | 0.98899 | -0.077339 | 0.0023869 | 0.00059821
35 | 0.9914 | -0.060305 | 0.0013138 | 0.00032926
36 | 0.98886 | -0.078283 | 0.00096871 | 0.00024278
37 | 0.98887 | -0.078246 | 0.0037257 | 0.00093374
38 | 0.99662 | -0.023622 | 0.00087795 | 0.00022003
39 | 0.99512 | -0.034162 | 0.0011584 | 0.00029031
40 | 0.9952 | -0.033571 | 0.0014642 | 0.00036698
41 | 0.99507 | -0.034502 | 0.0011733 | 0.00029405
42 | 0.99268 | -0.051328 | 0.00063163 | 0.0001583
43 | 0.99245 | -0.052934 | 0.0020752 | 0.00052009
44 | 0.98897 | -0.077496 | 0.0070328 | 0.0017626
45 | 0.99619 | -0.026683 | 0.0016947 | 0.00042474
46 | 0.99618 | -0.026716 | 0.002192 | 0.00054937
47 | 0.99601 | -0.027902 | 0.0059299 | 0.0014862
48 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0038834 | 0.00097301 | -0.0038833 | -0.00097303 | 9.1174e-08 | -2.1585e-08 | 0.0057976 | 0.0057977 | 0.0057977 | 0.9967 | -0.023046 | 0.99667 | -0.023215 | 2.1473
1 | -0.0049455 | -0.0012392 | 0.0049457 | 0.0012392 | 2.9367e-07 | 4.2366e-10 | 0.0073832 | 0.0073832 | 0.0073832 | 0.9967 | -0.023046 | 0.99676 | -0.022617 | 2.7345
2 | 0.0031565 | 0.00079088 | -0.0031564 | -0.00079093 | 9.5775e-08 | -5.3229e-08 | 0.0047125 | 0.0047126 | 0.0047126 | 0.99667 | -0.023215 | 0.99664 | -0.023435 | 1.7454
3 | -0.005498 | -0.0013776 | 0.0054986 | 0.0013776 | 6.0473e-07 | 4.5047e-08 | 0.0082075 | 0.0082075 | 0.0082075 | 0.99676 | -0.022617 | 0.99687 | -0.021822 | 3.0398
4 | 0.002494 | 0.00062492 | -0.002494 | -0.00062496 | 3.3472e-08 | -3.754e-08 | 0.0037236 | 0.0037236 | 0.0037236 | 0.99664 | -0.023435 | 0.99663 | -0.023532 | 1.3791
5 | 0.042308 | 0.010624 | -0.04218 | -0.010576 | 0.00012812 | 4.8608e-05 | 0.063159 | 0.06316 | 0.06316 | 0.99687 | -0.021822 | 0.99376 | -0.043677 | 23.3925
6 | -0.047806 | -0.012002 | 0.047873 | 0.012028 | 6.7169e-05 | 2.5558e-05 | 0.071367 | 0.071367 | 0.071367 | 0.99687 | -0.021822 | 0.99832 | -0.011722 | 26.4322
7 | 0.0015903 | 0.00039847 | -0.0015903 | -0.0003985 | 1.0605e-08 | -3.5206e-08 | 0.0023743 | 0.0023744 | 0.0023744 | 0.99663 | -0.023532 | 0.99662 | -0.02358 | 0.87939
8 | 0.024041 | 0.0060284 | -0.024033 | -0.0060256 | 7.7233e-06 | 2.8468e-06 | 0.035999 | 0.035999 | 0.035999 | 0.99376 | -0.043677 | 0.99343 | -0.045996 | 13.3328
9 | 0.018139 | 0.0045474 | -0.018134 | -0.0045456 | 5.0099e-06 | 1.7859e-06 | 0.027161 | 0.027161 | 0.027161 | 0.99376 | -0.043677 | 0.99348 | -0.045671 | 10.0597
10 | -0.048975 | -0.012304 | 0.049055 | 0.012334 | 7.9987e-05 | 3.0449e-05 | 0.073009 | 0.073009 | 0.073009 | 0.99832 | -0.011722 | 1 | 0 | 27.0404
11 | 0.00087795 | 0.00021997 | -0.00087795 | -0.00022003 | 5.0791e-09 | -5.9775e-08 | 0.0013108 | 0.0013108 | 0.0013108 | 0.99662 | -0.02358 | 0.99662 | -0.023622 | 0.48549
12 | 0.017434 | 0.0043722 | -0.017418 | -0.0043664 | 1.6273e-05 | 5.7643e-06 | 0.026115 | 0.026115 | 0.026115 | 0.99343 | -0.045996 | 0.99247 | -0.052735 | 9.6721
13 | 0.0065989 | 0.0016534 | -0.0065974 | -0.0016531 | 1.4672e-06 | 2.5277e-07 | 0.009884 | 0.0098841 | 0.0098841 | 0.99343 | -0.045996 | 0.9932 | -0.047603 | 3.6608
14 | 0.015462 | 0.0038759 | -0.015459 | -0.0038749 | 2.8636e-06 | 9.906e-07 | 0.023159 | 0.023159 | 0.023159 | 0.99348 | -0.045671 | 0.99329 | -0.047009 | 8.5774
15 | 0.035418 | 0.0088968 | -0.035382 | -0.0088834 | 3.57e-05 | 1.3461e-05 | 0.052709 | 0.052709 | 0.052709 | 1 | 0 | 0.99896 | -0.0072552 | 19.5219
16 | 0.010378 | 0.0026009 | -0.010374 | -0.0025999 | 3.3691e-06 | 1.0072e-06 | 0.015552 | 0.015552 | 0.015552 | 0.99294 | -0.04948 | 0.9926 | -0.051825 | 5.76
17 | -0.012117 | -0.0030368 | 0.012117 | 0.0030369 | 5.4158e-07 | 1.7425e-07 | 0.018158 | 0.018158 | 0.018158 | 0.99294 | -0.04948 | 0.99298 | -0.049157 | 6.7251
18 | 0.0076215 | 0.0019101 | -0.0076208 | -0.0019099 | 7.3957e-07 | 1.671e-07 | 0.011425 | 0.011425 | 0.011425 | 0.9926 | -0.051825 | 0.9925 | -0.052526 | 4.2316
19 | -0.01422 | -0.003564 | 0.014224 | 0.0035654 | 4.2306e-06 | 1.434e-06 | 0.021309 | 0.021309 | 0.021309 | 0.99298 | -0.049157 | 0.99329 | -0.047009 | 7.8923
20 | 0.0053386 | 0.0013379 | -0.0053383 | -0.0013379 | 2.7342e-07 | 1.6774e-08 | 0.0080039 | 0.008004 | 0.008004 | 0.9925 | -0.052526 | 0.99245 | -0.052896 | 2.9644
21 | -0.0025762 | -0.00064566 | 0.0025763 | 0.00064553 | 1.2433e-07 | -1.2512e-07 | 0.0038606 | 0.0038605 | 0.0038606 | 0.99297 | -0.049244 | 0.99302 | -0.048895 | 1.4298
22 | -0.0052072 | -0.0013049 | 0.0052081 | 0.0013049 | 9.3123e-07 | 4.0998e-08 | 0.0078028 | 0.0078026 | 0.0078028 | 0.99302 | -0.048895 | 0.9932 | -0.047603 | 2.8899
23 | 0.015828 | 0.0039681 | -0.015819 | -0.0039648 | 9.515e-06 | 3.31e-06 | 0.023732 | 0.023732 | 0.023732 | 0.99247 | -0.052735 | 0.99186 | -0.057077 | 8.7895
24 | 0.033869 | 0.0085042 | -0.033824 | -0.0084871 | 4.5495e-05 | 1.7124e-05 | 0.050456 | 0.050456 | 0.050456 | 0.99896 | -0.0072552 | 0.99758 | -0.016935 | 18.6874
25 | 0.029176 | 0.0073224 | -0.029148 | -0.0073117 | 2.8527e-05 | 1.0657e-05 | 0.043524 | 0.043524 | 0.043524 | 0.99758 | -0.016935 | 0.99657 | -0.023985 | 16.12
26 | 0.010814 | 0.0027103 | -0.010812 | -0.0027097 | 1.9884e-06 | 6.0555e-07 | 0.016147 | 0.016147 | 0.016147 | 0.99657 | -0.023985 | 0.99638 | -0.025314 | 5.9804
27 | 0.018334 | 0.0046014 | -0.018312 | -0.0045936 | 2.1804e-05 | 7.7793e-06 | 0.027377 | 0.027377 | 0.027377 | 0.99657 | -0.023985 | 0.99535 | -0.032561 | 10.1398
28 | 0.014665 | 0.0036756 | -0.014659 | -0.0036734 | 6.5512e-06 | 2.2399e-06 | 0.022001 | 0.022001 | 0.022001 | 0.99186 | -0.057077 | 0.9914 | -0.060305 | 8.1486
29 | -0.0080446 | -0.0020151 | 0.0080473 | 0.0020158 | 2.7064e-06 | 6.5969e-07 | 0.012094 | 0.012094 | 0.012094 | 0.98977 | -0.071849 | 0.99011 | -0.069417 | 4.4792
30 | 0.0046962 | 0.0011759 | -0.0046938 | -0.001176 | 2.3692e-06 | -6.7248e-08 | 0.0070599 | 0.0070602 | 0.0070602 | 0.98977 | -0.071849 | 0.98925 | -0.075499 | 2.6149
31 | 0.0025456 | 0.00063777 | -0.0025454 | -0.00063794 | 1.6555e-07 | -1.6945e-07 | 0.0038256 | 0.0038257 | 0.0038257 | 0.99011 | -0.069417 | 0.99005 | -0.069887 | 1.4169
32 | -0.010593 | -0.0026535 | 0.010602 | 0.0026562 | 8.708e-06 | 2.6404e-06 | 0.015919 | 0.015919 | 0.015919 | 0.99011 | -0.069417 | 0.99095 | -0.063476 | 5.8961
33 | 0.0046938 | 0.001176 | -0.0046928 | -0.001176 | 1.0364e-06 | -2.9067e-08 | 0.0070602 | 0.0070604 | 0.0070604 | 0.98925 | -0.075499 | 0.98903 | -0.077095 | 2.615
34 | 0.002387 | 0.00059811 | -0.0023869 | -0.00059821 | 8.0626e-08 | -9.7555e-08 | 0.0035912 | 0.0035912 | 0.0035912 | 0.98903 | -0.077095 | 0.98899 | -0.077339 | 1.3301
35 | 0.0098195 | 0.0024609 | -0.0098176 | -0.0024604 | 1.8614e-06 | 5.353e-07 | 0.014665 | 0.014665 | 0.014665 | 0.99638 | -0.025314 | 0.99619 | -0.026683 | 5.4313
36 | 0.014515 | 0.003643 | -0.014478 | -0.0036302 | 3.7735e-05 | 1.2849e-05 | 0.021702 | 0.021702 | 0.021702 | 0.99535 | -0.032561 | 0.99268 | -0.051328 | 8.0379
37 | 0.0037967 | 0.00095059 | -0.0037961 | -0.00095073 | 5.302e-07 | -1.3887e-07 | 0.0056756 | 0.0056757 | 0.0056757 | 0.99535 | -0.032561 | 0.9952 | -0.033571 | 2.1021
38 | -0.013339 | -0.0033422 | 0.013345 | 0.0033441 | 5.8558e-06 | 1.9507e-06 | 0.020029 | 0.020029 | 0.020029 | 0.99095 | -0.063476 | 0.9914 | -0.060305 | 7.4183
39 | -0.00096871 | -0.00024278 | 0.00096872 | 0.00024273 | 5.0479e-09 | -4.6899e-08 | 0.0014577 | 0.0014577 | 0.0014577 | 0.98886 | -0.078283 | 0.98887 | -0.078246 | 0.53989
40 | -0.0046944 | -0.0011765 | 0.0046949 | 0.0011765 | 4.8738e-07 | -1.3373e-08 | 0.007064 | 0.0070639 | 0.007064 | 0.98887 | -0.078246 | 0.98897 | -0.077496 | 2.6163
41 | -0.0023317 | -0.00058401 | 0.0023319 | 0.00058376 | 1.9042e-07 | -2.5295e-07 | 0.0034865 | 0.0034864 | 0.0034865 | 0.99512 | -0.034162 | 0.9952 | -0.033571 | 1.2913
42 | 0.0011733 | 0.0002937 | -0.0011733 | -0.00029405 | 5.5111e-08 | -3.5156e-07 | 0.0017544 | 0.0017545 | 0.0017545 | 0.99512 | -0.034162 | 0.99507 | -0.034502 | 0.64981
43 | 0.0020757 | 0.00051928 | -0.0020752 | -0.00052009 | 4.6065e-07 | -8.0853e-07 | 0.0031111 | 0.0031114 | 0.0031114 | 0.99268 | -0.051328 | 0.99245 | -0.052934 | 1.1524
44 | 0.01177 | 0.0029526 | -0.011728 | -0.002939 | 4.2598e-05 | 1.356e-05 | 0.017645 | 0.017646 | 0.017646 | 0.99268 | -0.051328 | 0.98897 | -0.077496 | 6.5354
45 | 0.0081229 | 0.0020357 | -0.0081228 | -0.0020356 | 3.6891e-08 | 8.9603e-09 | 0.012133 | 0.012133 | 0.012133 | 0.99619 | -0.026683 | 0.99618 | -0.026716 | 4.4938
46 | 0.0059308 | 0.0014863 | -0.0059299 | -0.0014862 | 9.7386e-07 | 1.1571e-07 | 0.008859 | 0.008859 | 0.008859 | 0.99618 | -0.026716 | 0.99601 | -0.027902 | 3.2811

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.086902 | 0.021639

## res_load
| p_mw | q_mvar
0 | 0.001062 | 0.00026617
1 | 0.00072681 | 0.00018216
2 | 0.00055221 | 0.0001384
3 | 0.00066238 | 0.00016601
4 | 0.00090372 | 0.00022649
5 | 0.0011018 | 0.00027613
6 | 0.00071233 | 0.00017853
7 | 0.0026721 | 0.0006697
8 | 0.0016288 | 0.00040821
9 | 0.001739 | 0.00043583
10 | 0.0027527 | 0.00068989
11 | 0.0021029 | 0.00052704
12 | 0.0022821 | 0.00057196
13 | 0.0012348 | 0.00030946
14 | 0.0053383 | 0.0013379
15 | 0.0025762 | 0.00064566
16 | 0.0026308 | 0.00065935
17 | 0.0013893 | 0.00034819
18 | 0.0015895 | 0.00039837
19 | 0.0015128 | 0.00037915
20 | 0.0046472 | 0.0011647
21 | 0.0011536 | 0.00028912
22 | 0.0033484 | 0.00083919
23 | 0.0023059 | 0.0005779
24 | 0.00099262 | 0.00024877
25 | 0.0025454 | 0.00063794
26 | 0.0027373 | 0.00068603
27 | 0.0023869 | 0.00059821
28 | 0.0013138 | 0.00032926
29 | 0.00096871 | 0.00024278
30 | 0.0037257 | 0.00093374
31 | 0.00087795 | 0.00022003
32 | 0.0011584 | 0.00029031
33 | 0.0014642 | 0.00036698
34 | 0.0011733 | 0.00029405
35 | 0.00063163 | 0.0001583
36 | 0.0020752 | 0.00052009
37 | 0.0070328 | 0.0017626
38 | 0.0016947 | 0.00042474
39 | 0.002192 | 0.00054937
40 | 0.0059299 | 0.0014862

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1