## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1032-2_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1032-2_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1032-2_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1032-2_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1032-2_0_3_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1032-2_0_3_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1032-2_0_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1032-2_0_3_node_47 | 0.4 | n |  | TRUE
8 | bus_LV_1032-2_0_3_node_44 | 0.4 | n |  | TRUE
9 | bus_LV_1032-2_0_3_node_111 | 0.4 | n |  | TRUE
10 | bus_LV_1032-2_0_3_node_28 | 0.4 | n |  | TRUE
11 | bus_LV_1032-2_0_3_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_1032-2_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1032-2_0_3_node_88 | 0.4 | n |  | TRUE
14 | bus_LV_1032-2_0_3_node_51 | 0.4 | n |  | TRUE
15 | bus_LV_1032-2_0_3_node_45 | 0.4 | n |  | TRUE
16 | bus_LV_1032-2_0_3_node_57 | 0.4 | n |  | TRUE
17 | bus_LV_1032-2_0_3_node_56 | 0.4 | n |  | TRUE
18 | bus_LV_1032-2_0_3_node_54 | 0.4 | n |  | TRUE
19 | bus_LV_1032-2_0_3_node_52 | 0.4 | n |  | TRUE
20 | bus_LV_1032-2_0_3_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_1032-2_0_3_node_99 | 0.4 | n |  | TRUE
22 | bus_LV_1032-2_0_3_node_86 | 0.4 | n |  | TRUE
23 | bus_LV_1032-2_0_3_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1032-2_0_3_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_1032-2_0_3_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_1032-2_0_3_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_1032-2_0_3_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_1032-2_0_3_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_1032-2_0_3_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1032-2_0_3_node_102 | 0.4 | n |  | TRUE
31 | bus_LV_1032-2_0_3_node_103 | 0.4 | n |  | TRUE
32 | bus_LV_1032-2_0_3_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_1032-2_0_3_node_113 | 0.4 | n |  | TRUE
34 | bus_LV_1032-2_0_3_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_1032-2_0_3_node_112 | 0.4 | n |  | TRUE
36 | bus_LV_1032-2_0_3_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_1032-2_0_3_node_123 | 0.4 | n |  | TRUE
38 | bus_LV_1032-2_0_3_node_18 | 0.4 | n |  | TRUE
39 | bus_LV_1032-2_0_3_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_1032-2_0_3_node_148 | 0.4 | n |  | TRUE
41 | bus_LV_1032-2_0_3_node_19 | 0.4 | n |  | TRUE
42 | bus_LV_1032-2_0_3_node_187 | 0.4 | n |  | TRUE
43 | bus_LV_1032-2_0_3_node_71 | 0.4 | n |  | TRUE
44 | bus_LV_1032-2_0_3_node_126 | 0.4 | n |  | TRUE
45 | bus_LV_1032-2_0_3_node_24 | 0.4 | n |  | TRUE
46 | bus_LV_1032-2_0_3_node_26 | 0.4 | n |  | TRUE
47 | bus_LV_1032-2_0_3_node_100 | 0.4 | n |  | TRUE
48 | bus_LV_1032-2_0_3_node_114 | 0.4 | n |  | TRUE
49 | bus_LV_1032-2_0_3_node_115 | 0.4 | n |  | TRUE
50 | bus_LV_1032-2_0_3_node_146 | 0.4 | n |  | TRUE
51 | bus_LV_1032-2_0_3_node_117 | 0.4 | n |  | TRUE
52 | bus_LV_1032-2_0_3_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_1032-2_0_3_node_119 | 0.4 | n |  | TRUE
54 | bus_LV_1032-2_0_3_node_101 | 0.4 | n |  | TRUE
55 | bus_LV_1032-2_0_3_node_129 | 0.4 | n |  | TRUE
56 | bus_LV_1032-2_0_3_node_147 | 0.4 | n |  | TRUE
57 | bus_LV_1032-2_0_3_node_121 | 0.4 | n |  | TRUE
58 | bus_LV_1032-2_0_3_node_95 | 0.4 | n |  | TRUE
59 | bus_LV_1032-2_0_3_node_120 | 0.4 | n |  | TRUE
60 | bus_LV_1032-2_0_3_node_97 | 0.4 | n |  | TRUE
61 | bus_LV_1032-2_0_3_node_70 | 0.4 | n |  | TRUE
62 | bus_LV_1032-2_0_3_node_128 | 0.4 | n |  | TRUE
63 | bus_LV_1032-2_0_3_node_116 | 0.4 | n |  | TRUE
64 | bus_LV_1032-2_0_3_node_145 | 0.4 | n |  | TRUE
65 | bus_LV_1032-2_0_3_node_31 | 0.4 | n |  | TRUE
66 | bus_LV_1032-2_0_3_node_127 | 0.4 | n |  | TRUE
67 | bus_LV_1032-2_0_3_node_136 | 0.4 | n |  | TRUE
68 | bus_LV_1032-2_0_3_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_1032-2_0_3_node_29 | 0.4 | n |  | TRUE
70 | bus_LV_1032-2_0_3_node_30 | 0.4 | n |  | TRUE
71 | bus_LV_1032-2_0_3_node_32 | 0.4 | n |  | TRUE
72 | bus_LV_1032-2_0_3_node_34 | 0.4 | n |  | TRUE
73 | bus_LV_1032-2_0_3_node_35 | 0.4 | n |  | TRUE
74 | bus_LV_1032-2_0_3_node_36 | 0.4 | n |  | TRUE
75 | bus_LV_1032-2_0_3_node_37 | 0.4 | n |  | TRUE
76 | bus_LV_1032-2_0_3_node_38 | 0.4 | n |  | TRUE
77 | bus_LV_1032-2_0_3_node_40 | 0.4 | n |  | TRUE
78 | bus_LV_1032-2_0_3_node_43 | 0.4 | n |  | TRUE
79 | bus_LV_1032-2_0_3_node_39 | 0.4 | n |  | TRUE
80 | bus_LV_1032-2_0_3_node_81 | 0.4 | n |  | TRUE
81 | bus_LV_1032-2_0_3_node_41 | 0.4 | n |  | TRUE
82 | bus_LV_1032-2_0_3_node_80 | 0.4 | n |  | TRUE
83 | bus_LV_1032-2_0_3_node_49 | 0.4 | n |  | TRUE
84 | bus_LV_1032-2_0_3_node_46 | 0.4 | n |  | TRUE
85 | bus_LV_1032-2_0_3_node_48 | 0.4 | n |  | TRUE
86 | bus_LV_1032-2_0_3_node_50 | 0.4 | n |  | TRUE
87 | bus_LV_1032-2_0_3_node_177 | 0.4 | n |  | TRUE
88 | bus_LV_1032-2_0_3_node_122 | 0.4 | n |  | TRUE
89 | bus_LV_1032-2_0_3_node_176 | 0.4 | n |  | TRUE
90 | bus_LV_1032-2_0_3_node_109 | 0.4 | n |  | TRUE
91 | bus_LV_1032-2_0_3_node_55 | 0.4 | n |  | TRUE
92 | bus_LV_1032-2_0_3_node_65 | 0.4 | n |  | TRUE
93 | bus_LV_1032-2_0_3_node_66 | 0.4 | n |  | TRUE
94 | bus_LV_1032-2_0_3_node_67 | 0.4 | n |  | TRUE
95 | bus_LV_1032-2_0_3_node_69 | 0.4 | n |  | TRUE
96 | bus_LV_1032-2_0_3_node_72 | 0.4 | n |  | TRUE
97 | bus_LV_1032-2_0_3_node_92 | 0.4 | n |  | TRUE
98 | bus_LV_1032-2_0_3_node_93 | 0.4 | n |  | TRUE
99 | bus_LV_1032-2_0_3_node_124 | 0.4 | n |  | TRUE
100 | bus_LV_1032-2_0_3_node_82 | 0.4 | n |  | TRUE
101 | bus_LV_1032-2_0_3_node_83 | 0.4 | n |  | TRUE
102 | bus_LV_1032-2_0_3_node_84 | 0.4 | n |  | TRUE
103 | bus_LV_1032-2_0_3_node_85 | 0.4 | n |  | TRUE
104 | bus_LV_1032-2_0_3_node_87 | 0.4 | n |  | TRUE
105 | bus_LV_1032-2_0_3_node_91 | 0.4 | n |  | TRUE
106 | bus_LV_1032-2_0_3_node_110 | 0.4 | n |  | TRUE
107 | bus_LV_1032-2_0_3_node_130 | 0.4 | n |  | TRUE
108 | bus_LV_1032-2_0_3_node_108 | 0.4 | n |  | TRUE
109 | bus_LV_1032-2_0_3_node_94 | 0.4 | n |  | TRUE
110 | bus_LV_1032-2_0_3_node_96 | 0.4 | n |  | TRUE
111 | bus_LV_1032-2_0_3_node_98 | 0.4 | n |  | TRUE
112 | bus_LV_1032-2_0_3_node_185 | 0.4 | n |  | TRUE
113 | bus_LV_1032-2_0_3_node_182 | 0.4 | n |  | TRUE
114 | bus_LV_1032-2_0_3_node_178 | 0.4 | n |  | TRUE
115 | bus_LV_1032-2_0_3_node_179 | 0.4 | n |  | TRUE
116 | bus_LV_1032-2_0_3_node_180 | 0.4 | n |  | TRUE
117 | bus_LV_1032-2_0_3_node_181 | 0.4 | n |  | TRUE
118 | bus_LV_1032-2_0_3_node_183 | 0.4 | n |  | TRUE
119 | bus_LV_1032-2_0_3_node_184 | 0.4 | n |  | TRUE
120 | bus_LV_1032-2_0_3_node_167 | 0.4 | n |  | TRUE
121 | bus_LV_1032-2_0_3_node_104 | 0.4 | n |  | TRUE
122 | bus_LV_1032-2_0_3_node_105 | 0.4 | n |  | TRUE
123 | bus_LV_1032-2_0_3_node_106 | 0.4 | n |  | TRUE
124 | bus_LV_1032-2_0_3_node_186 | 0.4 | n |  | TRUE
125 | bus_LV_1032-2_0_3_node_140 | 0.4 | n |  | TRUE
126 | bus_LV_1032-2_0_3_node_134 | 0.4 | n |  | TRUE
127 | bus_LV_1032-2_0_3_node_139 | 0.4 | n |  | TRUE
128 | bus_LV_1032-2_0_3_node_135 | 0.4 | n |  | TRUE
129 | bus_LV_1032-2_0_3_node_137 | 0.4 | n |  | TRUE
130 | bus_LV_1032-2_0_3_node_138 | 0.4 | n |  | TRUE
131 | bus_LV_1032-2_0_3_node_141 | 0.4 | n |  | TRUE
132 | bus_LV_1032-2_0_3_node_142 | 0.4 | n |  | TRUE
133 | bus_LV_1032-2_0_3_node_143 | 0.4 | n |  | TRUE
134 | bus_LV_1032-2_0_3_node_144 | 0.4 | n |  | TRUE
135 | bus_LV_1032-2_0_3_node_164 | 0.4 | n |  | TRUE
136 | bus_LV_1032-2_0_3_node_165 | 0.4 | n |  | TRUE
137 | bus_LV_1032-2_0_3_node_169 | 0.4 | n |  | TRUE
138 | bus_MV_353_1_node_173 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1032-2_0_3_load_0 | 0 | 0.0020631 | 0.00051707 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1032-2_0_3_load_1 | 1 | 0.0075113 | 0.0018825 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1032-2_0_3_load_47 | 7 | 0.00080195 | 0.00020099 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1032-2_0_3_load_44 | 8 | 0.0012989 | 0.00032554 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1032-2_0_3_load_111 | 9 | 0.00076168 | 0.00019089 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1032-2_0_3_load_11 | 11 | 0.002677 | 0.00067091 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1032-2_0_3_load_9 | 12 | 0.0042005 | 0.0010528 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1032-2_0_3_load_51 | 14 | 0.00078142 | 0.00019584 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1032-2_0_3_load_45 | 15 | 0.0010663 | 0.00026724 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1032-2_0_3_load_57 | 16 | 0.0017782 | 0.00044566 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1032-2_0_3_load_56 | 17 | 0.0011356 | 0.00028462 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1032-2_0_3_load_54 | 18 | 0.0015025 | 0.00037656 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1032-2_0_3_load_52 | 19 | 0.0022339 | 0.00055988 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1032-2_0_3_load_10 | 20 | 0.0014315 | 0.00035877 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1032-2_0_3_load_86 | 22 | 0.00061268 | 0.00015355 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1032-2_0_3_load_13 | 24 | 0.002936 | 0.00073582 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1032-2_0_3_load_102 | 30 | 0.0011501 | 0.00028824 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1032-2_0_3_load_103 | 31 | 0.00065386 | 0.00016387 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1032-2_0_3_load_113 | 33 | 0.0078072 | 0.0019567 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1032-2_0_3_load_112 | 35 | 0.0011732 | 0.00029403 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1032-2_0_3_load_123 | 37 | 0.0011738 | 0.00029418 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1032-2_0_3_load_148 | 40 | 0.0075781 | 0.0018992 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1032-2_0_3_load_187 | 42 | 0.001893 | 0.00047444 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1032-2_0_3_load_126 | 44 | 0.0015918 | 0.00039895 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1032-2_0_3_load_100 | 47 | 0.0010534 | 0.000264 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1032-2_0_3_load_115 | 49 | 0.0014966 | 0.00037508 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1032-2_0_3_load_146 | 50 | 0.0012994 | 0.00032566 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1032-2_0_3_load_117 | 51 | 0.00069241 | 0.00017353 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1032-2_0_3_load_33 | 52 | 0.00090088 | 0.00022578 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1032-2_0_3_load_119 | 53 | 0.0018949 | 0.00047491 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1032-2_0_3_load_101 | 54 | 0.0010538 | 0.00026411 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1032-2_0_3_load_129 | 55 | 0.0020874 | 0.00052315 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1032-2_0_3_load_147 | 56 | 0.0020439 | 0.00051224 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1032-2_0_3_load_120 | 59 | 0.0019316 | 0.00048411 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1032-2_0_3_load_97 | 60 | 0.00049283 | 0.00012351 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1032-2_0_3_load_128 | 62 | 0.0020975 | 0.00052567 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1032-2_0_3_load_116 | 63 | 0.00083667 | 0.00020969 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1032-2_0_3_load_145 | 64 | 0.0010185 | 0.00025525 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1032-2_0_3_load_127 | 66 | 0.0030428 | 0.00076259 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1032-2_0_3_load_29 | 69 | 0.0013826 | 0.00034651 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1032-2_0_3_load_32 | 71 | 0.0017888 | 0.00044831 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1032-2_0_3_load_34 | 72 | 0.001919 | 0.00048095 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1032-2_0_3_load_35 | 73 | 0.0012637 | 0.00031671 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1032-2_0_3_load_37 | 75 | 0.00074316 | 0.00018625 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1032-2_0_3_load_38 | 76 | 0.00074786 | 0.00018743 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1032-2_0_3_load_43 | 78 | 0.0021635 | 0.00054222 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1032-2_0_3_load_81 | 80 | 0.0031094 | 0.00077929 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1032-2_0_3_load_80 | 82 | 0.001915 | 0.00047993 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1032-2_0_3_load_48 | 85 | 0.00077704 | 0.00019475 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1032-2_0_3_load_50 | 86 | 0.00084328 | 0.00021135 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1032-2_0_3_load_177 | 87 | 0.0015626 | 0.00039163 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1032-2_0_3_load_122 | 88 | 0.00084365 | 0.00021144 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1032-2_0_3_load_176 | 89 | 0.0035178 | 0.00088163 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1032-2_0_3_load_109 | 90 | 0.0019539 | 0.0004897 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1032-2_0_3_load_55 | 91 | 0.00083354 | 0.00020891 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1032-2_0_3_load_65 | 92 | 0.0011315 | 0.00028358 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1032-2_0_3_load_66 | 93 | 0.00060599 | 0.00015188 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1032-2_0_3_load_67 | 94 | 0.00097148 | 0.00024348 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1032-2_0_3_load_69 | 95 | 0.00065334 | 0.00016374 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1032-2_0_3_load_92 | 97 | 0.0011854 | 0.00029709 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1032-2_0_3_load_93 | 98 | 0.0029541 | 0.00074037 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1032-2_0_3_load_124 | 99 | 0.0016079 | 0.00040299 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1032-2_0_3_load_82 | 100 | 0.00062263 | 0.00015605 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1032-2_0_3_load_83 | 101 | 0.00055601 | 0.00013935 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1032-2_0_3_load_84 | 102 | 0.0016425 | 0.00041165 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1032-2_0_3_load_85 | 103 | 0.0032283 | 0.00080909 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1032-2_0_3_load_87 | 104 | 0.00036581 | 9.1682e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1032-2_0_3_load_91 | 105 | 0.00030892 | 7.7421e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1032-2_0_3_load_110 | 106 | 0.0025511 | 0.00063936 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1032-2_0_3_load_130 | 107 | 0.0010812 | 0.00027098 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1032-2_0_3_load_108 | 108 | 0.00090274 | 0.00022625 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1032-2_0_3_load_98 | 111 | 0.00076532 | 0.00019181 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1032-2_0_3_load_178 | 114 | 0.00063381 | 0.00015885 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1032-2_0_3_load_179 | 115 | 0.0013206 | 0.00033097 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1032-2_0_3_load_181 | 117 | 0.0004593 | 0.00011511 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1032-2_0_3_load_183 | 118 | 0.0049662 | 0.0012447 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1032-2_0_3_load_184 | 119 | 0.0029142 | 0.00073037 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1032-2_0_3_load_167 | 120 | 0.00035222 | 8.8275e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1032-2_0_3_load_104 | 121 | 0.00079186 | 0.00019846 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1032-2_0_3_load_105 | 122 | 0.0012376 | 0.00031018 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1032-2_0_3_load_106 | 123 | 0.00090351 | 0.00022644 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1032-2_0_3_load_186 | 124 | 0.0015425 | 0.00038659 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1032-2_0_3_load_140 | 125 | 0.00069651 | 0.00017456 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1032-2_0_3_load_134 | 126 | 0.0053548 | 0.001342 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1032-2_0_3_load_139 | 127 | 0.0012884 | 0.00032289 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1032-2_0_3_load_135 | 128 | 0.0012608 | 0.00031599 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1032-2_0_3_load_137 | 129 | 0.0015252 | 0.00038226 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1032-2_0_3_load_138 | 130 | 0.0016315 | 0.00040888 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1032-2_0_3_load_141 | 131 | 0.0045065 | 0.0011294 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1032-2_0_3_load_143 | 133 | 0.0013767 | 0.00034504 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1032-2_0_3_load_144 | 134 | 0.0012601 | 0.00031581 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1032-2_0_3_load_164 | 135 | 0.0003808 | 9.5438e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1032-2_0_3_load_165 | 136 | 0.00038091 | 9.5465e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1032-2_0_3_load_169 | 137 | 0.00034357 | 8.6106e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 52 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1032-2_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.047432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1032-2_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.020534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1032-2_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.020123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1032-2_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.041824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1032-2_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.02567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1032-2_0_3_line_5 | NAYY 4x150 SE | 4 | 9 | 0.013923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1032-2_0_3_line_6 | NAYY 4x150 SE | 4 | 6 | 0.036114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1032-2_0_3_line_7 | NAYY 4x150 SE | 5 | 10 | 0.008068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1032-2_0_3_line_8 | NAYY 4x150 SE | 5 | 11 | 0.0029997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1032-2_0_3_line_9 | NAYY 4x150 SE | 6 | 7 | 0.01395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1032-2_0_3_line_10 | NAYY 4x150 SE | 6 | 8 | 0.0017917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1032-2_0_3_line_11 | NAYY 4x150 SE | 7 | 14 | 0.0022724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1032-2_0_3_line_12 | NAYY 4x150 SE | 8 | 15 | 0.0259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1032-2_0_3_line_13 | NAYY 4x150 SE | 10 | 18 | 0.00692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1032-2_0_3_line_14 | NAYY 4x150 SE | 10 | 19 | 0.013093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1032-2_0_3_line_15 | NAYY 4x150 SE | 11 | 20 | 0.023876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1032-2_0_3_line_16 | NAYY 4x150 SE | 12 | 13 | 0.01585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1032-2_0_3_line_17 | NAYY 4x150 SE | 13 | 21 | 0.012718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1032-2_0_3_line_18 | NAYY 4x150 SE | 13 | 22 | 0.048622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1032-2_0_3_line_19 | NAYY 4x150 SE | 14 | 89 | 0.013094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1032-2_0_3_line_20 | NAYY 4x150 SE | 15 | 84 | 0.0083895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1032-2_0_3_line_21 | NAYY 4x150 SE | 16 | 17 | 0.0052115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1032-2_0_3_line_22 | NAYY 4x150 SE | 17 | 68 | 0.0085872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1032-2_0_3_line_23 | NAYY 4x150 SE | 19 | 68 | 0.023137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1032-2_0_3_line_24 | NAYY 4x150 SE | 20 | 23 | 0.018744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1032-2_0_3_line_25 | NAYY 4x150 SE | 21 | 107 | 0.015678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1032-2_0_3_line_26 | NAYY 4x150 SE | 21 | 37 | 0.011947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1032-2_0_3_line_27 | NAYY 4x150 SE | 22 | 102 | 0.0022963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1032-2_0_3_line_28 | NAYY 4x150 SE | 23 | 24 | 0.027938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1032-2_0_3_line_29 | NAYY 4x150 SE | 23 | 25 | 0.012745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_1032-2_0_3_line_30 | NAYY 4x150 SE | 24 | 26 | 0.031632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1032-2_0_3_line_31 | NAYY 4x150 SE | 25 | 52 | 0.012262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_1032-2_0_3_line_32 | NAYY 4x150 SE | 25 | 53 | 0.021227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1032-2_0_3_line_33 | NAYY 4x150 SE | 26 | 36 | 0.019985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1032-2_0_3_line_34 | NAYY 4x150 SE | 26 | 37 | 0.013265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1032-2_0_3_line_35 | NAYY 4x150 SE | 27 | 28 | 0.026867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1032-2_0_3_line_36 | NAYY 4x150 SE | 27 | 29 | 0.012542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1032-2_0_3_line_37 | NAYY 4x150 SE | 28 | 30 | 0.020692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1032-2_0_3_line_38 | NAYY 4x150 SE | 28 | 31 | 0.010865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1032-2_0_3_line_39 | NAYY 4x150 SE | 29 | 48 | 0.02906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1032-2_0_3_line_40 | NAYY 4x150 SE | 29 | 49 | 0.033019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1032-2_0_3_line_41 | NAYY 4x150 SE | 29 | 35 | 0.01118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1032-2_0_3_line_42 | NAYY 4x150 SE | 30 | 55 | 0.0078514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1032-2_0_3_line_43 | NAYY 4x150 SE | 32 | 33 | 0.020369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1032-2_0_3_line_44 | NAYY 4x150 SE | 32 | 34 | 0.0070412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1032-2_0_3_line_45 | NAYY 4x150 SE | 32 | 35 | 0.0086205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1032-2_0_3_line_46 | NAYY 4x150 SE | 34 | 46 | 0.005811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1032-2_0_3_line_47 | NAYY 4x150 SE | 34 | 47 | 0.010009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1032-2_0_3_line_48 | NAYY 4x150 SE | 36 | 46 | 0.020369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1032-2_0_3_line_49 | NAYY 4x150 SE | 38 | 39 | 0.037152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1032-2_0_3_line_50 | NAYY 4x150 SE | 38 | 40 | 0.0065301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1032-2_0_3_line_51 | NAYY 4x150 SE | 39 | 44 | 0.022932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1032-2_0_3_line_52 | NAYY 4x150 SE | 39 | 45 | 0.020456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1032-2_0_3_line_53 | NAYY 4x150 SE | 40 | 56 | 0.046488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1032-2_0_3_line_54 | NAYY 4x150 SE | 41 | 42 | 0.015361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1032-2_0_3_line_55 | NAYY 4x150 SE | 41 | 43 | 0.022594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1032-2_0_3_line_56 | NAYY 4x150 SE | 43 | 57 | 0.012958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1032-2_0_3_line_57 | NAYY 4x150 SE | 43 | 58 | 0.014154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1032-2_0_3_line_58 | NAYY 4x150 SE | 43 | 59 | 0.016739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1032-2_0_3_line_59 | NAYY 4x150 SE | 44 | 62 | 0.0048977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1032-2_0_3_line_60 | NAYY 4x150 SE | 45 | 50 | 0.0090673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1032-2_0_3_line_61 | NAYY 4x150 SE | 45 | 51 | 0.01252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1032-2_0_3_line_62 | NAYY 4x150 SE | 46 | 54 | 0.0061161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1032-2_0_3_line_63 | NAYY 4x150 SE | 48 | 63 | 0.046337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1032-2_0_3_line_64 | NAYY 4x150 SE | 49 | 51 | 0.030895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1032-2_0_3_line_65 | NAYY 4x150 SE | 50 | 64 | 0.0063511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1032-2_0_3_line_66 | NAYY 4x150 SE | 52 | 65 | 0.020606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1032-2_0_3_line_67 | NAYY 4x150 SE | 53 | 59 | 0.021077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1032-2_0_3_line_68 | NAYY 4x150 SE | 56 | 134 | 0.013649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1032-2_0_3_line_69 | NAYY 4x150 SE | 57 | 99 | 0.0046064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1032-2_0_3_line_70 | NAYY 4x150 SE | 58 | 60 | 0.018586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1032-2_0_3_line_71 | NAYY 4x150 SE | 58 | 61 | 0.012131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1032-2_0_3_line_72 | NAYY 4x150 SE | 61 | 97 | 0.01934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1032-2_0_3_line_73 | NAYY 4x150 SE | 62 | 125 | 0.015137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1032-2_0_3_line_74 | NAYY 4x150 SE | 63 | 96 | 0.038888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1032-2_0_3_line_75 | NAYY 4x150 SE | 65 | 71 | 0.016835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1032-2_0_3_line_76 | NAYY 4x150 SE | 65 | 70 | 0.025739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1032-2_0_3_line_77 | NAYY 4x150 SE | 66 | 67 | 0.029303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1032-2_0_3_line_78 | NAYY 4x150 SE | 67 | 126 | 0.01473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1032-2_0_3_line_79 | NAYY 4x150 SE | 68 | 91 | 0.018278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1032-2_0_3_line_80 | NAYY 4x150 SE | 69 | 70 | 0.016249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1032-2_0_3_line_81 | NAYY 4x150 SE | 72 | 73 | 0.028217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1032-2_0_3_line_82 | NAYY 4x150 SE | 72 | 74 | 0.059915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1032-2_0_3_line_83 | NAYY 4x150 SE | 73 | 75 | 0.016379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1032-2_0_3_line_84 | NAYY 4x150 SE | 74 | 76 | 0.030165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1032-2_0_3_line_85 | NAYY 4x150 SE | 74 | 77 | 0.2232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1032-2_0_3_line_86 | NAYY 4x150 SE | 76 | 78 | 0.031522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1032-2_0_3_line_87 | NAYY 4x150 SE | 77 | 79 | 0.31557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1032-2_0_3_line_88 | NAYY 4x150 SE | 79 | 80 | 0.024393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1032-2_0_3_line_89 | NAYY 4x150 SE | 80 | 81 | 0.048591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1032-2_0_3_line_90 | NAYY 4x150 SE | 81 | 82 | 0.011714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1032-2_0_3_line_91 | NAYY 4x150 SE | 82 | 83 | 0.016205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1032-2_0_3_line_92 | NAYY 4x150 SE | 83 | 84 | 0.058321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1032-2_0_3_line_93 | NAYY 4x150 SE | 84 | 85 | 0.02089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1032-2_0_3_line_94 | NAYY 4x150 SE | 84 | 86 | 0.018124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1032-2_0_3_line_95 | NAYY 4x150 SE | 85 | 87 | 0.014399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1032-2_0_3_line_96 | NAYY 4x150 SE | 86 | 88 | 0.0093474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1032-2_0_3_line_97 | NAYY 4x150 SE | 88 | 90 | 0.02185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1032-2_0_3_line_98 | NAYY 4x150 SE | 92 | 93 | 0.0087043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1032-2_0_3_line_99 | NAYY 4x150 SE | 92 | 94 | 0.027281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1032-2_0_3_line_100 | NAYY 4x150 SE | 94 | 95 | 0.01576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1032-2_0_3_line_101 | NAYY 4x150 SE | 95 | 96 | 0.042905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1032-2_0_3_line_102 | NAYY 4x150 SE | 97 | 98 | 0.0058325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1032-2_0_3_line_103 | NAYY 4x150 SE | 98 | 109 | 0.16251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1032-2_0_3_line_104 | NAYY 4x150 SE | 99 | 124 | 0.012262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1032-2_0_3_line_105 | NAYY 4x150 SE | 100 | 101 | 0.0030192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1032-2_0_3_line_106 | NAYY 4x150 SE | 100 | 102 | 0.0098259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1032-2_0_3_line_107 | NAYY 4x150 SE | 101 | 103 | 0.0073656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1032-2_0_3_line_108 | NAYY 4x150 SE | 103 | 104 | 0.0054448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1032-2_0_3_line_109 | NAYY 4x150 SE | 104 | 105 | 0.0067302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1032-2_0_3_line_110 | NAYY 4x150 SE | 105 | 106 | 0.014082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1032-2_0_3_line_111 | NAYY 4x150 SE | 106 | 108 | 0.012672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1032-2_0_3_line_112 | NAYY 4x150 SE | 108 | 123 | 0.0094397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1032-2_0_3_line_113 | NAYY 4x150 SE | 109 | 110 | 0.18124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1032-2_0_3_line_114 | NAYY 4x150 SE | 110 | 111 | 0.13856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1032-2_0_3_line_115 | NAYY 4x150 SE | 111 | 112 | 0.058791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1032-2_0_3_line_116 | NAYY 4x150 SE | 111 | 113 | 0.37974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1032-2_0_3_line_117 | NAYY 4x150 SE | 112 | 120 | 0.22161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1032-2_0_3_line_118 | NAYY 4x150 SE | 113 | 117 | 0.043847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1032-2_0_3_line_119 | NAYY 4x150 SE | 114 | 115 | 0.040787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1032-2_0_3_line_120 | NAYY 4x150 SE | 114 | 116 | 0.01949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1032-2_0_3_line_121 | NAYY 4x150 SE | 115 | 117 | 0.0075291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_1032-2_0_3_line_122 | NAYY 4x150 SE | 116 | 118 | 0.029183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_1032-2_0_3_line_123 | NAYY 4x150 SE | 118 | 119 | 0.0077829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_1032-2_0_3_line_124 | NAYY 4x150 SE | 120 | 137 | 0.02593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_1032-2_0_3_line_125 | NAYY 4x150 SE | 120 | 136 | 0.02111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_1032-2_0_3_line_126 | NAYY 4x150 SE | 121 | 122 | 0.01937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_1032-2_0_3_line_127 | NAYY 4x150 SE | 121 | 123 | 0.014809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_1032-2_0_3_line_128 | NAYY 4x150 SE | 125 | 127 | 0.010522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_1032-2_0_3_line_129 | NAYY 4x150 SE | 126 | 128 | 0.012176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_1032-2_0_3_line_130 | NAYY 4x150 SE | 127 | 130 | 0.015644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_1032-2_0_3_line_131 | NAYY 4x150 SE | 128 | 129 | 0.0090436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_1032-2_0_3_line_132 | NAYY 4x150 SE | 129 | 130 | 0.010479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_1032-2_0_3_line_133 | NAYY 4x150 SE | 131 | 132 | 0.015978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_1032-2_0_3_line_134 | NAYY 4x150 SE | 132 | 133 | 0.060768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_1032-2_0_3_line_135 | NAYY 4x150 SE | 133 | 134 | 0.0019847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_1032-2_0_3_line_136 | NAYY 4x150 SE | 135 | 136 | 0.0090898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1032-2_0_3_trafo_33 | 0.25 MVA 20/0.4 kV | 138 | 52 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27
0 | 2665240.7039 | 1228876.2875 | 2665267.5788 | 1228856.436 | 2665278.8445 | 1228848.0905
1 | 2665222.571 | 1228885.6504 | 2665226.5911 | 1228884.5493 | 2665239.1021 | 1228877.4707 | 2665240.7039 | 1228876.2875
2 | 2665216.7132 | 1228866.3958 | 2665222.571 | 1228885.6504
3 | 2665222.571 | 1228885.6504 | 2665228.8024 | 1228905.3649 | 2665230.71 | 1228908.977 | 2665222.1404 | 1228918.0001 | 2665218.5326 | 1228920.8846
4 | 2665216.7132 | 1228866.3958 | 2665213.6216 | 1228860.9028 | 2665203.9567 | 1228851.6464 | 2665198.7313 | 1228848.6539
5 | 2665218.5326 | 1228920.8846 | 2665221.9425 | 1228934.3836
6 | 2665218.5326 | 1228920.8846 | 2665222.1404 | 1228918.0001 | 2665230.71 | 1228908.977 | 2665242.6011 | 1228923.8615
7 | 2665198.7313 | 1228848.6539 | 2665202.9362 | 1228841.7621
8 | 2665198.7313 | 1228848.6539 | 2665195.944 | 1228847.5451
9 | 2665242.6011 | 1228923.8615 | 2665252.2852 | 1228918.2307 | 2665254.1269 | 1228916.1917
10 | 2665242.6011 | 1228923.8615 | 2665243.9193 | 1228925.075
11 | 2665255.65 | 1228914.5054 | 2665254.1269 | 1228916.1917
12 | 2665262.9751 | 1228942.6165 | 2665243.9193 | 1228925.075
13 | 2665209.0526 | 1228845.0313 | 2665202.9362 | 1228841.7621
14 | 2665202.9362 | 1228841.7621 | 2665204.1783 | 1228839.73 | 2665208.2313 | 1228832.1806 | 2665208.8035 | 1228830.1153
15 | 2665172.7008 | 1228842.756 | 2665183.3812 | 1228843.7825 | 2665191.1724 | 1228845.6469 | 2665195.944 | 1228847.5451
16 | 2665177.8207 | 1228895.5554 | 2665190.2594 | 1228885.7324
17 | 2665177.8207 | 1228895.5554 | 2665165.4011 | 1228898.4545
18 | 2665177.8207 | 1228895.5554 | 2665173.471 | 1228912.2074 | 2665170.2271 | 1228931.6624 | 2665172.246 | 1228943.1747
19 | 2665264.4266 | 1228904.7885 | 2665255.65 | 1228914.5054
20 | 2665269.9773 | 1228947.1659 | 2665264.5186 | 1228944.0373 | 2665262.9751 | 1228942.6165
21 | 2665217.0319 | 1228802.7757 | 2665221.9339 | 1228801.0065
22 | 2665210.1554 | 1228807.3411 | 2665210.8146 | 1228805.9585 | 2665213.3428 | 1228804.1072 | 2665217.0319 | 1228802.7757
23 | 2665210.1554 | 1228807.3411 | 2665209.5273 | 1228808.6572 | 2665209.4839 | 1228812.6149 | 2665210.1446 | 1228819.3821 | 2665210.1878 | 1228825.1197 | 2665208.8035 | 1228830.1153
24 | 2665154.0868 | 1228840.5818 | 2665163.536 | 1228841.875 | 2665172.7008 | 1228842.756
25 | 2665165.4011 | 1228898.4545 | 2665164.2971 | 1228893.4169 | 2665162.0382 | 1228883.1411
26 | 2665165.4011 | 1228898.4545 | 2665153.5299 | 1228899.797
27 | 2665172.6426 | 1228945.4365 | 2665172.246 | 1228943.1747
28 | 2665154.0868 | 1228840.5818 | 2665153.537 | 1228862.4123 | 2665153.0267 | 1228868.4915
29 | 2665146.7679 | 1228846.0942 | 2665150.1285 | 1228845.7196 | 2665150.4101 | 1228840.0746 | 2665153.474 | 1228840.4973 | 2665154.0868 | 1228840.5818
30 | 2665140.9033 | 1228896.6073 | 2665147.4515 | 1228889.5077 | 2665150.6027 | 1228882.66 | 2665152.378 | 1228876.2197 | 2665153.0267 | 1228868.4915
31 | 2665146.7679 | 1228846.0942 | 2665134.58 | 1228847.4436
32 | 2665146.7679 | 1228846.0942 | 2665146.9603 | 1228832.6875 | 2665146.2062 | 1228824.9054
33 | 2665140.9033 | 1228896.6073 | 2665135.6555 | 1228899.8075 | 2665130.8083 | 1228901.0219 | 2665121.9501 | 1228901.8144
34 | 2665140.9033 | 1228896.6073 | 2665142.7596 | 1228897.9841 | 2665152.7627 | 1228899.8837 | 2665153.5299 | 1228899.797
35 | 2665073.9102 | 1228912.5624 | 2665048.8965 | 1228922.551
36 | 2665073.9102 | 1228912.5624 | 2665072.5671 | 1228909.2901 | 2665077.5443 | 1228907.2654 | 2665075.6004 | 1228904.1977
37 | 2665048.8965 | 1228922.551 | 2665051.5935 | 1228928.1174 | 2665054.1898 | 1228938.0412 | 2665054.5672 | 1228942.2731
38 | 2665048.8965 | 1228922.551 | 2665038.8473 | 1228926.6824
39 | 2665075.6004 | 1228904.1977 | 2665073.068 | 1228900.2119 | 2665051.9336 | 1228888.0284
40 | 2665075.6004 | 1228904.1977 | 2665044.9958 | 1228916.5911
41 | 2665075.6004 | 1228904.1977 | 2665086.0681 | 1228900.2703
42 | 2665051.4714 | 1228948.9741 | 2665053.9905 | 1228946.5668 | 2665054.6622 | 1228943.3387 | 2665054.5672 | 1228942.2731
43 | 2665094.3087 | 1228897.8204 | 2665100.9537 | 1228896.4144 | 2665114.4661 | 1228895.0924
44 | 2665094.3087 | 1228897.8204 | 2665095.1268 | 1228901.2983 | 2665095.9157 | 1228904.6758
45 | 2665094.3087 | 1228897.8204 | 2665090.3141 | 1228898.6773 | 2665086.0681 | 1228900.2703
46 | 2665095.9157 | 1228904.6758 | 2665099.4425 | 1228903.647 | 2665101.5887 | 1228903.4704
47 | 2665095.9157 | 1228904.6758 | 2665087.6689 | 1228907.0649 | 2665086.347 | 1228907.5931
48 | 2665101.5887 | 1228903.4704 | 2665121.9501 | 1228901.8144
49 | 2664967.1028 | 1228953.4441 | 2664969.7538 | 1228954.9074 | 2664971.7989 | 1228957.0422 | 2664978.4922 | 1228951.2004 | 2664984.0807 | 1228947.3144 | 2664988.2928 | 1228944.592 | 2664994.2587 | 1228941.533 | 2664996.5292 | 1228944.5264
50 | 2664967.1028 | 1228953.4441 | 2664966.0258 | 1228952.8542 | 2664960.8722 | 1228951.6083
51 | 2664996.5292 | 1228944.5264 | 2664997.5823 | 1228945.9166 | 2665004.9962 | 1228961.4966 | 2665007.4623 | 1228964.5616
52 | 2664996.5292 | 1228944.5264 | 2664994.2587 | 1228941.533 | 2665006.0801 | 1228936.5033 | 2665004.7558 | 1228932.8864
53 | 2664916.0913 | 1228963.8641 | 2664951.7258 | 1228953.1316 | 2664960.8722 | 1228951.6083
54 | 2665162.907 | 1228801.7865 | 2665148.028 | 1228805.7706
55 | 2665143.1922 | 1228787.2612 | 2665146.938 | 1228787.002 | 2665146.7152 | 1228792.8144 | 2665148.028 | 1228805.7706
56 | 2665130.2815 | 1228788.6318 | 2665135.6552 | 1228787.779 | 2665143.1922 | 1228787.2612
57 | 2665143.1922 | 1228787.2612 | 2665146.938 | 1228787.002 | 2665147.0973 | 1228782.8344 | 2665148.089 | 1228776.6857
58 | 2665143.1922 | 1228787.2612 | 2665142.9032 | 1228790.8159 | 2665144.1736 | 1228803.9269
59 | 2665010.5326 | 1228968.3775 | 2665007.4623 | 1228964.5616
60 | 2665004.7558 | 1228932.8864 | 2665004.5497 | 1228932.3394 | 2665004.0665 | 1228928.7206 | 2665004.6746 | 1228923.9273
61 | 2665004.7558 | 1228932.8864 | 2665016.36 | 1228928.1873
62 | 2665101.5887 | 1228903.4704 | 2665103.0052 | 1228908.3446 | 2665103.5621 | 1228909.2232
63 | 2665051.9336 | 1228888.0284 | 2665040.6699 | 1228880.845 | 2665038.2328 | 1228879.9178 | 2665022.8264 | 1228880.194 | 2665018.7025 | 1228879.7042 | 2665013.8896 | 1228877.7837 | 2665009.4514 | 1228874.326
64 | 2665016.36 | 1228928.1873 | 2665044.9958 | 1228916.5911
65 | 2665005.4874 | 1228917.6289 | 2665005.4511 | 1228917.8064 | 2665004.6746 | 1228923.9273
66 | 2665114.0884 | 1228847.5819 | 2665117.3633 | 1228848.1181 | 2665124.837 | 1228848.5223 | 2665134.58 | 1228847.4436
67 | 2665146.2062 | 1228824.9054 | 2665144.1736 | 1228803.9269
68 | 2664903.0218 | 1228967.8004 | 2664916.0913 | 1228963.8641
69 | 2665130.2815 | 1228788.6318 | 2665126.2967 | 1228789.2664 | 2665125.7602 | 1228789.463
70 | 2665148.089 | 1228776.6857 | 2665154.9977 | 1228777.5063 | 2665162.6371 | 1228778.0125 | 2665166.6011 | 1228777.7431
71 | 2665151.3763 | 1228765.0252 | 2665148.4304 | 1228774.5769 | 2665148.089 | 1228776.6857
72 | 2665151.3763 | 1228765.0252 | 2665155.4177 | 1228755.7634 | 2665160.3779 | 1228747.9738
73 | 2665010.5326 | 1228968.3775 | 2665015.962 | 1228975.1253 | 2665016.1651 | 1228978.0294 | 2665015.4601 | 1228981.524 | 2665015.4601 | 1228981.524
74 | 2664991.2689 | 1228843.5142 | 2665003.0286 | 1228851.7703 | 2665002.9324 | 1228860.575 | 2665004.1515 | 1228866.8813 | 2665007.3761 | 1228872.7092 | 2665009.4514 | 1228874.326
75 | 2665114.0884 | 1228847.5819 | 2665113.18 | 1228840.5896 | 2665110.7231 | 1228831.1187
76 | 2665114.0884 | 1228847.5819 | 2665107.7882 | 1228846.5567 | 2665093.9624 | 1228846.4054 | 2665088.3665 | 1228846.0995
77 | 2664974.8386 | 1229040.7966 | 2664954.2756 | 1229019.9201
78 | 2664974.8386 | 1229040.7966 | 2664983.9222 | 1229029.2015
79 | 2665210.1554 | 1228807.3411 | 2665204.5904 | 1228801.454 | 2665202.1089 | 1228799.7368 | 2665200.6281 | 1228799.3537 | 2665195.1421 | 1228800.7723
80 | 2665088.3665 | 1228846.0995 | 2665079.0148 | 1228845.5969 | 2665072.3891 | 1228843.7288
81 | 2665732.3459 | 1229067.8568 | 2665720.134 | 1229069.1116 | 2665714.494 | 1229065.2802 | 2665708.7992 | 1229058.1534
82 | 2665672.4585 | 1229010.5248 | 2665688.8561 | 1229031.5973 | 2665696.8451 | 1229042.2703 | 2665704.8761 | 1229053.2439 | 2665708.7992 | 1229058.1534
83 | 2665732.3459 | 1229067.8568 | 2665732.3459 | 1229067.8568 | 2665743.7771 | 1229063.2134 | 2665747.061 | 1229060.8593
84 | 2665672.4585 | 1229010.5248 | 2665684.5909 | 1229008.2461 | 2665702.0221 | 1229004.5398
85 | 2665559.4494 | 1229019.2509 | 2665566.5681 | 1229019.5406 | 2665560.3667 | 1229010.9556 | 2665553.0955 | 1229006.6282 | 2665544.1742 | 1229004.9066 | 2665535.2988 | 1229005.8872 | 2665533.958 | 1228998.9902 | 2665533.8227 | 1228992.7068 | 2665536.6422 | 1228987.8013 | 2665553.2326 | 1228975.6317 | 2665567.5692 | 1228965.8611 | 2665572.5313 | 1228963.8478 | 2665591.3706 | 1228981.3446 | 2665605.4525 | 1228985.0467 | 2665609.3191 | 1228993.7395 | 2665616.6511 | 1229000.1134 | 2665628.027 | 1229004.5973 | 2665647.1663 | 1229009.3115 | 2665672.4585 | 1229010.5248
86 | 2665702.0221 | 1229004.5398 | 2665715.8569 | 1229001.5981 | 2665725.1295 | 1228998.2761 | 2665731.3323 | 1228994.0104
87 | 2665413.4453 | 1228925.3382 | 2665417.0686 | 1228928.6247 | 2665418.3658 | 1228932.6193 | 2665417.1226 | 1228960.2236 | 2665419.2994 | 1228965.5177 | 2665425.3962 | 1228970.5547 | 2665437.7013 | 1228973.2362 | 2665467.178 | 1228974.2611 | 2665474.0087 | 1228972.5018 | 2665481.2903 | 1228967.6343 | 2665492.8778 | 1228958.4336 | 2665504.5828 | 1228950.9354 | 2665514.3848 | 1228949.0643 | 2665531.1214 | 1228948.3926 | 2665544.722 | 1228948.3312 | 2665559.4397 | 1228956.2208 | 2665572.5313 | 1228963.8478 | 2665567.5692 | 1228965.8611 | 2665553.2326 | 1228975.6317 | 2665536.6422 | 1228987.8013 | 2665533.8227 | 1228992.7068 | 2665533.958 | 1228998.9902 | 2665535.2988 | 1229005.8872 | 2665544.1742 | 1229004.9066 | 2665553.0955 | 1229006.6282 | 2665560.3667 | 1229010.9556 | 2665566.5681 | 1229019.5406 | 2665559.4494 | 1229019.2509
88 | 2665413.4453 | 1228925.3382 | 2665408.1807 | 1228923.8572 | 2665400.2533 | 1228923.3697 | 2665394.3447 | 1228925.3283 | 2665390.8029 | 1228928.5045
89 | 2665353.8753 | 1228960.0396 | 2665366.2234 | 1228950.5468 | 2665390.8029 | 1228928.5045
90 | 2665353.8753 | 1228960.0396 | 2665342.9619 | 1228955.7833
91 | 2665328.1348 | 1228949.2721 | 2665336.2746 | 1228953.1752 | 2665342.9619 | 1228955.7833
92 | 2665269.9773 | 1228947.1659 | 2665277.0791 | 1228949.0005 | 2665296.4425 | 1228949.9025 | 2665312.5194 | 1228950.6572 | 2665328.1348 | 1228949.2721
93 | 2665269.9773 | 1228947.1659 | 2665263.6064 | 1228948.4524 | 2665250.0411 | 1228953.2553
94 | 2665269.9773 | 1228947.1659 | 2665270.4908 | 1228965.2822
95 | 2665236.4677 | 1228958.061 | 2665250.0411 | 1228953.2553
96 | 2665270.4908 | 1228965.2822 | 2665270.7364 | 1228973.9472 | 2665270.7581 | 1228974.6258
97 | 2665271.4555 | 1228996.4647 | 2665270.7581 | 1228974.6258
98 | 2665066.1969 | 1228786.6995 | 2665058.5619 | 1228790.8795
99 | 2665035.1394 | 1228804.8374 | 2665037.5647 | 1228803.1494 | 2665049.4184 | 1228795.8853 | 2665058.5619 | 1228790.8795
100 | 2665022.3114 | 1228813.9765 | 2665023.3791 | 1228813.023 | 2665035.1394 | 1228804.8374
101 | 2664991.2689 | 1228843.5142 | 2664992.0477 | 1228842.2775 | 2665008.3363 | 1228826.4562 | 2665022.3114 | 1228813.9765
102 | 2665160.3779 | 1228747.9738 | 2665162.7649 | 1228744.2252 | 2665163.5832 | 1228743.1035
103 | 2665170.2025 | 1228595.1541 | 2665195.4442 | 1228661.9518 | 2665196.8629 | 1228670.7731 | 2665197.4254 | 1228682.3535 | 2665195.9636 | 1228689.9091 | 2665193.7881 | 1228698.98 | 2665187.5884 | 1228710.1972 | 2665163.5832 | 1228743.1035
104 | 2665114.2468 | 1228793.6818 | 2665125.7602 | 1228789.463
105 | 2665174.3398 | 1228955.1146 | 2665174.8613 | 1228958.0884
106 | 2665174.3398 | 1228955.1146 | 2665172.6426 | 1228945.4365
107 | 2665174.8613 | 1228958.0884 | 2665175.3043 | 1228960.6146 | 2665177.0835 | 1228965.0736
108 | 2665177.0835 | 1228965.0736 | 2665179.1013 | 1228970.1308
109 | 2665181.5955 | 1228976.3818 | 2665179.1013 | 1228970.1308
110 | 2665181.5955 | 1228976.3818 | 2665182.8479 | 1228979.5207 | 2665188.8659 | 1228988.3705
111 | 2665196.5794 | 1228998.3393 | 2665194.1293 | 1228996.1107 | 2665188.8659 | 1228988.3705
112 | 2665196.5794 | 1228998.3393 | 2665203.5623 | 1229004.6912
113 | 2665170.2025 | 1228595.1541 | 2665155.8419 | 1228563.5318 | 2665130.352 | 1228519.3128 | 2665122.1398 | 1228499.8103 | 2665119.2707 | 1228484.3466 | 2665119.2896 | 1228469.4705 | 2665127.3378 | 1228426.4639
114 | 2665127.3378 | 1228426.4639 | 2665137.5257 | 1228375.5979 | 2665143.0731 | 1228345.0832 | 2665144.9656 | 1228339.7227 | 2665150.7292 | 1228323.3751 | 2665158.7059 | 1228309.0643 | 2665171.1765 | 1228298.6243
115 | 2665216.5642 | 1228262.3233 | 2665210.6588 | 1228270.853 | 2665206.5356 | 1228274.399 | 2665200.3318 | 1228279.7345 | 2665175.9052 | 1228294.6655 | 2665171.1765 | 1228298.6243
116 | 2665171.1765 | 1228298.6243 | 2664796.4411 | 1228237.1619
117 | 2665216.5642 | 1228262.3233 | 2665437.5869 | 1228246.1947
118 | 2664796.4411 | 1228237.1619 | 2664775.3629 | 1228248.0729 | 2664765.0605 | 1228260.3243 | 2664762.3019 | 1228263.3646
119 | 2664750.846 | 1228305.6968 | 2664751.409 | 1228301.1022 | 2664749.6735 | 1228292.7779 | 2664746.6952 | 1228285.8521 | 2664752.3139 | 1228274.3724 | 2664757.2426 | 1228268.9404
120 | 2664758.5651 | 1228321.0041 | 2664753.4522 | 1228318.747 | 2664750.0701 | 1228312.028 | 2664750.846 | 1228305.6968
121 | 2664762.3019 | 1228263.3646 | 2664757.2426 | 1228268.9404
122 | 2664758.5651 | 1228321.0041 | 2664730.7802 | 1228329.9298
123 | 2664730.7802 | 1228329.9298 | 2664730.7802 | 1228329.9298 | 2664723.7293 | 1228333.2248
124 | 2665443.5891 | 1228221.0734 | 2665442.2334 | 1228231.603 | 2665437.5869 | 1228246.1947
125 | 2665437.5869 | 1228246.1947 | 2665437.5869 | 1228246.1947 | 2665438.4564 | 1228255.3213 | 2665441.1635 | 1228261.3439 | 2665445.1301 | 1228264.9175
126 | 2665214.5997 | 1229014.5601 | 2665229.627 | 1229026.7821
127 | 2665214.5997 | 1229014.5601 | 2665212.8235 | 1229013.1155 | 2665203.5623 | 1229004.6912
128 | 2665015.4601 | 1228981.524 | 2665010.1967 | 1228990.6351
129 | 2664983.9222 | 1229029.2015 | 2664991.4314 | 1229019.6162
130 | 2665003.4708 | 1229004.2479 | 2665007.9323 | 1228998.5528 | 2665008.4711 | 1228993.6221 | 2665010.1967 | 1228990.6351
131 | 2664997.0085 | 1229012.497 | 2664991.4314 | 1229019.6162
132 | 2665003.4708 | 1229004.2479 | 2664997.0085 | 1229012.497
133 | 2664851.1999 | 1228941.3163 | 2664851.7177 | 1228936.908 | 2664849.705 | 1228925.5453
134 | 2664851.1999 | 1228941.3163 | 2664857.1987 | 1228942.8716 | 2664875.8085 | 1228962.1648 | 2664892.8745 | 1228970.8566 | 2664901.1214 | 1228968.3728
135 | 2664903.0218 | 1228967.8004 | 2664901.1214 | 1228968.3728
136 | 2665451.8835 | 1228271.0017 | 2665445.1301 | 1228264.9175

## bus_geodata
| x | y | coords
0 | 2665240.7039 | 1228876.2875
1 | 2665278.8445 | 1228848.0905
2 | 2665222.571 | 1228885.6504
3 | 2665216.7132 | 1228866.3958
4 | 2665218.5326 | 1228920.8846
5 | 2665198.7313 | 1228848.6539
6 | 2665242.6011 | 1228923.8615
7 | 2665254.1269 | 1228916.1917
8 | 2665243.9193 | 1228925.075
9 | 2665221.9425 | 1228934.3836
10 | 2665202.9362 | 1228841.7621
11 | 2665195.944 | 1228847.5451
12 | 2665190.2594 | 1228885.7324
13 | 2665177.8207 | 1228895.5554
14 | 2665255.65 | 1228914.5054
15 | 2665262.9751 | 1228942.6165
16 | 2665221.9339 | 1228801.0065
17 | 2665217.0319 | 1228802.7757
18 | 2665209.0526 | 1228845.0313
19 | 2665208.8035 | 1228830.1153
20 | 2665172.7008 | 1228842.756
21 | 2665165.4011 | 1228898.4545
22 | 2665172.246 | 1228943.1747
23 | 2665154.0868 | 1228840.5818
24 | 2665153.0267 | 1228868.4915
25 | 2665146.7679 | 1228846.0942
26 | 2665140.9033 | 1228896.6073
27 | 2665073.9102 | 1228912.5624
28 | 2665048.8965 | 1228922.551
29 | 2665075.6004 | 1228904.1977
30 | 2665054.5672 | 1228942.2731
31 | 2665038.8473 | 1228926.6824
32 | 2665094.3087 | 1228897.8204
33 | 2665114.4661 | 1228895.0924
34 | 2665095.9157 | 1228904.6758
35 | 2665086.0681 | 1228900.2703
36 | 2665121.9501 | 1228901.8144
37 | 2665153.5299 | 1228899.797
38 | 2664967.1028 | 1228953.4441
39 | 2664996.5292 | 1228944.5264
40 | 2664960.8722 | 1228951.6083
41 | 2665148.028 | 1228805.7706
42 | 2665162.907 | 1228801.7865
43 | 2665143.1922 | 1228787.2612
44 | 2665007.4623 | 1228964.5616
45 | 2665004.7558 | 1228932.8864
46 | 2665101.5887 | 1228903.4704
47 | 2665086.347 | 1228907.5931
48 | 2665051.9336 | 1228888.0284
49 | 2665044.9958 | 1228916.5911
50 | 2665004.6746 | 1228923.9273
51 | 2665016.36 | 1228928.1873
52 | 2665134.58 | 1228847.4436
53 | 2665146.2062 | 1228824.9054
54 | 2665103.5621 | 1228909.2232
55 | 2665051.4714 | 1228948.9741
56 | 2664916.0913 | 1228963.8641
57 | 2665130.2815 | 1228788.6318
58 | 2665148.089 | 1228776.6857
59 | 2665144.1736 | 1228803.9269
60 | 2665166.6011 | 1228777.7431
61 | 2665151.3763 | 1228765.0252
62 | 2665010.5326 | 1228968.3775
63 | 2665009.4514 | 1228874.326
64 | 2665005.4874 | 1228917.6289
65 | 2665114.0884 | 1228847.5819
66 | 2664954.2756 | 1229019.92
67 | 2664974.8386 | 1229040.7966
68 | 2665210.1554 | 1228807.3411
69 | 2665072.3891 | 1228843.7288
70 | 2665088.3665 | 1228846.0995
71 | 2665110.7231 | 1228831.1187
72 | 2665708.7992 | 1229058.1534
73 | 2665732.3459 | 1229067.8568
74 | 2665672.4585 | 1229010.5248
75 | 2665747.061 | 1229060.8593
76 | 2665702.0221 | 1229004.5398
77 | 2665559.4494 | 1229019.2509
78 | 2665731.3323 | 1228994.0104
79 | 2665413.4453 | 1228925.3382
80 | 2665390.8029 | 1228928.5045
81 | 2665353.8753 | 1228960.0396
82 | 2665342.9619 | 1228955.7833
83 | 2665328.1348 | 1228949.2721
84 | 2665269.9773 | 1228947.1659
85 | 2665250.0411 | 1228953.2553
86 | 2665270.4908 | 1228965.2822
87 | 2665236.4677 | 1228958.061
88 | 2665270.7581 | 1228974.6258
89 | 2665264.4266 | 1228904.7885
90 | 2665271.4555 | 1228996.4647
91 | 2665195.1421 | 1228800.7723
92 | 2665058.5619 | 1228790.8795
93 | 2665066.1969 | 1228786.6995
94 | 2665035.1394 | 1228804.8374
95 | 2665022.3114 | 1228813.9765
96 | 2664991.2689 | 1228843.5142
97 | 2665160.3779 | 1228747.9738
98 | 2665163.5832 | 1228743.1035
99 | 2665125.7602 | 1228789.463
100 | 2665174.3398 | 1228955.1146
101 | 2665174.8613 | 1228958.0884
102 | 2665172.6426 | 1228945.4365
103 | 2665177.0835 | 1228965.0736
104 | 2665179.1013 | 1228970.1308
105 | 2665181.5955 | 1228976.3818
106 | 2665188.8659 | 1228988.3705
107 | 2665162.0382 | 1228883.1411
108 | 2665196.5794 | 1228998.3393
109 | 2665170.2025 | 1228595.1541
110 | 2665127.3378 | 1228426.4639
111 | 2665171.1765 | 1228298.6243
112 | 2665216.5642 | 1228262.3233
113 | 2664796.4411 | 1228237.1619
114 | 2664750.846 | 1228305.6968
115 | 2664757.2426 | 1228268.9404
116 | 2664758.5651 | 1228321.0041
117 | 2664762.3019 | 1228263.3646
118 | 2664730.7803 | 1228329.9298
119 | 2664723.7293 | 1228333.2248
120 | 2665437.5869 | 1228246.1947
121 | 2665214.5997 | 1229014.5601
122 | 2665229.627 | 1229026.7821
123 | 2665203.5623 | 1229004.6912
124 | 2665114.2468 | 1228793.6818
125 | 2665015.4601 | 1228981.524
126 | 2664983.9222 | 1229029.2015
127 | 2665010.1967 | 1228990.6351
128 | 2664991.4314 | 1229019.6162
129 | 2664997.0085 | 1229012.497
130 | 2665003.4708 | 1229004.2479
131 | 2664849.705 | 1228925.5453
132 | 2664851.1999 | 1228941.3163
133 | 2664901.1214 | 1228968.3728
134 | 2664903.0218 | 1228967.8004
135 | 2665451.8835 | 1228271.0017
136 | 2665445.1301 | 1228264.9175
137 | 2665443.5891 | 1228221.0734
138 | 2665146.7679 | 1228846.0942

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99175 | -0.057647 | 0.0020631 | 0.00051707
1 | 0.99124 | -0.061265 | 0.0075113 | 0.0018825
2 | 0.99204 | -0.055652 | 0 | 0
3 | 0.99307 | -0.048362 | 0 | 0
4 | 0.99046 | -0.066771 | 0 | 0
5 | 0.99439 | -0.039085 | 0 | 0
6 | 0.98914 | -0.076118 | 0 | 0
7 | 0.98904 | -0.076844 | 0.00080195 | 0.00020099
8 | 0.98909 | -0.076489 | 0.0012989 | 0.00032554
9 | 0.99044 | -0.066878 | 0.00076168 | 0.00019089
10 | 0.99431 | -0.039695 | 0 | 0
11 | 0.99458 | -0.037776 | 0.002677 | 0.00067091
12 | 0.98934 | -0.074361 | 0.0042005 | 0.0010528
13 | 0.98943 | -0.073682 | 0 | 0
14 | 0.98902 | -0.076943 | 0.00078142 | 0.00019584
15 | 0.98838 | -0.081513 | 0.0010663 | 0.00026724
16 | 0.99402 | -0.04171 | 0.0017782 | 0.00044566
17 | 0.99403 | -0.041616 | 0.0011356 | 0.00028462
18 | 0.99429 | -0.0398 | 0.0015025 | 0.00037656
19 | 0.99419 | -0.040487 | 0.0022339 | 0.00055988
20 | 0.99615 | -0.026729 | 0.0014315 | 0.00035877
21 | 0.98976 | -0.071356 | 0 | 0
22 | 0.98847 | -0.080497 | 0.00061268 | 0.00015355
23 | 0.99743 | -0.017811 | 0 | 0
24 | 0.99411 | -0.040915 | 0.002936 | 0.00073582
25 | 0.99862 | -0.0095404 | 0 | 0
26 | 0.99047 | -0.066315 | 0 | 0
27 | 0.98448 | -0.10855 | 0 | 0
28 | 0.98433 | -0.10963 | 0 | 0
29 | 0.98455 | -0.10805 | 0 | 0
30 | 0.98423 | -0.11032 | 0.0011501 | 0.00028824
31 | 0.98432 | -0.10971 | 0.00065386 | 0.00016387
32 | 0.98594 | -0.098191 | 0 | 0
33 | 0.98571 | -0.099824 | 0.0078072 | 0.0019567
34 | 0.98653 | -0.09408 | 0 | 0
35 | 0.98533 | -0.10254 | 0.0011732 | 0.00029403
36 | 0.98876 | -0.078334 | 0 | 0
37 | 0.99009 | -0.069042 | 0.0011738 | 0.00029418
38 | 0.97827 | -0.15275 | 0 | 0
39 | 0.97918 | -0.14625 | 0 | 0
40 | 0.97811 | -0.15389 | 0.0075781 | 0.0018992
41 | 0.9965 | -0.02442 | 0 | 0
42 | 0.99645 | -0.024712 | 0.001893 | 0.00047444
43 | 0.99656 | -0.023989 | 0 | 0
44 | 0.97856 | -0.15067 | 0.0015918 | 0.00039895
45 | 0.98023 | -0.13875 | 0 | 0
46 | 0.98702 | -0.090627 | 0 | 0
47 | 0.98651 | -0.094188 | 0.0010534 | 0.000264
48 | 0.98437 | -0.10931 | 0 | 0
49 | 0.98264 | -0.12161 | 0.0014966 | 0.00037508
50 | 0.9802 | -0.13897 | 0.0012994 | 0.00032566
51 | 0.98091 | -0.13386 | 0.00069241 | 0.00017353
52 | 1 | 0 | -0.16147 | -0.040508
53 | 0.99783 | -0.015103 | 0.0018949 | 0.00047491
54 | 0.98701 | -0.090694 | 0.0010538 | 0.00026411
55 | 0.98421 | -0.11049 | 0.0020874 | 0.00052315
56 | 0.97749 | -0.15835 | 0.0020439 | 0.00051224
57 | 0.9965 | -0.0244 | 0 | 0
58 | 0.99621 | -0.026449 | 0 | 0
59 | 0.99709 | -0.020234 | 0.0019316 | 0.00048411
60 | 0.99619 | -0.026541 | 0.00049283 | 0.00012351
61 | 0.99591 | -0.028497 | 0 | 0
62 | 0.97844 | -0.15154 | 0.0020975 | 0.00052567
63 | 0.98409 | -0.11132 | 0.00083667 | 0.00020969
64 | 0.98019 | -0.13903 | 0.0010185 | 0.00025525
65 | 0.99991 | -0.00065365 | 0 | 0
66 | 0.97696 | -0.16213 | 0.0030428 | 0.00076259
67 | 0.97709 | -0.16119 | 0 | 0
68 | 0.99407 | -0.041363 | 0 | 0
69 | 0.99982 | -0.0012341 | 0.0013826 | 0.00034651
70 | 0.99986 | -0.0010096 | 0 | 0
71 | 0.99986 | -0.00095442 | 0.0017888 | 0.00044831
72 | 0.98007 | -0.1408 | 0.001919 | 0.00048095
73 | 0.97999 | -0.14139 | 0.0012637 | 0.00031671
74 | 0.98041 | -0.13835 | 0 | 0
75 | 0.97997 | -0.14152 | 0.00074316 | 0.00018625
76 | 0.98028 | -0.13927 | 0.00074786 | 0.00018743
77 | 0.98263 | -0.12248 | 0 | 0
78 | 0.98018 | -0.13997 | 0.0021635 | 0.00054222
79 | 0.98577 | -0.10008 | 0 | 0
80 | 0.98601 | -0.098353 | 0.0031094 | 0.00077929
81 | 0.98671 | -0.09336 | 0 | 0
82 | 0.98688 | -0.092157 | 0.001915 | 0.00047993
83 | 0.98716 | -0.090175 | 0 | 0
84 | 0.98816 | -0.08305 | 0 | 0
85 | 0.98809 | -0.08355 | 0.00077704 | 0.00019475
86 | 0.98807 | -0.083725 | 0.00084328 | 0.00021135
87 | 0.98806 | -0.08378 | 0.0015626 | 0.00039163
88 | 0.98803 | -0.083993 | 0.00084365 | 0.00021144
89 | 0.98896 | -0.077414 | 0.0035178 | 0.00088163
90 | 0.98797 | -0.084429 | 0.0019539 | 0.0004897
91 | 0.99405 | -0.041517 | 0.00083354 | 0.00020891
92 | 0.98356 | -0.1151 | 0.0011315 | 0.00028358
93 | 0.98355 | -0.11515 | 0.00060599 | 0.00015188
94 | 0.98363 | -0.11461 | 0.00097148 | 0.00024348
95 | 0.98369 | -0.11417 | 0.00065334 | 0.00016374
96 | 0.9839 | -0.11268 | 0 | 0
97 | 0.99545 | -0.031766 | 0.0011854 | 0.00029709
98 | 0.99532 | -0.032682 | 0.0029541 | 0.00074037
99 | 0.99648 | -0.024546 | 0.0016079 | 0.00040299
100 | 0.98826 | -0.081957 | 0.00062263 | 0.00015605
101 | 0.98822 | -0.082292 | 0.00055601 | 0.00013935
102 | 0.98843 | -0.080805 | 0.0016425 | 0.00041165
103 | 0.98811 | -0.083067 | 0.0032283 | 0.00080909
104 | 0.98805 | -0.083461 | 0.00036581 | 9.1682e-05
105 | 0.98799 | -0.083922 | 0.00030892 | 7.7421e-05
106 | 0.98786 | -0.084843 | 0.0025511 | 0.00063936
107 | 0.98974 | -0.071529 | 0.0010812 | 0.00027098
108 | 0.98779 | -0.08534 | 0.00090274 | 0.00022625
109 | 0.99236 | -0.053434 | 0 | 0
110 | 0.98906 | -0.076693 | 0 | 0
111 | 0.98654 | -0.094558 | 0.00076532 | 0.00019181
112 | 0.98642 | -0.095454 | 0 | 0
113 | 0.98085 | -0.135 | 0 | 0
114 | 0.97958 | -0.14408 | 0.00063381 | 0.00015885
115 | 0.98009 | -0.14046 | 0.0013206 | 0.00033097
116 | 0.97936 | -0.14567 | 0 | 0
117 | 0.9802 | -0.13969 | 0.0004593 | 0.00011511
118 | 0.97902 | -0.14807 | 0.0049662 | 0.0012447
119 | 0.97899 | -0.1483 | 0.0029142 | 0.00073037
120 | 0.98595 | -0.098805 | 0.00035222 | 8.8275e-05
121 | 0.9877 | -0.085932 | 0.00079186 | 0.00019846
122 | 0.98767 | -0.086177 | 0.0012376 | 0.00031018
123 | 0.98775 | -0.085624 | 0.00090351 | 0.00022644
124 | 0.99645 | -0.024736 | 0.0015425 | 0.00038659
125 | 0.97811 | -0.15387 | 0.00069651 | 0.00017456
126 | 0.97715 | -0.16072 | 0.0053548 | 0.001342
127 | 0.97789 | -0.15542 | 0.0012884 | 0.00032289
128 | 0.9773 | -0.15965 | 0.0012608 | 0.00031599
129 | 0.97743 | -0.15874 | 0.0015252 | 0.00038226
130 | 0.9776 | -0.15752 | 0.0016315 | 0.00040888
131 | 0.97682 | -0.16312 | 0.0045065 | 0.0011294
132 | 0.97693 | -0.16236 | 0 | 0
133 | 0.97733 | -0.1595 | 0.0013767 | 0.00034504
134 | 0.97734 | -0.15937 | 0.0012601 | 0.00031581
135 | 0.98592 | -0.099006 | 0.0003808 | 9.5438e-05
136 | 0.98593 | -0.09897 | 0.00038091 | 9.5465e-05
137 | 0.98594 | -0.098897 | 0.00034357 | 8.6106e-05
138 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0075151 | 0.0018834 | -0.0075113 | -0.0018825 | 3.763e-06 | 8.3558e-07 | 0.011276 | 0.011276 | 0.011276 | 0.99175 | -0.057647 | 0.99124 | -0.061265 | 4.1762
1 | -0.0095782 | -0.0024004 | 0.0095809 | 0.0024012 | 2.6463e-06 | 7.5276e-07 | 0.014371 | 0.014371 | 0.014371 | 0.99175 | -0.057647 | 0.99204 | -0.055652 | 5.3226
2 | -0.035807 | -0.008981 | 0.035844 | 0.0089947 | 3.6226e-05 | 1.3673e-05 | 0.053712 | 0.053712 | 0.053712 | 0.99204 | -0.055652 | 0.99307 | -0.048362 | 19.8934
3 | 0.026226 | 0.0065799 | -0.026186 | -0.0065649 | 4.0393e-05 | 1.4997e-05 | 0.039341 | 0.039341 | 0.039341 | 0.99204 | -0.055652 | 0.99046 | -0.066771 | 14.5709
4 | -0.035844 | -0.0089947 | 0.03589 | 0.0090122 | 4.6212e-05 | 1.7441e-05 | 0.053712 | 0.053712 | 0.053712 | 0.99307 | -0.048362 | 0.99439 | -0.039085 | 19.8933
5 | 0.00076169 | 0.00019072 | -0.00076168 | -0.00019089 | 1.1376e-08 | -1.7481e-07 | 0.0011443 | 0.0011443 | 0.0011443 | 0.99046 | -0.066771 | 0.99044 | -0.066878 | 0.42382
6 | 0.025424 | 0.0063741 | -0.025392 | -0.006362 | 3.288e-05 | 1.2182e-05 | 0.038197 | 0.038197 | 0.038197 | 0.99046 | -0.066771 | 0.98914 | -0.076118 | 14.1471
7 | 0.0074857 | 0.0018753 | -0.0074851 | -0.0018751 | 6.3168e-07 | 1.383e-07 | 0.011201 | 0.011201 | 0.011201 | 0.99439 | -0.039085 | 0.99431 | -0.039695 | 4.1487
8 | -0.043376 | -0.010887 | 0.043383 | 0.01089 | 7.8874e-06 | 2.9947e-06 | 0.064913 | 0.064913 | 0.064913 | 0.99439 | -0.039085 | 0.99458 | -0.037776 | 24.042
9 | 0.0051019 | 0.0012784 | -0.0051014 | -0.0012784 | 5.1276e-07 | 1.8176e-08 | 0.007675 | 0.0076751 | 0.0076751 | 0.98914 | -0.076118 | 0.98904 | -0.076844 | 2.8426
10 | 0.02029 | 0.0050836 | -0.020289 | -0.0050832 | 1.0415e-06 | 3.776e-07 | 0.030522 | 0.030522 | 0.030522 | 0.98914 | -0.076118 | 0.98909 | -0.076489 | 11.3045
11 | 0.0042995 | 0.0010774 | -0.0042994 | -0.0010774 | 5.933e-08 | -6.342e-09 | 0.0064685 | 0.0064685 | 0.0064685 | 0.98904 | -0.076844 | 0.98902 | -0.076943 | 2.3958
12 | 0.01899 | 0.0047577 | -0.018976 | -0.0047529 | 1.319e-05 | 4.741e-06 | 0.028568 | 0.028568 | 0.028568 | 0.98909 | -0.076489 | 0.98838 | -0.081513 | 10.5808
13 | 0.0015025 | 0.00037648 | -0.0015025 | -0.00037656 | 2.1832e-08 | -8.1356e-08 | 0.0022485 | 0.0022486 | 0.0022486 | 0.99431 | -0.039695 | 0.99429 | -0.0398 | 0.8328
14 | 0.0059826 | 0.0014987 | -0.0059819 | -0.0014986 | 6.5489e-07 | 8.2075e-08 | 0.0089529 | 0.008953 | 0.008953 | 0.99431 | -0.039695 | 0.99419 | -0.040487 | 3.3159
15 | -0.04606 | -0.011561 | 0.046131 | 0.011588 | 7.0765e-05 | 2.6907e-05 | 0.068918 | 0.068918 | 0.068918 | 0.99458 | -0.037776 | 0.99615 | -0.026729 | 25.5253
16 | -0.0042005 | -0.0010528 | 0.0042009 | 0.0010527 | 3.9476e-07 | -5.1713e-08 | 0.0063178 | 0.0063178 | 0.0063178 | 0.98934 | -0.074361 | 0.98943 | -0.073682 | 2.3399
17 | -0.017944 | -0.0044975 | 0.017949 | 0.0044996 | 5.7793e-06 | 2.0594e-06 | 0.026986 | 0.026986 | 0.026986 | 0.98943 | -0.073682 | 0.98976 | -0.071356 | 9.9948
18 | 0.013743 | 0.0034448 | -0.01373 | -0.0034405 | 1.2961e-05 | 4.361e-06 | 0.020668 | 0.020668 | 0.020668 | 0.98943 | -0.073682 | 0.98847 | -0.080497 | 7.6549
19 | 0.003518 | 0.00088155 | -0.0035178 | -0.00088163 | 2.289e-07 | -7.9982e-08 | 0.0052929 | 0.0052929 | 0.0052929 | 0.98902 | -0.076943 | 0.98896 | -0.077414 | 1.9603
20 | 0.01791 | 0.0044857 | -0.017906 | -0.0044843 | 3.8059e-06 | 1.3563e-06 | 0.026963 | 0.026963 | 0.026963 | 0.98838 | -0.081513 | 0.98816 | -0.08305 | 9.9863
21 | -0.0017782 | -0.00044566 | 0.0017782 | 0.00044561 | 2.3043e-08 | -5.8694e-08 | 0.0026619 | 0.0026619 | 0.0026619 | 0.99402 | -0.04171 | 0.99403 | -0.041616 | 0.9859
22 | -0.0029139 | -0.00073022 | 0.002914 | 0.00073015 | 1.0195e-07 | -7.211e-08 | 0.0043619 | 0.0043619 | 0.0043619 | 0.99403 | -0.041616 | 0.99407 | -0.041363 | 1.6155
23 | 0.003748 | 0.0009387 | -0.0037476 | -0.00093883 | 4.543e-07 | -1.2526e-07 | 0.0056094 | 0.0056095 | 0.0056095 | 0.99419 | -0.040487 | 0.99407 | -0.041363 | 2.0776
24 | -0.047563 | -0.011947 | 0.047622 | 0.011969 | 5.9056e-05 | 2.2469e-05 | 0.071057 | 0.071057 | 0.071057 | 0.99615 | -0.026729 | 0.99743 | -0.017811 | 26.3173
25 | 0.0010813 | 0.00027079 | -0.0010812 | -0.00027098 | 2.5851e-08 | -1.9155e-07 | 0.0016255 | 0.0016256 | 0.0016256 | 0.98976 | -0.071356 | 0.98974 | -0.071529 | 0.60207
26 | -0.019031 | -0.0047704 | 0.019037 | 0.0047726 | 6.1025e-06 | 2.1935e-06 | 0.028611 | 0.028611 | 0.028611 | 0.98976 | -0.071356 | 0.99009 | -0.069042 | 10.5968
27 | 0.013117 | 0.0032869 | -0.013117 | -0.0032868 | 5.5869e-07 | 1.8545e-07 | 0.019746 | 0.019746 | 0.019746 | 0.98847 | -0.080497 | 0.98843 | -0.080805 | 7.3133
28 | 0.083241 | 0.021007 | -0.082972 | -0.020904 | 0.00026907 | 0.00010313 | 0.12423 | 0.12423 | 0.12423 | 0.99743 | -0.017811 | 0.99411 | -0.040915 | 46.0129
29 | -0.13086 | -0.032977 | 0.13101 | 0.033035 | 0.00015166 | 5.7996e-05 | 0.19529 | 0.19529 | 0.19529 | 0.99743 | -0.017811 | 0.99862 | -0.0095404 | 36.1651
30 | 0.080036 | 0.020168 | -0.079753 | -0.02006 | 0.00028348 | 0.00010862 | 0.11984 | 0.11984 | 0.11984 | 0.99411 | -0.040915 | 0.99047 | -0.066315 | 44.3853
31 | -0.15729 | -0.039634 | 0.1575 | 0.039714 | 0.00021029 | 8.0558e-05 | 0.23445 | 0.23445 | 0.23445 | 0.99862 | -0.0095404 | 1 | 0 | 43.4158
32 | 0.026273 | 0.006599 | -0.026253 | -0.0065915 | 2.0306e-05 | 7.5325e-06 | 0.039154 | 0.039154 | 0.039154 | 0.99862 | -0.0095404 | 0.99783 | -0.015103 | 14.5016
33 | 0.059535 | 0.01499 | -0.059435 | -0.014952 | 9.9815e-05 | 3.8134e-05 | 0.089465 | 0.089465 | 0.089465 | 0.99047 | -0.066315 | 0.98876 | -0.078334 | 33.1353
34 | 0.020218 | 0.0050695 | -0.020211 | -0.0050668 | 7.6373e-06 | 2.7668e-06 | 0.030375 | 0.030375 | 0.030375 | 0.99047 | -0.066315 | 0.99009 | -0.069042 | 11.2501
35 | 0.0038923 | 0.00097479 | -0.0038917 | -0.00097491 | 5.8022e-07 | -1.1841e-07 | 0.0058829 | 0.005883 | 0.005883 | 0.98448 | -0.10855 | 0.98433 | -0.10963 | 2.1789
36 | -0.0038923 | -0.00097479 | 0.0038926 | 0.00097473 | 2.7086e-07 | -5.5315e-08 | 0.0058829 | 0.0058828 | 0.0058829 | 0.98448 | -0.10855 | 0.98455 | -0.10805 | 2.1788
37 | 0.0032379 | 0.00081117 | -0.0032375 | -0.00081131 | 3.0933e-07 | -1.4402e-07 | 0.0048946 | 0.0048947 | 0.0048947 | 0.98433 | -0.10963 | 0.98423 | -0.11032 | 1.8128
38 | 0.00065387 | 0.00016374 | -0.00065386 | -0.00016387 | 6.624e-09 | -1.3556e-07 | 0.0009884 | 0.00098845 | 0.00098845 | 0.98433 | -0.10963 | 0.98432 | -0.10971 | 0.36609
39 | 0.0042025 | 0.0010511 | -0.0042017 | -0.0010511 | 7.3136e-07 | -8.8199e-08 | 0.0063507 | 0.0063508 | 0.0063508 | 0.98455 | -0.10805 | 0.98437 | -0.10931 | 2.3522
40 | 0.040021 | 0.01006 | -0.039946 | -0.010031 | 7.5408e-05 | 2.8584e-05 | 0.060497 | 0.060497 | 0.060497 | 0.98455 | -0.10805 | 0.98264 | -0.12161 | 22.4064
41 | -0.048116 | -0.012085 | 0.048153 | 0.012099 | 3.6904e-05 | 1.4051e-05 | 0.072731 | 0.072731 | 0.072731 | 0.98455 | -0.10805 | 0.98533 | -0.10254 | 26.9373
42 | 0.0020874 | 0.00052307 | -0.0020874 | -0.00052315 | 4.8796e-08 | -8.1012e-08 | 0.0031559 | 0.0031559 | 0.0031559 | 0.98423 | -0.11032 | 0.98421 | -0.11049 | 1.1689
43 | 0.007809 | 0.0019571 | -0.0078072 | -0.0019567 | 1.7654e-06 | 4.1931e-07 | 0.011786 | 0.011786 | 0.011786 | 0.98594 | -0.098191 | 0.98571 | -0.099824 | 4.365
44 | -0.057165 | -0.014362 | 0.057198 | 0.014374 | 3.2714e-05 | 1.2492e-05 | 0.086288 | 0.086288 | 0.086288 | 0.98594 | -0.098191 | 0.98653 | -0.09408 | 31.9585
45 | 0.049356 | 0.012405 | -0.049326 | -0.012393 | 2.9858e-05 | 1.1374e-05 | 0.074502 | 0.074502 | 0.074502 | 0.98594 | -0.098191 | 0.98533 | -0.10254 | 27.5935
46 | -0.058251 | -0.014638 | 0.058279 | 0.014649 | 2.8002e-05 | 1.0696e-05 | 0.087877 | 0.087877 | 0.087877 | 0.98653 | -0.09408 | 0.98702 | -0.090627 | 32.5469
47 | 0.0010534 | 0.00026388 | -0.0010534 | -0.000264 | 1.5767e-08 | -1.2174e-07 | 0.0015888 | 0.0015889 | 0.0015889 | 0.98653 | -0.09408 | 0.98651 | -0.094188 | 0.58847
48 | 0.059435 | 0.014952 | -0.059333 | -0.014913 | 0.00010173 | 3.8867e-05 | 0.089465 | 0.089465 | 0.089465 | 0.98876 | -0.078334 | 0.98702 | -0.090627 | 33.1353
49 | -0.016777 | -0.0042045 | 0.016792 | 0.0042098 | 1.5097e-05 | 5.3396e-06 | 0.025519 | 0.025519 | 0.025519 | 0.97827 | -0.15275 | 0.97918 | -0.14625 | 9.4515
50 | 0.016777 | 0.0042045 | -0.016774 | -0.0042035 | 2.6536e-06 | 9.3863e-07 | 0.025519 | 0.025519 | 0.025519 | 0.97827 | -0.15275 | 0.97811 | -0.15389 | 9.4515
51 | 0.018519 | 0.0046435 | -0.018508 | -0.0046394 | 1.1334e-05 | 4.071e-06 | 0.028144 | 0.028144 | 0.028144 | 0.97918 | -0.14625 | 0.97856 | -0.15067 | 10.4236
52 | -0.035311 | -0.0088533 | 0.035348 | 0.0088672 | 3.6757e-05 | 1.388e-05 | 0.053662 | 0.053662 | 0.053662 | 0.97918 | -0.14625 | 0.98023 | -0.13875 | 19.8749
53 | 0.0091963 | 0.0023043 | -0.0091906 | -0.0023027 | 5.6779e-06 | 1.6007e-06 | 0.01399 | 0.013991 | 0.013991 | 0.97811 | -0.15389 | 0.97749 | -0.15835 | 5.1817
54 | 0.0018931 | 0.00047427 | -0.001893 | -0.00047444 | 7.6596e-08 | -1.7065e-07 | 0.0028268 | 0.0028269 | 0.0028269 | 0.9965 | -0.02442 | 0.99645 | -0.024712 | 1.047
55 | -0.0018931 | -0.00047427 | 0.0018932 | 0.00047401 | 1.1266e-07 | -2.5103e-07 | 0.0028268 | 0.0028267 | 0.0028268 | 0.9965 | -0.02442 | 0.99656 | -0.023989 | 1.047
56 | 0.0031507 | 0.0007893 | -0.0031505 | -0.0007894 | 1.7895e-07 | -9.9994e-08 | 0.0047044 | 0.0047045 | 0.0047045 | 0.99656 | -0.023989 | 0.9965 | -0.0244 | 1.7424
57 | 0.017354 | 0.0043585 | -0.017348 | -0.0043564 | 5.9313e-06 | 2.0969e-06 | 0.025915 | 0.025915 | 0.025915 | 0.99656 | -0.023989 | 0.99621 | -0.026449 | 9.5981
58 | -0.022397 | -0.0056218 | 0.022409 | 0.0056261 | 1.1684e-05 | 4.2757e-06 | 0.033446 | 0.033446 | 0.033446 | 0.99656 | -0.023989 | 0.99709 | -0.020234 | 12.3874
59 | 0.016916 | 0.0042405 | -0.016914 | -0.0042398 | 2.0222e-06 | 7.1625e-07 | 0.025723 | 0.025723 | 0.025723 | 0.97856 | -0.15067 | 0.97844 | -0.15154 | 9.5271
60 | 0.002318 | 0.00058075 | -0.0023179 | -0.00058084 | 7.0053e-08 | -8.7352e-08 | 0.0035187 | 0.0035187 | 0.0035187 | 0.98023 | -0.13875 | 0.9802 | -0.13897 | 1.3032
61 | -0.037666 | -0.0094479 | 0.037691 | 0.0094576 | 2.5543e-05 | 9.6664e-06 | 0.057181 | 0.057181 | 0.057181 | 0.98023 | -0.13875 | 0.98091 | -0.13386 | 21.1781
62 | 0.0010538 | 0.00026403 | -0.0010538 | -0.00026411 | 9.6325e-09 | -7.4463e-08 | 0.0015887 | 0.0015887 | 0.0015887 | 0.98702 | -0.090627 | 0.98701 | -0.090694 | 0.58841
63 | 0.0042017 | 0.0010511 | -0.0042006 | -0.0010513 | 1.1662e-06 | -1.4034e-07 | 0.0063508 | 0.006351 | 0.006351 | 0.98437 | -0.10931 | 0.98409 | -0.11132 | 2.3522
64 | 0.038449 | 0.0096559 | -0.038384 | -0.0096311 | 6.537e-05 | 2.4752e-05 | 0.058231 | 0.058231 | 0.058231 | 0.98264 | -0.12161 | 0.98091 | -0.13386 | 21.5671
65 | 0.0010185 | 0.00025518 | -0.0010185 | -0.00025525 | 9.4739e-09 | -7.641e-08 | 0.0015461 | 0.0015461 | 0.0015461 | 0.9802 | -0.13897 | 0.98019 | -0.13903 | 0.57265
66 | 0.0031719 | 0.00079396 | -0.0031716 | -0.00079412 | 2.8639e-07 | -1.6016e-07 | 0.0047194 | 0.0047195 | 0.0047195 | 1 | 0 | 0.99991 | -0.00065365 | 1.748
67 | 0.024358 | 0.0061166 | -0.024341 | -0.0061102 | 1.7357e-05 | 6.4008e-06 | 0.036328 | 0.036329 | 0.036329 | 0.99783 | -0.015103 | 0.99709 | -0.020234 | 13.455
68 | 0.0071468 | 0.0017904 | -0.0071458 | -0.0017902 | 1.0081e-06 | 2.1665e-07 | 0.010879 | 0.010879 | 0.010879 | 0.97749 | -0.15835 | 0.97734 | -0.15937 | 4.0294
69 | 0.0031505 | 0.0007894 | -0.0031505 | -0.00078943 | 6.3616e-08 | -3.5541e-08 | 0.0047045 | 0.0047045 | 0.0047045 | 0.9965 | -0.0244 | 0.99648 | -0.024546 | 1.7424
70 | 0.00049284 | 0.00012328 | -0.00049283 | -0.00012351 | 6.2843e-09 | -2.3957e-07 | 0.00073606 | 0.00073614 | 0.00073614 | 0.99621 | -0.026449 | 0.99619 | -0.026541 | 0.27265
71 | 0.016855 | 0.0042331 | -0.01685 | -0.0042314 | 4.799e-06 | 1.6879e-06 | 0.025179 | 0.025179 | 0.025179 | 0.99621 | -0.026449 | 0.99591 | -0.028497 | 9.3255
72 | 0.01685 | 0.0042314 | -0.016842 | -0.0042287 | 7.6509e-06 | 2.6911e-06 | 0.025179 | 0.025179 | 0.025179 | 0.99591 | -0.028497 | 0.99545 | -0.031766 | 9.3256
73 | 0.014816 | 0.0037141 | -0.014812 | -0.0037124 | 4.7959e-06 | 1.6545e-06 | 0.022533 | 0.022533 | 0.022533 | 0.97844 | -0.15154 | 0.97811 | -0.15387 | 8.3457
74 | 0.0033639 | 0.00084159 | -0.0033633 | -0.00084184 | 6.2771e-07 | -2.5256e-07 | 0.0050859 | 0.0050861 | 0.0050861 | 0.98409 | -0.11132 | 0.9839 | -0.11268 | 1.8837
75 | 0.0017889 | 0.00044812 | -0.0017888 | -0.00044831 | 7.4448e-08 | -1.9219e-07 | 0.002662 | 0.0026621 | 0.0026621 | 0.99991 | -0.00065365 | 0.99986 | -0.00095442 | 0.98597
76 | 0.0013827 | 0.000346 | -0.0013826 | -0.00034631 | 6.7995e-08 | -3.1145e-07 | 0.0020575 | 0.0020576 | 0.0020576 | 0.99991 | -0.00065365 | 0.99986 | -0.0010096 | 0.76208
77 | -0.0030428 | -0.00076259 | 0.0030432 | 0.00076238 | 3.9273e-07 | -2.1592e-07 | 0.0046345 | 0.0046344 | 0.0046345 | 0.97696 | -0.16213 | 0.97709 | -0.16119 | 1.7165
78 | -0.0030432 | -0.00076238 | 0.0030434 | 0.00076227 | 1.974e-07 | -1.0858e-07 | 0.0046344 | 0.0046343 | 0.0046344 | 0.97709 | -0.16119 | 0.97715 | -0.16072 | 1.7164
79 | 0.00083356 | 0.00020868 | -0.00083354 | -0.00020891 | 1.7756e-08 | -2.3012e-07 | 0.0012477 | 0.0012478 | 0.0012478 | 0.99407 | -0.041363 | 0.99405 | -0.041517 | 0.46213
80 | -0.0013826 | -0.00034651 | 0.0013826 | 0.00034631 | 4.293e-08 | -1.966e-07 | 0.0020577 | 0.0020576 | 0.0020577 | 0.99982 | -0.0012341 | 0.99986 | -0.0010096 | 0.76211
81 | 0.002007 | 0.00050247 | -0.0020069 | -0.00050277 | 1.6348e-07 | -2.9267e-07 | 0.003047 | 0.0030472 | 0.0030472 | 0.98007 | -0.1408 | 0.97999 | -0.14139 | 1.1286
82 | -0.0039261 | -0.00098342 | 0.0039274 | 0.00098318 | 1.3283e-06 | -2.4441e-07 | 0.0059606 | 0.0059604 | 0.0059606 | 0.98007 | -0.1408 | 0.98041 | -0.13835 | 2.2076
83 | 0.00074317 | 0.00018605 | -0.00074316 | -0.00018625 | 1.3013e-08 | -2.0135e-07 | 0.0011284 | 0.0011284 | 0.0011284 | 0.97999 | -0.14139 | 0.97997 | -0.14152 | 0.41794
84 | 0.0029119 | 0.0007291 | -0.0029116 | -0.00072934 | 3.6764e-07 | -2.3895e-07 | 0.0044193 | 0.0044195 | 0.0044195 | 0.98041 | -0.13835 | 0.98028 | -0.13927 | 1.6368
85 | -0.0068393 | -0.0017123 | 0.0068543 | 0.0017152 | 1.5004e-05 | 2.9498e-06 | 0.01038 | 0.010379 | 0.01038 | 0.98041 | -0.13835 | 0.98263 | -0.12248 | 3.8443
86 | 0.0021637 | 0.00054191 | -0.0021635 | -0.00054222 | 2.1217e-07 | -3.1575e-07 | 0.0032843 | 0.0032844 | 0.0032844 | 0.98028 | -0.13927 | 0.98018 | -0.13997 | 1.2164
87 | -0.0068543 | -0.0017152 | 0.0068755 | 0.0017194 | 2.1209e-05 | 4.1469e-06 | 0.010379 | 0.010377 | 0.010379 | 0.98263 | -0.12248 | 0.98577 | -0.10008 | 3.844
88 | -0.0068755 | -0.0017194 | 0.0068772 | 0.0017197 | 1.6392e-06 | 3.1939e-07 | 0.010377 | 0.010377 | 0.010377 | 0.98577 | -0.10008 | 0.98601 | -0.098353 | 3.8434
89 | -0.0099866 | -0.002499 | 0.0099934 | 0.002501 | 6.8855e-06 | 2.0281e-06 | 0.01507 | 0.015069 | 0.01507 | 0.98601 | -0.098353 | 0.98671 | -0.09336 | 5.5814
90 | -0.0099934 | -0.002501 | 0.0099951 | 0.0025015 | 1.6599e-06 | 4.8878e-07 | 0.015069 | 0.015069 | 0.015069 | 0.98671 | -0.09336 | 0.98688 | -0.092157 | 5.5813
91 | -0.01191 | -0.0029814 | 0.011913 | 0.0029825 | 3.2605e-06 | 1.0469e-06 | 0.017957 | 0.017957 | 0.017957 | 0.98688 | -0.092157 | 0.98716 | -0.090175 | 6.6507
92 | -0.011913 | -0.0029825 | 0.011925 | 0.0029862 | 1.1734e-05 | 3.7668e-06 | 0.017957 | 0.017956 | 0.017957 | 0.98716 | -0.090175 | 0.98816 | -0.08305 | 6.6506
93 | 0.0023399 | 0.000586 | -0.0023397 | -0.00058621 | 1.6182e-07 | -2.0535e-07 | 0.0035233 | 0.0035234 | 0.0035234 | 0.98816 | -0.08305 | 0.98809 | -0.08355 | 1.305
94 | 0.0036414 | 0.00091207 | -0.0036411 | -0.00091217 | 3.4002e-07 | -1.0137e-07 | 0.0054832 | 0.0054833 | 0.0054833 | 0.98816 | -0.08305 | 0.98807 | -0.083725 | 2.0309
95 | 0.0015627 | 0.00039146 | -0.0015626 | -0.00039163 | 4.9757e-08 | -1.6529e-07 | 0.0023532 | 0.0023533 | 0.0023533 | 0.98809 | -0.08355 | 0.98806 | -0.08378 | 0.87159
96 | 0.0027978 | 0.00070083 | -0.0027977 | -0.00070091 | 1.0355e-07 | -7.9892e-08 | 0.0042133 | 0.0042134 | 0.0042134 | 0.98807 | -0.083725 | 0.98803 | -0.083993 | 1.5605
97 | 0.001954 | 0.00048947 | -0.0019539 | -0.0004897 | 1.1808e-07 | -2.344e-07 | 0.0029428 | 0.0029429 | 0.0029429 | 0.98803 | -0.083993 | 0.98797 | -0.084429 | 1.09
98 | 0.00060599 | 0.00015177 | -0.00060599 | -0.00015188 | 4.5651e-09 | -1.0871e-07 | 0.00091676 | 0.0009168 | 0.0009168 | 0.98356 | -0.1151 | 0.98355 | -0.11515 | 0.33955
99 | -0.0017375 | -0.00043534 | 0.0017376 | 0.00043504 | 1.1762e-07 | -3.0103e-07 | 0.0026286 | 0.0026284 | 0.0026286 | 0.98356 | -0.1151 | 0.98363 | -0.11461 | 0.97354
100 | -0.0027091 | -0.00067852 | 0.0027092 | 0.00067838 | 1.6516e-07 | -1.3654e-07 | 0.0040981 | 0.004098 | 0.0040981 | 0.98363 | -0.11461 | 0.98369 | -0.11417 | 1.5178
101 | -0.0033626 | -0.00084212 | 0.0033633 | 0.00084184 | 6.926e-07 | -2.7841e-07 | 0.0050863 | 0.0050861 | 0.0050863 | 0.98369 | -0.11417 | 0.9839 | -0.11268 | 1.8838
102 | 0.015657 | 0.0039316 | -0.015655 | -0.0039309 | 1.994e-06 | 6.9112e-07 | 0.023407 | 0.023407 | 0.023407 | 0.99545 | -0.031766 | 0.99532 | -0.032682 | 8.6693
103 | 0.012701 | 0.0031906 | -0.012664 | -0.0031786 | 3.6573e-05 | 1.1961e-05 | 0.018991 | 0.018991 | 0.018991 | 0.99532 | -0.032682 | 0.99236 | -0.053434 | 7.0338
104 | 0.0015425 | 0.00038644 | -0.0015425 | -0.00038659 | 4.0597e-08 | -1.4412e-07 | 0.0023034 | 0.0023034 | 0.0023034 | 0.99648 | -0.024546 | 0.99645 | -0.024736 | 0.85313
105 | 0.01085 | 0.0027185 | -0.010849 | -0.0027183 | 5.0276e-07 | 1.5468e-07 | 0.016336 | 0.016336 | 0.016336 | 0.98826 | -0.081957 | 0.98822 | -0.082292 | 6.0503
106 | -0.011472 | -0.0028745 | 0.011474 | 0.0028751 | 1.8294e-06 | 5.7769e-07 | 0.017273 | 0.017273 | 0.017273 | 0.98826 | -0.081957 | 0.98843 | -0.080805 | 6.3975
107 | 0.010293 | 0.002579 | -0.010292 | -0.0025786 | 1.104e-06 | 3.3027e-07 | 0.015499 | 0.015499 | 0.015499 | 0.98822 | -0.082292 | 0.98811 | -0.083067 | 5.7403
108 | 0.0070637 | 0.0017696 | -0.0070633 | -0.0017695 | 3.8443e-07 | 7.8119e-08 | 0.010637 | 0.010637 | 0.010637 | 0.98811 | -0.083067 | 0.98805 | -0.083461 | 3.9397
109 | 0.0066975 | 0.0016778 | -0.0066971 | -0.0016777 | 4.2724e-07 | 7.8131e-08 | 0.010086 | 0.010086 | 0.010086 | 0.98805 | -0.083461 | 0.98799 | -0.083922 | 3.7357
110 | 0.0063882 | 0.0016003 | -0.0063873 | -0.0016002 | 8.1336e-07 | 1.3252e-07 | 0.009621 | 0.0096211 | 0.0096211 | 0.98799 | -0.083922 | 0.98786 | -0.084843 | 3.5634
111 | 0.0038363 | 0.0009608 | -0.003836 | -0.00096086 | 2.6403e-07 | -6.0677e-08 | 0.0057783 | 0.0057784 | 0.0057784 | 0.98786 | -0.084843 | 0.98779 | -0.08534 | 2.1401
112 | 0.0029332 | 0.00073462 | -0.0029331 | -0.00073469 | 1.15e-07 | -7.66e-08 | 0.0044185 | 0.0044185 | 0.0044185 | 0.98779 | -0.08534 | 0.98775 | -0.085624 | 1.6365
113 | 0.012664 | 0.0031786 | -0.012623 | -0.0031652 | 4.0792e-05 | 1.3355e-05 | 0.018991 | 0.018992 | 0.018992 | 0.99236 | -0.053434 | 0.98906 | -0.076693 | 7.0341
114 | 0.012623 | 0.0031652 | -0.012592 | -0.003155 | 3.1187e-05 | 1.0221e-05 | 0.018992 | 0.018993 | 0.018993 | 0.98906 | -0.076693 | 0.98654 | -0.094558 | 7.0344
115 | 0.0014584 | 0.00036132 | -0.0014582 | -0.00036201 | 1.7729e-07 | -6.8239e-07 | 0.0021982 | 0.0021985 | 0.0021985 | 0.98654 | -0.094558 | 0.98642 | -0.095454 | 0.81425
116 | 0.010369 | 0.0026019 | -0.010311 | -0.0025844 | 5.7971e-05 | 1.7476e-05 | 0.01564 | 0.015642 | 0.015642 | 0.98654 | -0.094558 | 0.98085 | -0.135 | 5.7933
117 | 0.0014582 | 0.00036201 | -0.0014575 | -0.00036458 | 6.6867e-07 | -2.5704e-06 | 0.0021985 | 0.0021995 | 0.0021995 | 0.98642 | -0.095454 | 0.98595 | -0.098805 | 0.81462
118 | 0.010311 | 0.0025844 | -0.010304 | -0.0025824 | 6.6945e-06 | 2.0217e-06 | 0.015642 | 0.015642 | 0.015642 | 0.98085 | -0.135 | 0.9802 | -0.13969 | 5.7934
119 | -0.0085187 | -0.0021349 | 0.008523 | 0.002136 | 4.2617e-06 | 1.1254e-06 | 0.01294 | 0.01294 | 0.01294 | 0.97958 | -0.14408 | 0.98009 | -0.14046 | 4.7927
120 | 0.0078849 | 0.001976 | -0.0078832 | -0.0019756 | 1.7447e-06 | 4.2573e-07 | 0.011977 | 0.011977 | 0.011977 | 0.97958 | -0.14408 | 0.97936 | -0.14567 | 4.4361
121 | -0.0098436 | -0.002467 | 0.0098446 | 0.0024673 | 1.0493e-06 | 3.087e-07 | 0.014945 | 0.014945 | 0.014945 | 0.98009 | -0.14046 | 0.9802 | -0.13969 | 5.5352
122 | 0.0078832 | 0.0019756 | -0.0078806 | -0.001975 | 2.6125e-06 | 6.3771e-07 | 0.011977 | 0.011978 | 0.011978 | 0.97936 | -0.14567 | 0.97902 | -0.14807 | 4.4362
123 | 0.0029143 | 0.00073031 | -0.0029142 | -0.00073037 | 9.5285e-08 | -6.1216e-08 | 0.0044294 | 0.0044295 | 0.0044295 | 0.97902 | -0.14807 | 0.97899 | -0.1483 | 1.6405
124 | 0.00034357 | 8.5777e-05 | -0.00034357 | -8.6106e-05 | 4.3494e-09 | -3.2902e-07 | 0.00051841 | 0.00051852 | 0.00051852 | 0.98595 | -0.098805 | 0.98594 | -0.098897 | 0.19205
125 | 0.00076173 | 0.00019053 | -0.00076171 | -0.00019079 | 1.7407e-08 | -2.6252e-07 | 0.0011495 | 0.0011496 | 0.0011496 | 0.98595 | -0.098805 | 0.98593 | -0.09897 | 0.42577
126 | 0.0012377 | 0.00030995 | -0.0012376 | -0.00031018 | 4.2021e-08 | -2.3174e-07 | 0.0018645 | 0.0018646 | 0.0018646 | 0.9877 | -0.085932 | 0.98767 | -0.086177 | 0.6906
127 | -0.0020295 | -0.00050841 | 0.0020296 | 0.00050825 | 8.6384e-08 | -1.5632e-07 | 0.0030575 | 0.0030574 | 0.0030575 | 0.9877 | -0.085932 | 0.98775 | -0.085624 | 1.1324
128 | 0.014115 | 0.0035379 | -0.014112 | -0.0035368 | 3.0277e-06 | 1.0324e-06 | 0.021474 | 0.021474 | 0.021474 | 0.97811 | -0.15387 | 0.97789 | -0.15542 | 7.9532
129 | -0.0083982 | -0.0021043 | 0.0083994 | 0.0021046 | 1.2427e-06 | 3.2539e-07 | 0.012789 | 0.012789 | 0.012789 | 0.97715 | -0.16072 | 0.9773 | -0.15965 | 4.7365
130 | 0.012824 | 0.003214 | -0.01282 | -0.0032127 | 3.7171e-06 | 1.2334e-06 | 0.019513 | 0.019513 | 0.019513 | 0.97789 | -0.15542 | 0.9776 | -0.15752 | 7.2272
131 | -0.0096602 | -0.0024206 | 0.0096614 | 0.002421 | 1.2208e-06 | 3.562e-07 | 0.014708 | 0.014708 | 0.014708 | 0.9773 | -0.15965 | 0.97743 | -0.15874 | 5.4475
132 | -0.011187 | -0.0028032 | 0.011189 | 0.0028038 | 1.8964e-06 | 5.9804e-07 | 0.01703 | 0.01703 | 0.01703 | 0.97743 | -0.15874 | 0.9776 | -0.15752 | 6.3075
133 | -0.0045065 | -0.0011294 | 0.004507 | 0.0011294 | 4.6987e-07 | -1.9319e-08 | 0.0068649 | 0.0068649 | 0.0068649 | 0.97682 | -0.16312 | 0.97693 | -0.16236 | 2.5426
134 | -0.004507 | -0.0011294 | 0.0045088 | 0.0011294 | 1.7869e-06 | -7.39e-08 | 0.0068649 | 0.0068646 | 0.0068649 | 0.97693 | -0.16236 | 0.97733 | -0.1595 | 2.5425
135 | -0.0058855 | -0.0014744 | 0.0058856 | 0.0014744 | 9.9442e-08 | 1.3376e-08 | 0.0089607 | 0.0089607 | 0.0089607 | 0.97733 | -0.1595 | 0.97734 | -0.15937 | 3.3188
136 | -0.0003808 | -9.5438e-05 | 0.0003808 | 9.5323e-05 | 1.8734e-09 | -1.152e-07 | 0.00057473 | 0.00057469 | 0.00057473 | 0.98592 | -0.099006 | 0.98593 | -0.09897 | 0.21286

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.16237 | 0.040734

## res_load
| p_mw | q_mvar
0 | 0.0020631 | 0.00051707
1 | 0.0075113 | 0.0018825
2 | 0.00080195 | 0.00020099
3 | 0.0012989 | 0.00032554
4 | 0.00076168 | 0.00019089
5 | 0.002677 | 0.00067091
6 | 0.0042005 | 0.0010528
7 | 0.00078142 | 0.00019584
8 | 0.0010663 | 0.00026724
9 | 0.0017782 | 0.00044566
10 | 0.0011356 | 0.00028462
11 | 0.0015025 | 0.00037656
12 | 0.0022339 | 0.00055988
13 | 0.0014315 | 0.00035877
14 | 0.00061268 | 0.00015355
15 | 0.002936 | 0.00073582
16 | 0.0011501 | 0.00028824
17 | 0.00065386 | 0.00016387
18 | 0.0078072 | 0.0019567
19 | 0.0011732 | 0.00029403
20 | 0.0011738 | 0.00029418
21 | 0.0075781 | 0.0018992
22 | 0.001893 | 0.00047444
23 | 0.0015918 | 0.00039895
24 | 0.0010534 | 0.000264
25 | 0.0014966 | 0.00037508
26 | 0.0012994 | 0.00032566
27 | 0.00069241 | 0.00017353
28 | 0.00090088 | 0.00022578
29 | 0.0018949 | 0.00047491
30 | 0.0010538 | 0.00026411
31 | 0.0020874 | 0.00052315
32 | 0.0020439 | 0.00051224
33 | 0.0019316 | 0.00048411
34 | 0.00049283 | 0.00012351
35 | 0.0020975 | 0.00052567
36 | 0.00083667 | 0.00020969
37 | 0.0010185 | 0.00025525
38 | 0.0030428 | 0.00076259
39 | 0.0013826 | 0.00034651
40 | 0.0017888 | 0.00044831
41 | 0.001919 | 0.00048095
42 | 0.0012637 | 0.00031671
43 | 0.00074316 | 0.00018625
44 | 0.00074786 | 0.00018743
45 | 0.0021635 | 0.00054222
46 | 0.0031094 | 0.00077929
47 | 0.001915 | 0.00047993
48 | 0.00077704 | 0.00019475
49 | 0.00084328 | 0.00021135
50 | 0.0015626 | 0.00039163
51 | 0.00084365 | 0.00021144
52 | 0.0035178 | 0.00088163
53 | 0.0019539 | 0.0004897
54 | 0.00083354 | 0.00020891
55 | 0.0011315 | 0.00028358
56 | 0.00060599 | 0.00015188
57 | 0.00097148 | 0.00024348
58 | 0.00065334 | 0.00016374
59 | 0.0011854 | 0.00029709
60 | 0.0029541 | 0.00074037
61 | 0.0016079 | 0.00040299
62 | 0.00062263 | 0.00015605
63 | 0.00055601 | 0.00013935
64 | 0.0016425 | 0.00041165
65 | 0.0032283 | 0.00080909
66 | 0.00036581 | 9.1682e-05
67 | 0.00030892 | 7.7421e-05
68 | 0.0025511 | 0.00063936
69 | 0.0010812 | 0.00027098
70 | 0.00090274 | 0.00022625
71 | 0.00076532 | 0.00019181
72 | 0.00063381 | 0.00015885
73 | 0.0013206 | 0.00033097
74 | 0.0004593 | 0.00011511
75 | 0.0049662 | 0.0012447
76 | 0.0029142 | 0.00073037
77 | 0.00035222 | 8.8275e-05
78 | 0.00079186 | 0.00019846
79 | 0.0012376 | 0.00031018
80 | 0.00090351 | 0.00022644
81 | 0.0015425 | 0.00038659
82 | 0.00069651 | 0.00017456
83 | 0.0053548 | 0.001342
84 | 0.0012884 | 0.00032289
85 | 0.0012608 | 0.00031599
86 | 0.0015252 | 0.00038226
87 | 0.0016315 | 0.00040888
88 | 0.0045065 | 0.0011294
89 | 0.0013767 | 0.00034504
90 | 0.0012601 | 0.00031581
91 | 0.0003808 | 9.5438e-05
92 | 0.00038091 | 9.5465e-05
93 | 0.00034357 | 8.6106e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1