## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1032-7_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1032-7_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1032-7_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1032-7_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1032-7_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1032-7_0_3_node_73 | 0.4 | n |  | TRUE
6 | bus_LV_1032-7_0_3_node_83 | 0.4 | n |  | TRUE
7 | bus_LV_1032-7_0_3_node_72 | 0.4 | n |  | TRUE
8 | bus_LV_1032-7_0_3_node_82 | 0.4 | n |  | TRUE
9 | bus_LV_1032-7_0_3_node_35 | 0.4 | n |  | TRUE
10 | bus_LV_1032-7_0_3_node_109 | 0.4 | n |  | TRUE
11 | bus_LV_1032-7_0_3_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_1032-7_0_3_node_108 | 0.4 | n |  | TRUE
13 | bus_LV_1032-7_0_3_node_79 | 0.4 | n |  | TRUE
14 | bus_LV_1032-7_0_3_node_112 | 0.4 | n |  | TRUE
15 | bus_LV_1032-7_0_3_node_41 | 0.4 | n |  | TRUE
16 | bus_LV_1032-7_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1032-7_0_3_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1032-7_0_3_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1032-7_0_3_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1032-7_0_3_node_132 | 0.4 | n |  | TRUE
21 | bus_LV_1032-7_0_3_node_110 | 0.4 | n |  | TRUE
22 | bus_LV_1032-7_0_3_node_111 | 0.4 | n |  | TRUE
23 | bus_LV_1032-7_0_3_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1032-7_0_3_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1032-7_0_3_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1032-7_0_3_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1032-7_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_1032-7_0_3_node_76 | 0.4 | n |  | TRUE
29 | bus_LV_1032-7_0_3_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_1032-7_0_3_node_81 | 0.4 | n |  | TRUE
31 | bus_LV_1032-7_0_3_node_77 | 0.4 | n |  | TRUE
32 | bus_LV_1032-7_0_3_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_1032-7_0_3_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_1032-7_0_3_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_1032-7_0_3_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_1032-7_0_3_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_1032-7_0_3_node_25 | 0.4 | n |  | TRUE
38 | bus_LV_1032-7_0_3_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_1032-7_0_3_node_43 | 0.4 | n |  | TRUE
40 | bus_LV_1032-7_0_3_node_78 | 0.4 | n |  | TRUE
41 | bus_LV_1032-7_0_3_node_80 | 0.4 | n |  | TRUE
42 | bus_LV_1032-7_0_3_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_1032-7_0_3_node_27 | 0.4 | n |  | TRUE
44 | bus_LV_1032-7_0_3_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_1032-7_0_3_node_65 | 0.4 | n |  | TRUE
46 | bus_LV_1032-7_0_3_node_64 | 0.4 | n |  | TRUE
47 | bus_LV_1032-7_0_3_node_102 | 0.4 | n |  | TRUE
48 | bus_LV_1032-7_0_3_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_1032-7_0_3_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_1032-7_0_3_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_1032-7_0_3_node_55 | 0.4 | n |  | TRUE
52 | bus_LV_1032-7_0_3_node_95 | 0.4 | n |  | TRUE
53 | bus_LV_1032-7_0_3_node_36 | 0.4 | n |  | TRUE
54 | bus_LV_1032-7_0_3_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_1032-7_0_3_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_1032-7_0_3_node_39 | 0.4 | n |  | TRUE
57 | bus_LV_1032-7_0_3_node_40 | 0.4 | n |  | TRUE
58 | bus_LV_1032-7_0_3_node_61 | 0.4 | n |  | TRUE
59 | bus_LV_1032-7_0_3_node_54 | 0.4 | n |  | TRUE
60 | bus_LV_1032-7_0_3_node_62 | 0.4 | n |  | TRUE
61 | bus_LV_1032-7_0_3_node_51 | 0.4 | n |  | TRUE
62 | bus_LV_1032-7_0_3_node_88 | 0.4 | n |  | TRUE
63 | bus_LV_1032-7_0_3_node_49 | 0.4 | n |  | TRUE
64 | bus_LV_1032-7_0_3_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_1032-7_0_3_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_1032-7_0_3_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_1032-7_0_3_node_86 | 0.4 | n |  | TRUE
68 | bus_LV_1032-7_0_3_node_87 | 0.4 | n |  | TRUE
69 | bus_LV_1032-7_0_3_node_84 | 0.4 | n |  | TRUE
70 | bus_LV_1032-7_0_3_node_96 | 0.4 | n |  | TRUE
71 | bus_LV_1032-7_0_3_node_56 | 0.4 | n |  | TRUE
72 | bus_LV_1032-7_0_3_node_57 | 0.4 | n |  | TRUE
73 | bus_LV_1032-7_0_3_node_58 | 0.4 | n |  | TRUE
74 | bus_LV_1032-7_0_3_node_59 | 0.4 | n |  | TRUE
75 | bus_LV_1032-7_0_3_node_60 | 0.4 | n |  | TRUE
76 | bus_LV_1032-7_0_3_node_71 | 0.4 | n |  | TRUE
77 | bus_LV_1032-7_0_3_node_100 | 0.4 | n |  | TRUE
78 | bus_LV_1032-7_0_3_node_98 | 0.4 | n |  | TRUE
79 | bus_LV_1032-7_0_3_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_1032-7_0_3_node_66 | 0.4 | n |  | TRUE
81 | bus_LV_1032-7_0_3_node_67 | 0.4 | n |  | TRUE
82 | bus_LV_1032-7_0_3_node_68 | 0.4 | n |  | TRUE
83 | bus_LV_1032-7_0_3_node_69 | 0.4 | n |  | TRUE
84 | bus_LV_1032-7_0_3_node_70 | 0.4 | n |  | TRUE
85 | bus_LV_1032-7_0_3_node_131 | 0.4 | n |  | TRUE
86 | bus_LV_1032-7_0_3_node_122 | 0.4 | n |  | TRUE
87 | bus_LV_1032-7_0_3_node_74 | 0.4 | n |  | TRUE
88 | bus_LV_1032-7_0_3_node_75 | 0.4 | n |  | TRUE
89 | bus_LV_1032-7_0_3_node_93 | 0.4 | n |  | TRUE
90 | bus_LV_1032-7_0_3_node_94 | 0.4 | n |  | TRUE
91 | bus_LV_1032-7_0_3_node_91 | 0.4 | n |  | TRUE
92 | bus_LV_1032-7_0_3_node_130 | 0.4 | n |  | TRUE
93 | bus_LV_1032-7_0_3_node_113 | 0.4 | n |  | TRUE
94 | bus_LV_1032-7_0_3_node_89 | 0.4 | n |  | TRUE
95 | bus_LV_1032-7_0_3_node_85 | 0.4 | n |  | TRUE
96 | bus_LV_1032-7_0_3_node_90 | 0.4 | n |  | TRUE
97 | bus_LV_1032-7_0_3_node_117 | 0.4 | n |  | TRUE
98 | bus_LV_1032-7_0_3_node_92 | 0.4 | n |  | TRUE
99 | bus_LV_1032-7_0_3_node_97 | 0.4 | n |  | TRUE
100 | bus_LV_1032-7_0_3_node_119 | 0.4 | n |  | TRUE
101 | bus_LV_1032-7_0_3_node_116 | 0.4 | n |  | TRUE
102 | bus_LV_1032-7_0_3_node_99 | 0.4 | n |  | TRUE
103 | bus_LV_1032-7_0_3_node_101 | 0.4 | n |  | TRUE
104 | bus_LV_1032-7_0_3_node_121 | 0.4 | n |  | TRUE
105 | bus_LV_1032-7_0_3_node_103 | 0.4 | n |  | TRUE
106 | bus_LV_1032-7_0_3_node_104 | 0.4 | n |  | TRUE
107 | bus_LV_1032-7_0_3_node_105 | 0.4 | n |  | TRUE
108 | bus_LV_1032-7_0_3_node_106 | 0.4 | n |  | TRUE
109 | bus_LV_1032-7_0_3_node_107 | 0.4 | n |  | TRUE
110 | bus_LV_1032-7_0_3_node_129 | 0.4 | n |  | TRUE
111 | bus_LV_1032-7_0_3_node_114 | 0.4 | n |  | TRUE
112 | bus_LV_1032-7_0_3_node_115 | 0.4 | n |  | TRUE
113 | bus_LV_1032-7_0_3_node_120 | 0.4 | n |  | TRUE
114 | bus_MV_353_1_node_184 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1032-7_0_3_load_0 | 0 | 0.0013241 | 0.00033185 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1032-7_0_3_load_1 | 1 | 0.00089781 | 0.00022501 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1032-7_0_3_load_2 | 2 | 0.0010957 | 0.00027461 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1032-7_0_3_load_3 | 3 | 0.0013382 | 0.0003354 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1032-7_0_3_load_4 | 4 | 0.0039407 | 0.00098764 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1032-7_0_3_load_73 | 5 | 0.00089799 | 0.00022506 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1032-7_0_3_load_83 | 6 | 0.0047924 | 0.0012011 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1032-7_0_3_load_72 | 7 | 0.00089798 | 0.00022506 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1032-7_0_3_load_82 | 8 | 0.0017702 | 0.00044366 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1032-7_0_3_load_35 | 9 | 0.00043805 | 0.00010979 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1032-7_0_3_load_109 | 10 | 0.00037047 | 9.2849e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1032-7_0_3_load_33 | 11 | 0.00053072 | 0.00013301 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1032-7_0_3_load_108 | 12 | 0.0035389 | 0.00088692 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1032-7_0_3_load_79 | 13 | 0.00050064 | 0.00012547 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1032-7_0_3_load_112 | 14 | 0.0017521 | 0.00043913 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1032-7_0_3_load_41 | 15 | 0.00030376 | 7.6129e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1032-7_0_3_load_12 | 16 | 0.012293 | 0.003081 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1032-7_0_3_load_13 | 17 | 0.00057743 | 0.00014472 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1032-7_0_3_load_132 | 20 | 0.00074121 | 0.00018577 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1032-7_0_3_load_110 | 21 | 0.0035126 | 0.00088035 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1032-7_0_3_load_111 | 22 | 0.0037094 | 0.00092966 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1032-7_0_3_load_16 | 23 | 0.0029375 | 0.0007362 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1032-7_0_3_load_17 | 24 | 0.0015057 | 0.00037737 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1032-7_0_3_load_19 | 25 | 0.0014149 | 0.00035461 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1032-7_0_3_load_18 | 26 | 0.0019174 | 0.00048054 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1032-7_0_3_load_76 | 28 | 0.0014095 | 0.00035325 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1032-7_0_3_load_28 | 29 | 0.0024401 | 0.00061154 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1032-7_0_3_load_81 | 30 | 0.0035199 | 0.00088217 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1032-7_0_3_load_77 | 31 | 0.0021267 | 0.000533 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1032-7_0_3_load_26 | 32 | 0.0029452 | 0.00073813 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1032-7_0_3_load_21 | 33 | 0.0078894 | 0.0019773 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1032-7_0_3_load_22 | 34 | 0.0011457 | 0.00028713 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1032-7_0_3_load_23 | 35 | 0.0038733 | 0.00097074 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1032-7_0_3_load_24 | 36 | 0.00056574 | 0.00014179 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1032-7_0_3_load_25 | 37 | 0.00059351 | 0.00014875 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1032-7_0_3_load_30 | 38 | 0.0011873 | 0.00029757 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1032-7_0_3_load_78 | 40 | 0.00076088 | 0.00019069 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1032-7_0_3_load_42 | 42 | 0.00094618 | 0.00023714 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1032-7_0_3_load_27 | 43 | 0.0038241 | 0.00095842 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1032-7_0_3_load_29 | 44 | 0.0029454 | 0.00073818 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1032-7_0_3_load_65 | 45 | 0.0023497 | 0.00058889 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1032-7_0_3_load_64 | 46 | 0.0025566 | 0.00064075 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1032-7_0_3_load_31 | 48 | 0.00033227 | 8.3275e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1032-7_0_3_load_32 | 49 | 0.0023058 | 0.00057788 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1032-7_0_3_load_34 | 50 | 0.00041583 | 0.00010422 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1032-7_0_3_load_55 | 51 | 0.0022539 | 0.00056487 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1032-7_0_3_load_95 | 52 | 0.00037907 | 9.5005e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1032-7_0_3_load_36 | 53 | 0.0019927 | 0.00049941 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1032-7_0_3_load_37 | 54 | 0.0017582 | 0.00044064 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1032-7_0_3_load_39 | 56 | 0.0018728 | 0.00046936 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1032-7_0_3_load_40 | 57 | 0.0018371 | 0.00046041 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1032-7_0_3_load_61 | 58 | 0.001823 | 0.00045688 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1032-7_0_3_load_54 | 59 | 0.0017832 | 0.00044692 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1032-7_0_3_load_62 | 60 | 0.0018964 | 0.00047529 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1032-7_0_3_load_88 | 62 | 0.0015747 | 0.00039465 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1032-7_0_3_load_49 | 63 | 0.00092776 | 0.00023252 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1032-7_0_3_load_50 | 64 | 0.00095632 | 0.00023968 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1032-7_0_3_load_52 | 65 | 0.00088832 | 0.00022263 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1032-7_0_3_load_53 | 66 | 0.00092405 | 0.00023159 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1032-7_0_3_load_86 | 67 | 0.0011532 | 0.00028903 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1032-7_0_3_load_87 | 68 | 0.00097731 | 0.00024494 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1032-7_0_3_load_84 | 69 | 0.00098309 | 0.00024638 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1032-7_0_3_load_96 | 70 | 0.0034865 | 0.0008738 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1032-7_0_3_load_56 | 71 | 0.00053529 | 0.00013416 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1032-7_0_3_load_57 | 72 | 0.00083068 | 0.00020819 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1032-7_0_3_load_59 | 74 | 0.0005188 | 0.00013002 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1032-7_0_3_load_60 | 75 | 0.0016188 | 0.00040572 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1032-7_0_3_load_71 | 76 | 0.0011958 | 0.0002997 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1032-7_0_3_load_98 | 78 | 0.0018281 | 0.00045817 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1032-7_0_3_load_63 | 79 | 0.0020806 | 0.00052145 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1032-7_0_3_load_67 | 81 | 0.0017032 | 0.00042685 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1032-7_0_3_load_68 | 82 | 0.0050523 | 0.0012662 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1032-7_0_3_load_70 | 84 | 0.00034041 | 8.5314e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1032-7_0_3_load_131 | 85 | 0.00054306 | 0.0001361 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1032-7_0_3_load_74 | 87 | 0.0019375 | 0.00048558 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1032-7_0_3_load_75 | 88 | 0.0018858 | 0.00047262 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1032-7_0_3_load_94 | 90 | 0.0025994 | 0.00065148 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1032-7_0_3_load_91 | 91 | 0.0017212 | 0.00043139 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1032-7_0_3_load_130 | 92 | 0.0020858 | 0.00052275 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1032-7_0_3_load_113 | 93 | 0.0027098 | 0.00067914 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1032-7_0_3_load_89 | 94 | 0.001979 | 0.00049599 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1032-7_0_3_load_85 | 95 | 0.0011565 | 0.00028985 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1032-7_0_3_load_90 | 96 | 0.0012706 | 0.00031844 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1032-7_0_3_load_117 | 97 | 0.00038633 | 9.6824e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1032-7_0_3_load_92 | 98 | 0.00067521 | 0.00016922 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1032-7_0_3_load_97 | 99 | 0.0032481 | 0.00081406 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1032-7_0_3_load_119 | 100 | 0.0035683 | 0.00089429 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1032-7_0_3_load_99 | 102 | 0.0011938 | 0.0002992 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1032-7_0_3_load_101 | 103 | 0.00032888 | 8.2425e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1032-7_0_3_load_121 | 104 | 0.00035771 | 8.9651e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1032-7_0_3_load_103 | 105 | 0.0059287 | 0.0014859 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1032-7_0_3_load_104 | 106 | 0.003833 | 0.00096064 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1032-7_0_3_load_105 | 107 | 0.0035286 | 0.00088434 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1032-7_0_3_load_106 | 108 | 0.0037203 | 0.00093239 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1032-7_0_3_load_107 | 109 | 0.0033503 | 0.00083966 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1032-7_0_3_load_129 | 110 | 0.0032551 | 0.00081581 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1032-7_0_3_load_114 | 111 | 0.0018445 | 0.00046228 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1032-7_0_3_load_115 | 112 | 0.0018435 | 0.00046204 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1032-7_0_3_load_120 | 113 | 0.00091151 | 0.00022844 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1032-7_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.00044926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1032-7_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.017617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1032-7_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.011483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1032-7_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.029126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1032-7_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0040054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1032-7_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.015598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1032-7_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.020107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1032-7_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.0059645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1032-7_0_3_line_8 | NAYY 4x150 SE | 7 | 87 | 0.003242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1032-7_0_3_line_9 | NAYY 4x150 SE | 8 | 30 | 0.028531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1032-7_0_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.0332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1032-7_0_3_line_11 | NAYY 4x150 SE | 9 | 11 | 0.00075957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1032-7_0_3_line_12 | NAYY 4x150 SE | 10 | 12 | 0.0045683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1032-7_0_3_line_13 | NAYY 4x150 SE | 11 | 48 | 0.021306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1032-7_0_3_line_14 | NAYY 4x150 SE | 12 | 21 | 0.023313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1032-7_0_3_line_15 | NAYY 4x150 SE | 12 | 19 | 0.03622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1032-7_0_3_line_16 | NAYY 4x150 SE | 13 | 14 | 0.041788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1032-7_0_3_line_17 | NAYY 4x150 SE | 13 | 15 | 0.077562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1032-7_0_3_line_18 | NAYY 4x150 SE | 14 | 93 | 0.024563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1032-7_0_3_line_19 | NAYY 4x150 SE | 14 | 90 | 0.020358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1032-7_0_3_line_20 | NAYY 4x150 SE | 15 | 42 | 0.008167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1032-7_0_3_line_21 | NAYY 4x150 SE | 16 | 17 | 0.014663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1032-7_0_3_line_22 | NAYY 4x150 SE | 16 | 18 | 0.042895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1032-7_0_3_line_23 | NAYY 4x150 SE | 17 | 19 | 0.01751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1032-7_0_3_line_24 | NAYY 4x150 SE | 18 | 20 | 0.083062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1032-7_0_3_line_25 | NAYY 4x150 SE | 21 | 22 | 0.018234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1032-7_0_3_line_26 | NAYY 4x150 SE | 22 | 93 | 0.0078421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1032-7_0_3_line_27 | NAYY 4x150 SE | 23 | 24 | 0.019846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1032-7_0_3_line_28 | NAYY 4x150 SE | 24 | 25 | 0.0038522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1032-7_0_3_line_29 | NAYY 4x150 SE | 25 | 28 | 0.0054927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1032-7_0_3_line_30 | NAYY 4x150 SE | 26 | 27 | 0.016379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1032-7_0_3_line_31 | NAYY 4x150 SE | 27 | 29 | 0.022545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1032-7_0_3_line_32 | NAYY 4x150 SE | 27 | 30 | 0.0079933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1032-7_0_3_line_33 | NAYY 4x150 SE | 28 | 31 | 0.0061252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1032-7_0_3_line_34 | NAYY 4x150 SE | 29 | 32 | 0.0015217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1032-7_0_3_line_35 | NAYY 4x150 SE | 31 | 65 | 0.0036874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1032-7_0_3_line_36 | NAYY 4x150 SE | 32 | 43 | 0.027885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1032-7_0_3_line_37 | NAYY 4x150 SE | 33 | 34 | 0.021213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1032-7_0_3_line_38 | NAYY 4x150 SE | 33 | 35 | 0.0057395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1032-7_0_3_line_39 | NAYY 4x150 SE | 34 | 36 | 0.024397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1032-7_0_3_line_40 | NAYY 4x150 SE | 35 | 37 | 0.0072837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1032-7_0_3_line_41 | NAYY 4x150 SE | 36 | 38 | 0.01248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1032-7_0_3_line_42 | NAYY 4x150 SE | 37 | 39 | 0.025539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1032-7_0_3_line_43 | NAYY 4x150 SE | 38 | 40 | 0.034708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1032-7_0_3_line_44 | NAYY 4x150 SE | 39 | 41 | 0.028291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1032-7_0_3_line_45 | NAYY 4x150 SE | 39 | 42 | 0.040024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1032-7_0_3_line_46 | NAYY 4x150 SE | 40 | 47 | 0.015942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1032-7_0_3_line_47 | NAYY 4x150 SE | 41 | 62 | 0.038642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1032-7_0_3_line_48 | NAYY 4x150 SE | 43 | 44 | 0.0028698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1032-7_0_3_line_49 | NAYY 4x150 SE | 44 | 45 | 0.028466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1032-7_0_3_line_50 | NAYY 4x150 SE | 45 | 46 | 0.0044671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1032-7_0_3_line_51 | NAYY 4x150 SE | 46 | 80 | 0.012196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1032-7_0_3_line_52 | NAYY 4x150 SE | 47 | 92 | 0.016706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1032-7_0_3_line_53 | NAYY 4x150 SE | 47 | 77 | 0.005525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1032-7_0_3_line_54 | NAYY 4x150 SE | 48 | 49 | 0.015659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1032-7_0_3_line_55 | NAYY 4x150 SE | 49 | 50 | 0.010928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1032-7_0_3_line_56 | NAYY 4x150 SE | 50 | 51 | 0.012472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1032-7_0_3_line_57 | NAYY 4x150 SE | 51 | 52 | 0.01445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1032-7_0_3_line_58 | NAYY 4x150 SE | 52 | 70 | 0.0095922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1032-7_0_3_line_59 | NAYY 4x150 SE | 53 | 54 | 0.015195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1032-7_0_3_line_60 | NAYY 4x150 SE | 53 | 55 | 0.0084727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1032-7_0_3_line_61 | NAYY 4x150 SE | 55 | 56 | 0.0070064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1032-7_0_3_line_62 | NAYY 4x150 SE | 55 | 57 | 0.013869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1032-7_0_3_line_63 | NAYY 4x150 SE | 56 | 58 | 0.015092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1032-7_0_3_line_64 | NAYY 4x150 SE | 57 | 59 | 0.00045188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1032-7_0_3_line_65 | NAYY 4x150 SE | 58 | 60 | 0.00061327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1032-7_0_3_line_66 | NAYY 4x150 SE | 59 | 61 | 0.014036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1032-7_0_3_line_67 | NAYY 4x150 SE | 60 | 79 | 0.0076837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1032-7_0_3_line_68 | NAYY 4x150 SE | 61 | 66 | 0.010493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1032-7_0_3_line_69 | NAYY 4x150 SE | 61 | 63 | 0.0058923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1032-7_0_3_line_70 | NAYY 4x150 SE | 62 | 94 | 0.062603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1032-7_0_3_line_71 | NAYY 4x150 SE | 63 | 64 | 0.014843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1032-7_0_3_line_72 | NAYY 4x150 SE | 64 | 65 | 0.016045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1032-7_0_3_line_73 | NAYY 4x150 SE | 66 | 67 | 0.024146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1032-7_0_3_line_74 | NAYY 4x150 SE | 67 | 68 | 0.013451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1032-7_0_3_line_75 | NAYY 4x150 SE | 67 | 69 | 0.015354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1032-7_0_3_line_76 | NAYY 4x150 SE | 68 | 81 | 0.014447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1032-7_0_3_line_77 | NAYY 4x150 SE | 69 | 95 | 0.0040865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1032-7_0_3_line_78 | NAYY 4x150 SE | 70 | 99 | 0.018803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1032-7_0_3_line_79 | NAYY 4x150 SE | 71 | 72 | 0.019582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1032-7_0_3_line_80 | NAYY 4x150 SE | 71 | 73 | 0.04105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1032-7_0_3_line_81 | NAYY 4x150 SE | 73 | 74 | 0.011162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1032-7_0_3_line_82 | NAYY 4x150 SE | 73 | 75 | 0.016835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1032-7_0_3_line_83 | NAYY 4x150 SE | 74 | 76 | 0.028863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1032-7_0_3_line_84 | NAYY 4x150 SE | 75 | 77 | 0.019321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1032-7_0_3_line_85 | NAYY 4x150 SE | 77 | 78 | 0.025612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1032-7_0_3_line_86 | NAYY 4x150 SE | 78 | 102 | 0.0072633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1032-7_0_3_line_87 | NAYY 4x150 SE | 80 | 81 | 0.044977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1032-7_0_3_line_88 | NAYY 4x150 SE | 82 | 83 | 0.026773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1032-7_0_3_line_89 | NAYY 4x150 SE | 83 | 84 | 0.037673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1032-7_0_3_line_90 | NAYY 4x150 SE | 84 | 85 | 0.014962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1032-7_0_3_line_91 | NAYY 4x150 SE | 85 | 86 | 0.038417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1032-7_0_3_line_92 | NAYY 4x150 SE | 86 | 104 | 0.023028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1032-7_0_3_line_93 | NAYY 4x150 SE | 86 | 103 | 0.034154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1032-7_0_3_line_94 | NAYY 4x150 SE | 87 | 88 | 0.010539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
95 | LV_1032-7_0_3_line_95 | NAYY 4x150 SE | 88 | 89 | 0.018386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
96 | LV_1032-7_0_3_line_96 | NAYY 4x150 SE | 89 | 90 | 0.020045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
97 | LV_1032-7_0_3_line_97 | NAYY 4x150 SE | 89 | 91 | 0.016648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1032-7_0_3_line_98 | NAYY 4x150 SE | 91 | 98 | 0.0013689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1032-7_0_3_line_99 | NAYY 4x150 SE | 94 | 96 | 0.035444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1032-7_0_3_line_100 | NAYY 4x150 SE | 96 | 97 | 0.024158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1032-7_0_3_line_101 | NAYY 4x150 SE | 99 | 100 | 0.010405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1032-7_0_3_line_102 | NAYY 4x150 SE | 100 | 101 | 0.023575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1032-7_0_3_line_103 | NAYY 4x150 SE | 101 | 112 | 0.065622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1032-7_0_3_line_104 | NAYY 4x150 SE | 102 | 103 | 0.013965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1032-7_0_3_line_105 | NAYY 4x150 SE | 104 | 113 | 0.029846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1032-7_0_3_line_106 | NAYY 4x150 SE | 105 | 106 | 0.01455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1032-7_0_3_line_107 | NAYY 4x150 SE | 105 | 107 | 0.020244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1032-7_0_3_line_108 | NAYY 4x150 SE | 106 | 108 | 0.00088667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1032-7_0_3_line_109 | NAYY 4x150 SE | 107 | 109 | 0.011261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1032-7_0_3_line_110 | NAYY 4x150 SE | 108 | 110 | 0.024623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1032-7_0_3_line_111 | NAYY 4x150 SE | 109 | 111 | 0.033048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1032-7_0_3_line_112 | NAYY 4x150 SE | 111 | 112 | 0.0133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1032-7_0_3_trafo_72 | 0.25 MVA 20/0.4 kV | 114 | 7 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2666428.2 | 1226144.185 | 2666428.192 | 1226143.7358
1 | 2666428.192 | 1226143.7358 | 2666428.0825 | 1226137.5764 | 2666429.1483 | 1226126.9925 | 2666429.3018 | 1226126.1881
2 | 2666428.7313 | 1226155.648 | 2666428.3246 | 1226151.199 | 2666428.2 | 1226144.185
3 | 2666440.641 | 1226100.4258 | 2666436.9885 | 1226103.7094 | 2666433.7858 | 1226107.4428 | 2666431.145 | 1226116.5303 | 2666429.3018 | 1226126.1881
4 | 2666428.7313 | 1226155.648 | 2666429.096 | 1226159.6368
5 | 2666440.641 | 1226100.4258 | 2666440.641 | 1226100.4258 | 2666445.7897 | 1226098.9157 | 2666450.986 | 1226098.5734 | 2666455.8427 | 1226099.8606
6 | 2666429.6226 | 1226179.6614 | 2666430.2701 | 1226172.479 | 2666429.096 | 1226159.6368
7 | 2666461.4832 | 1226101.7971 | 2666456.1102 | 1226099.9315 | 2666455.8427 | 1226099.8606
8 | 2666429.6226 | 1226179.6614 | 2666429.3316 | 1226182.8903
9 | 2666488.4358 | 1226111.1553 | 2666461.4832 | 1226101.7971
10 | 2666371.4367 | 1226101.3246 | 2666373.3231 | 1226085.9433 | 2666378.1773 | 1226068.9182
11 | 2666378.1773 | 1226068.9182 | 2666378.3856 | 1226068.1877
12 | 2666370.8806 | 1226105.8589 | 2666371.4367 | 1226101.3246
13 | 2666384.9266 | 1226047.9405 | 2666382.4113 | 1226054.0684 | 2666378.3856 | 1226068.1877
14 | 2666370.8806 | 1226105.8589 | 2666369.5456 | 1226116.7433 | 2666369.5585 | 1226129.0902
15 | 2666370.8806 | 1226105.8589 | 2666334.6604 | 1226105.9586
16 | 2666373.1468 | 1226179.558 | 2666342.6526 | 1226208.1295
17 | 2666342.6526 | 1226208.1295 | 2666320.1325 | 1226282.3497
18 | 2666373.1468 | 1226179.558 | 2666370.8063 | 1226155.1072
19 | 2666387.5749 | 1226192.2683 | 2666383.345 | 1226191.1676 | 2666377.437 | 1226187.3659 | 2666373.2043 | 1226180.1585 | 2666373.1468 | 1226179.558
20 | 2666320.1325 | 1226282.3497 | 2666322.836 | 1226290.0562
21 | 2666302.6351 | 1226108.9085 | 2666306.6259 | 1226108.2477 | 2666317.209 | 1226107.3836
22 | 2666260.3162 | 1226115.9148 | 2666302.6351 | 1226108.9085
23 | 2666334.6604 | 1226105.9586 | 2666317.209 | 1226107.3836
24 | 2666260.3162 | 1226115.9148 | 2666236.9588 | 1226036.2044
25 | 2666370.059 | 1226147.3008 | 2666369.5722 | 1226142.2157 | 2666369.5585 | 1226129.0902
26 | 2666370.8063 | 1226155.1072 | 2666370.059 | 1226147.3008
27 | 2666492.0274 | 1226180.1445 | 2666491.2713 | 1226187.7477 | 2666492.2829 | 1226194.897 | 2666494.6067 | 1226199.3067
28 | 2666496.4025 | 1226202.7147 | 2666496.4025 | 1226202.7147 | 2666494.6067 | 1226199.3067
29 | 2666501.4112 | 1226204.9691 | 2666496.4025 | 1226202.7147
30 | 2666495.8773 | 1226114.0736 | 2666495.427 | 1226122.4852 | 2666495.3381 | 1226130.4401
31 | 2666495.8773 | 1226114.0736 | 2666511.1727 | 1226118.9588 | 2666517.3949 | 1226120.7999
32 | 2666495.8773 | 1226114.0736 | 2666488.4358 | 1226111.1553 | 2666488.4358 | 1226111.1553
33 | 2666501.4112 | 1226204.9691 | 2666502.7606 | 1226205.5765 | 2666507.3756 | 1226206.1078
34 | 2666518.8541 | 1226121.2316 | 2666517.3949 | 1226120.7999
35 | 2666511.0388 | 1226206.5296 | 2666507.3756 | 1226206.1078
36 | 2666518.8541 | 1226121.2316 | 2666545.5933 | 1226129.1435
37 | 2666354.9294 | 1226374.6177 | 2666353.853 | 1226359.4923 | 2666353.4241 | 1226353.4579
38 | 2666353.0172 | 1226347.7328 | 2666353.4241 | 1226353.4579
39 | 2666354.9294 | 1226374.6177 | 2666356.6612 | 1226398.9527
40 | 2666353.0172 | 1226347.7328 | 2666352.5008 | 1226340.4674
41 | 2666356.6612 | 1226398.9527 | 2666356.7821 | 1226400.6516 | 2666356.0369 | 1226411.4023
42 | 2666350.8096 | 1226314.9851 | 2666351.7565 | 1226329.9942 | 2666352.5008 | 1226340.4674
43 | 2666356.0369 | 1226411.4023 | 2666354.7405 | 1226430.1035 | 2666352.312 | 1226445.8798
44 | 2666378.7098 | 1226310.382 | 2666359.3409 | 1226314.6466 | 2666350.8096 | 1226314.9851
45 | 2666350.8096 | 1226314.9851 | 2666340.0657 | 1226308.4611 | 2666328.3232 | 1226303.805 | 2666325.7535 | 1226298.3728 | 2666322.836 | 1226290.0562
46 | 2666349.8864 | 1226461.6365 | 2666352.312 | 1226445.8798
47 | 2666378.7098 | 1226310.382 | 2666391.4727 | 1226309.8685 | 2666405.2844 | 1226311.1345 | 2666417.0763 | 1226313.3538
48 | 2666545.5933 | 1226129.1435 | 2666548.3452 | 1226129.9578
49 | 2666548.3452 | 1226129.9578 | 2666575.6418 | 1226138.0346
50 | 2666579.9253 | 1226139.302 | 2666575.6418 | 1226138.0346
51 | 2666591.6206 | 1226142.7625 | 2666579.9253 | 1226139.302
52 | 2666349.8864 | 1226461.6365 | 2666333.2996 | 1226459.6458
53 | 2666348.6741 | 1226467.0264 | 2666349.8864 | 1226461.6365
54 | 2666384.9266 | 1226047.9405 | 2666390.8729 | 1226033.4541
55 | 2666390.8729 | 1226033.4541 | 2666395.0224 | 1226023.345
56 | 2666399.7584 | 1226011.8073 | 2666395.0224 | 1226023.345
57 | 2666405.2453 | 1225998.4399 | 2666399.7584 | 1226011.8073
58 | 2666405.2453 | 1225998.4399 | 2666408.8878 | 1225989.5662
59 | 2666558.1678 | 1226183.6132 | 2666573.2223 | 1226185.673
60 | 2666549.7733 | 1226182.4647 | 2666558.1678 | 1226183.6132
61 | 2666549.7733 | 1226182.4647 | 2666542.8315 | 1226181.5157
62 | 2666549.7733 | 1226182.4647 | 2666548.6993 | 1226196.2915
63 | 2666527.8785 | 1226179.4715 | 2666542.8315 | 1226181.5157
64 | 2666548.6643 | 1226196.7421 | 2666548.6993 | 1226196.2915
65 | 2666527.2709 | 1226179.3884 | 2666527.8785 | 1226179.4715
66 | 2666547.5772 | 1226210.7362 | 2666548.6643 | 1226196.7421
67 | 2666519.6579 | 1226178.3476 | 2666527.2709 | 1226179.3884
68 | 2666547.5772 | 1226210.7362 | 2666557.9742 | 1226212.1528
69 | 2666547.5772 | 1226210.7362 | 2666541.7236 | 1226210.0623
70 | 2666417.0763 | 1226313.3538 | 2666428.7709 | 1226315.5549 | 2666436.3209 | 1226317.5627 | 2666447.0387 | 1226322.341 | 2666474.6726 | 1226336.7314
71 | 2666541.7236 | 1226210.0623 | 2666526.9781 | 1226208.3647
72 | 2666511.0388 | 1226206.5296 | 2666526.9781 | 1226208.3647
73 | 2666581.9846 | 1226214.6902 | 2666561.2688 | 1226212.6016 | 2666557.9742 | 1226212.1528
74 | 2666581.9846 | 1226214.6902 | 2666582.9092 | 1226201.2714
75 | 2666581.9846 | 1226214.6902 | 2666581.7306 | 1226230.0419
76 | 2666582.9092 | 1226201.2714 | 2666583.9024 | 1226186.8581
77 | 2666581.7306 | 1226230.0419 | 2666581.663 | 1226234.1278
78 | 2666416.0279 | 1225972.1713 | 2666408.8878 | 1225989.5662
79 | 2666420.2708 | 1226449.558 | 2666413.0472 | 1226467.7585
80 | 2666382.8955 | 1226478.6933 | 2666398.6864 | 1226483.9284 | 2666403.2144 | 1226484.3459 | 2666407.9169 | 1226480.6848 | 2666413.0472 | 1226467.7585
81 | 2666382.8955 | 1226478.6933 | 2666385.8166 | 1226467.9201
82 | 2666382.8955 | 1226478.6933 | 2666366.9615 | 1226473.261
83 | 2666393.3699 | 1226440.0629 | 2666385.8166 | 1226467.9201
84 | 2666348.6741 | 1226467.0264 | 2666366.9615 | 1226473.261
85 | 2666348.6741 | 1226467.0264 | 2666342.1784 | 1226491.8006
86 | 2666342.1784 | 1226491.8006 | 2666341.9451 | 1226492.6903 | 2666339.7686 | 1226498.6488
87 | 2666591.6206 | 1226142.7625 | 2666585.3331 | 1226166.0962 | 2666583.9024 | 1226186.8581
88 | 2666268.0539 | 1226616.8588 | 2666251.9243 | 1226638.2272
89 | 2666268.0539 | 1226616.8588 | 2666291.0337 | 1226587.0059
90 | 2666291.0337 | 1226587.0059 | 2666300.1601 | 1226575.1497
91 | 2666320.9127 | 1226542.8773 | 2666306.2396 | 1226567.2519 | 2666300.1601 | 1226575.1497
92 | 2666320.9127 | 1226542.8773 | 2666341.64 | 1226552.9113
93 | 2666320.9127 | 1226542.8773 | 2666333.6654 | 1226515.3572 | 2666334.9771 | 1226511.7661
94 | 2666425.2051 | 1226192.2908 | 2666429.0155 | 1226186.3962 | 2666429.3316 | 1226182.8903
95 | 2666407.3194 | 1226195.3822 | 2666419.6681 | 1226194.6417 | 2666425.2051 | 1226192.2908
96 | 2666407.3194 | 1226195.3822 | 2666394.773 | 1226194.1414 | 2666387.5749 | 1226192.2683
97 | 2666407.3194 | 1226195.3822 | 2666405.1993 | 1226211.8945
98 | 2666405.0249 | 1226213.2522 | 2666405.1993 | 1226211.8945
99 | 2666507.3683 | 1226350.0772 | 2666507.3683 | 1226350.0772 | 2666498.5486 | 1226347.7438 | 2666489.9449 | 1226344.4011 | 2666479.9413 | 1226339.475 | 2666474.6726 | 1226336.7314
100 | 2666531.164 | 1226354.079 | 2666520.405 | 1226352.858 | 2666507.3683 | 1226350.0772
101 | 2666416.0279 | 1225972.1713 | 2666419.9792 | 1225962.5453
102 | 2666428.9312 | 1225940.7362 | 2666419.9792 | 1225962.5453
103 | 2666428.9312 | 1225940.7362 | 2666437.0018 | 1225943.6837 | 2666448.913 | 1225951.6218 | 2666472.2066 | 1225974.7858 | 2666473.2995 | 1225980.7796 | 2666472.7087 | 1225984.5058
104 | 2666334.9771 | 1226511.7661 | 2666339.7686 | 1226498.6488
105 | 2666370.0433 | 1226561.9358 | 2666351.8401 | 1226556.9422 | 2666342.3762 | 1226553.2677 | 2666341.64 | 1226552.9113
106 | 2666474.1437 | 1226043.6186 | 2666477.7147 | 1226039.4892 | 2666482.1095 | 1226031.5311
107 | 2666474.1437 | 1226043.6186 | 2666474.1437 | 1226043.6186 | 2666469.0558 | 1226045.1072 | 2666461.7995 | 1226043.9254 | 2666458.0897 | 1226040.8042 | 2666456.9271 | 1226038.32
108 | 2666482.5381 | 1226030.7549 | 2666482.1095 | 1226031.5311
109 | 2666456.9271 | 1226038.32 | 2666455.5058 | 1226035.2829 | 2666455.3743 | 1226027.3763 | 2666455.3743 | 1226027.3763
110 | 2666495.5146 | 1226009.8814 | 2666489.4129 | 1226018.3061 | 2666482.5381 | 1226030.7549
111 | 2666468.3721 | 1225996.9921 | 2666455.3743 | 1226027.3763
112 | 2666472.7087 | 1225984.5058 | 2666472.117 | 1225988.2379 | 2666468.3721 | 1225996.9921

## bus_geodata
| x | y | coords
0 | 2666428.192 | 1226143.7358
1 | 2666428.2 | 1226144.185
2 | 2666429.3018 | 1226126.1881
3 | 2666428.7313 | 1226155.648
4 | 2666440.641 | 1226100.4258
5 | 2666429.096 | 1226159.6368
6 | 2666455.8427 | 1226099.8606
7 | 2666429.6226 | 1226179.6614
8 | 2666461.4832 | 1226101.7971
9 | 2666378.1773 | 1226068.9182
10 | 2666371.4367 | 1226101.3246
11 | 2666378.3856 | 1226068.1877
12 | 2666370.8806 | 1226105.8589
13 | 2666342.6526 | 1226208.1295
14 | 2666373.1468 | 1226179.558
15 | 2666320.1325 | 1226282.3497
16 | 2666302.6351 | 1226108.9085
17 | 2666317.209 | 1226107.3836
18 | 2666260.3162 | 1226115.9148
19 | 2666334.6604 | 1226105.9586
20 | 2666236.9588 | 1226036.2044
21 | 2666369.5585 | 1226129.0902
22 | 2666370.059 | 1226147.3008
23 | 2666492.0274 | 1226180.1445
24 | 2666494.6067 | 1226199.3067
25 | 2666496.4025 | 1226202.7147
26 | 2666495.3381 | 1226130.4401
27 | 2666495.8773 | 1226114.0736
28 | 2666501.4112 | 1226204.9691
29 | 2666517.3949 | 1226120.7999
30 | 2666488.4358 | 1226111.1553
31 | 2666507.3756 | 1226206.1078
32 | 2666518.8541 | 1226121.2316
33 | 2666353.4241 | 1226353.4579
34 | 2666354.9294 | 1226374.6177
35 | 2666353.0172 | 1226347.7328
36 | 2666356.6612 | 1226398.9527
37 | 2666352.5008 | 1226340.4674
38 | 2666356.0369 | 1226411.4023
39 | 2666350.8096 | 1226314.9851
40 | 2666352.312 | 1226445.8798
41 | 2666378.7098 | 1226310.382
42 | 2666322.836 | 1226290.0562
43 | 2666545.5933 | 1226129.1435
44 | 2666548.3452 | 1226129.9578
45 | 2666575.6418 | 1226138.0346
46 | 2666579.9253 | 1226139.302
47 | 2666349.8864 | 1226461.6365
48 | 2666384.9266 | 1226047.9405
49 | 2666390.8729 | 1226033.4541
50 | 2666395.0224 | 1226023.345
51 | 2666399.7584 | 1226011.8073
52 | 2666405.2453 | 1225998.4399
53 | 2666558.1678 | 1226183.6132
54 | 2666573.2223 | 1226185.673
55 | 2666549.7733 | 1226182.4647
56 | 2666542.8315 | 1226181.5157
57 | 2666548.6993 | 1226196.2915
58 | 2666527.8785 | 1226179.4715
59 | 2666548.6643 | 1226196.7421
60 | 2666527.2709 | 1226179.3884
61 | 2666547.5772 | 1226210.7362
62 | 2666417.0763 | 1226313.3538
63 | 2666541.7236 | 1226210.0623
64 | 2666526.9781 | 1226208.3647
65 | 2666511.0388 | 1226206.5296
66 | 2666557.9742 | 1226212.1528
67 | 2666581.9846 | 1226214.6902
68 | 2666582.9092 | 1226201.2714
69 | 2666581.7306 | 1226230.0419
70 | 2666408.8878 | 1225989.5662
71 | 2666413.0472 | 1226467.7585
72 | 2666420.2708 | 1226449.558
73 | 2666382.8955 | 1226478.6933
74 | 2666385.8166 | 1226467.9201
75 | 2666366.9615 | 1226473.261
76 | 2666393.3699 | 1226440.0629
77 | 2666348.6741 | 1226467.0264
78 | 2666342.1784 | 1226491.8006
79 | 2666519.6579 | 1226178.3476
80 | 2666591.6206 | 1226142.7625
81 | 2666583.9024 | 1226186.8581
82 | 2666251.9243 | 1226638.2272
83 | 2666268.0539 | 1226616.8588
84 | 2666291.0337 | 1226587.0059
85 | 2666300.1601 | 1226575.1497
86 | 2666320.9127 | 1226542.8773
87 | 2666429.3316 | 1226182.8903
88 | 2666425.2051 | 1226192.2908
89 | 2666407.3194 | 1226195.3822
90 | 2666387.5749 | 1226192.2683
91 | 2666405.1993 | 1226211.8945
92 | 2666333.2996 | 1226459.6458
93 | 2666370.8063 | 1226155.1072
94 | 2666474.6726 | 1226336.7314
95 | 2666581.663 | 1226234.1278
96 | 2666507.3683 | 1226350.0772
97 | 2666531.164 | 1226354.079
98 | 2666405.0249 | 1226213.2522
99 | 2666416.0279 | 1225972.1713
100 | 2666419.9792 | 1225962.5453
101 | 2666428.9312 | 1225940.7362
102 | 2666339.7686 | 1226498.6488
103 | 2666334.9771 | 1226511.7661
104 | 2666341.64 | 1226552.9113
105 | 2666474.1437 | 1226043.6186
106 | 2666482.1095 | 1226031.5311
107 | 2666456.9271 | 1226038.32
108 | 2666482.5381 | 1226030.7549
109 | 2666455.3743 | 1226027.3763
110 | 2666495.5146 | 1226009.8814
111 | 2666468.3721 | 1225996.9921
112 | 2666472.7087 | 1225984.5058
113 | 2666370.0433 | 1226561.9358
114 | 2666407.3194 | 1226195.3822

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99624 | -0.025949 | 0.0013241 | 0.00033185
1 | 0.99629 | -0.025635 | 0.00089781 | 0.00022501
2 | 0.99449 | -0.038061 | 0.0010957 | 0.00027461
3 | 0.99746 | -0.017507 | 0.0013382 | 0.0003354
4 | 0.99165 | -0.057855 | 0.0039407 | 0.00098764
5 | 0.99788 | -0.014623 | 0.00089799 | 0.00022506
6 | 0.99022 | -0.067876 | 0.0047924 | 0.0012011
7 | 1 | 0 | -0.19961 | -0.050275
8 | 0.98971 | -0.071424 | 0.0017702 | 0.00044366
9 | 0.98419 | -0.11022 | 0.00043805 | 0.00010979
10 | 0.98634 | -0.0951 | 0.00037047 | 9.2849e-05
11 | 0.98414 | -0.11056 | 0.00053072 | 0.00013301
12 | 0.98663 | -0.093007 | 0.0035389 | 0.00088692
13 | 0.99137 | -0.059851 | 0.00050064 | 0.00012547
14 | 0.99382 | -0.042749 | 0.0017521 | 0.00043913
15 | 0.98688 | -0.091417 | 0.00030376 | 7.6129e-05
16 | 0.9853 | -0.10249 | 0.012293 | 0.003081
17 | 0.98558 | -0.10052 | 0.00057743 | 0.00014472
18 | 0.98525 | -0.10282 | 0 | 0
19 | 0.98592 | -0.098072 | 0 | 0
20 | 0.98517 | -0.10346 | 0.00074121 | 0.00018577
21 | 0.98873 | -0.078258 | 0.0035126 | 0.00088035
22 | 0.99047 | -0.066115 | 0.0037094 | 0.00092966
23 | 0.97463 | -0.17842 | 0.0029375 | 0.0007362
24 | 0.97471 | -0.17781 | 0.0015057 | 0.00037737
25 | 0.97474 | -0.17763 | 0.0014149 | 0.00035461
26 | 0.9867 | -0.092602 | 0.0019174 | 0.00048054
27 | 0.98674 | -0.09228 | 0 | 0
28 | 0.97478 | -0.17729 | 0.0014095 | 0.00035325
29 | 0.98506 | -0.10413 | 0.0024401 | 0.00061154
30 | 0.98736 | -0.08793 | 0.0035199 | 0.00088217
31 | 0.97485 | -0.17683 | 0.0021267 | 0.000533
32 | 0.98495 | -0.1049 | 0.0029452 | 0.00073813
33 | 0.98234 | -0.12362 | 0.0078894 | 0.0019773
34 | 0.9817 | -0.12824 | 0.0011457 | 0.00028713
35 | 0.98259 | -0.1219 | 0.0038733 | 0.00097074
36 | 0.98099 | -0.13327 | 0.00056574 | 0.00014179
37 | 0.98293 | -0.11943 | 0.00059351 | 0.00014875
38 | 0.98064 | -0.13578 | 0.0011873 | 0.00029757
39 | 0.98417 | -0.11063 | 0 | 0
40 | 0.97972 | -0.14232 | 0.00076088 | 0.00019069
41 | 0.98396 | -0.11215 | 0 | 0
42 | 0.98641 | -0.094732 | 0.00094618 | 0.00023714
43 | 0.98309 | -0.11807 | 0.0038241 | 0.00095842
44 | 0.98291 | -0.11931 | 0.0029454 | 0.00073818
45 | 0.98129 | -0.13081 | 0.0023497 | 0.00058889
46 | 0.98105 | -0.13251 | 0.0025566 | 0.00064075
47 | 0.97932 | -0.1452 | 0 | 0
48 | 0.98279 | -0.12009 | 0.00033227 | 8.3275e-05
49 | 0.98181 | -0.12705 | 0.0023058 | 0.00057788
50 | 0.98116 | -0.13166 | 0.00041583 | 0.00010422
51 | 0.98042 | -0.13687 | 0.0022539 | 0.00056487
52 | 0.97962 | -0.14257 | 0.00037907 | 9.5005e-05
53 | 0.9749 | -0.1765 | 0.0019927 | 0.00049941
54 | 0.97486 | -0.17678 | 0.0017582 | 0.00044064
55 | 0.97494 | -0.17617 | 0 | 0
56 | 0.97486 | -0.17673 | 0.0018728 | 0.00046936
57 | 0.97517 | -0.17451 | 0.0018371 | 0.00046041
58 | 0.97473 | -0.17765 | 0.001823 | 0.00045688
59 | 0.97518 | -0.17444 | 0.0017832 | 0.00044692
60 | 0.97473 | -0.17768 | 0.0018964 | 0.00047529
61 | 0.97549 | -0.17223 | 0 | 0
62 | 0.98367 | -0.11424 | 0.0015747 | 0.00039465
63 | 0.97539 | -0.17298 | 0.00092776 | 0.00023252
64 | 0.97514 | -0.17473 | 0.00095632 | 0.00023968
65 | 0.9749 | -0.17646 | 0.00088832 | 0.00022263
66 | 0.97591 | -0.16923 | 0.00092405 | 0.00023159
67 | 0.9769 | -0.16212 | 0.0011532 | 0.00028903
68 | 0.97752 | -0.15769 | 0.00097731 | 0.00024494
69 | 0.97685 | -0.16246 | 0.00098309 | 0.00024638
70 | 0.97909 | -0.14633 | 0.0034865 | 0.0008738
71 | 0.97891 | -0.14815 | 0.00053529 | 0.00013416
72 | 0.97889 | -0.14832 | 0.00083068 | 0.00020819
73 | 0.97899 | -0.14757 | 0 | 0
74 | 0.97896 | -0.14777 | 0.0005188 | 0.00013002
75 | 0.97907 | -0.14703 | 0.0016188 | 0.00040572
76 | 0.97891 | -0.14813 | 0.0011958 | 0.0002997
77 | 0.9792 | -0.14608 | 0 | 0
78 | 0.9788 | -0.1489 | 0.0018281 | 0.00045817
79 | 0.97471 | -0.17785 | 0.0020806 | 0.00052145
80 | 0.98045 | -0.13683 | 0 | 0
81 | 0.9782 | -0.1528 | 0.0017032 | 0.00042685
82 | 0.97727 | -0.15986 | 0.0050523 | 0.0012662
83 | 0.97747 | -0.15845 | 0 | 0
84 | 0.97775 | -0.15646 | 0.00034041 | 8.5314e-05
85 | 0.97787 | -0.15562 | 0.00054306 | 0.0001361
86 | 0.9782 | -0.15323 | 0 | 0
87 | 0.99971 | -0.0019867 | 0.0019375 | 0.00048558
88 | 0.99879 | -0.0083507 | 0.0018858 | 0.00047262
89 | 0.9972 | -0.019307 | 0 | 0
90 | 0.9955 | -0.03105 | 0.0025994 | 0.00065148
91 | 0.99714 | -0.019708 | 0.0017212 | 0.00043139
92 | 0.97927 | -0.14556 | 0.0020858 | 0.00052275
93 | 0.99126 | -0.060609 | 0.0027098 | 0.00067914
94 | 0.98334 | -0.11659 | 0.001979 | 0.00049599
95 | 0.97685 | -0.16251 | 0.0011565 | 0.00028985
96 | 0.98325 | -0.1172 | 0.0012706 | 0.00031844
97 | 0.98324 | -0.11729 | 0.00038633 | 9.6824e-05
98 | 0.99714 | -0.019717 | 0.00067521 | 0.00016922
99 | 0.97815 | -0.15302 | 0.0032481 | 0.00081406
100 | 0.97768 | -0.15637 | 0.0035683 | 0.00089429
101 | 0.97674 | -0.16311 | 0 | 0
102 | 0.97871 | -0.14956 | 0.0011938 | 0.0002992
103 | 0.97856 | -0.15066 | 0.00032888 | 8.2425e-05
104 | 0.97816 | -0.15354 | 0.00035771 | 8.9651e-05
105 | 0.97164 | -0.19969 | 0.0059287 | 0.0014859
106 | 0.9714 | -0.20136 | 0.003833 | 0.00096064
107 | 0.97213 | -0.19611 | 0.0035286 | 0.00088434
108 | 0.9714 | -0.20142 | 0.0037203 | 0.00093239
109 | 0.97247 | -0.1937 | 0.0033503 | 0.00083966
110 | 0.97128 | -0.20227 | 0.0032551 | 0.00081581
111 | 0.97361 | -0.18547 | 0.0018445 | 0.00046228
112 | 0.97411 | -0.18191 | 0.0018435 | 0.00046204
113 | 0.97812 | -0.15382 | 0.00091151 | 0.00022844
114 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.070567 | -0.017818 | 0.07057 | 0.01782 | 3.1172e-06 | 1.1931e-06 | 0.10545 | 0.10545 | 0.10545 | 0.99624 | -0.025949 | 0.99629 | -0.025635 | 39.0548
1 | 0.069243 | 0.017487 | -0.069125 | -0.017442 | 0.00011769 | 4.5037e-05 | 0.10347 | 0.10347 | 0.10347 | 0.99624 | -0.025949 | 0.99449 | -0.038061 | 38.3224
2 | -0.071468 | -0.018045 | 0.07155 | 0.018076 | 8.1711e-05 | 3.1278e-05 | 0.10679 | 0.10679 | 0.10679 | 0.99629 | -0.025635 | 0.99746 | -0.017507 | 39.5515
3 | 0.06803 | 0.017167 | -0.067841 | -0.017095 | 0.00018846 | 7.2109e-05 | 0.10183 | 0.10183 | 0.10183 | 0.99449 | -0.038061 | 0.99165 | -0.057855 | 37.7152
4 | -0.072888 | -0.018411 | 0.072918 | 0.018423 | 2.9578e-05 | 1.1324e-05 | 0.10879 | 0.10879 | 0.10879 | 0.99746 | -0.017507 | 0.99788 | -0.014623 | 40.2909
5 | 0.0639 | 0.016107 | -0.063811 | -0.016073 | 8.9545e-05 | 3.4239e-05 | 0.095918 | 0.095918 | 0.095918 | 0.99165 | -0.057855 | 0.99022 | -0.067876 | 35.5252
6 | -0.073816 | -0.018648 | 0.073968 | 0.018706 | 0.00015216 | 5.8261e-05 | 0.11012 | 0.11012 | 0.11012 | 0.99788 | -0.014623 | 1 | 0 | 40.7868
7 | 0.059018 | 0.014872 | -0.058989 | -0.014861 | 2.9293e-05 | 1.119e-05 | 0.088716 | 0.088716 | 0.088716 | 0.99022 | -0.067876 | 0.98971 | -0.071424 | 32.8579
8 | 0.12485 | 0.031569 | -0.12481 | -0.031555 | 3.4946e-05 | 1.3356e-05 | 0.18587 | 0.18587 | 0.18587 | 1 | 0 | 0.99971 | -0.0019867 | 34.4209
9 | 0.057219 | 0.014417 | -0.057087 | -0.014367 | 0.00013184 | 5.0343e-05 | 0.086055 | 0.086055 | 0.086055 | 0.98971 | -0.071424 | 0.98736 | -0.08793 | 31.8722
10 | -0.044672 | -0.011247 | 0.044766 | 0.011283 | 9.4555e-05 | 3.5944e-05 | 0.067559 | 0.067558 | 0.067559 | 0.98419 | -0.11022 | 0.98634 | -0.0951 | 25.0217
11 | 0.044234 | 0.011137 | -0.044232 | -0.011136 | 2.1211e-06 | 8.0615e-07 | 0.066896 | 0.066896 | 0.066896 | 0.98419 | -0.11022 | 0.98414 | -0.11056 | 24.7764
12 | -0.045137 | -0.011375 | 0.04515 | 0.01138 | 1.3227e-05 | 5.0289e-06 | 0.068117 | 0.068117 | 0.068117 | 0.98634 | -0.0951 | 0.98663 | -0.093007 | 25.2286
13 | 0.043701 | 0.011003 | -0.043643 | -0.010981 | 5.8078e-05 | 2.2067e-05 | 0.066094 | 0.066094 | 0.066094 | 0.98414 | -0.11056 | 0.98279 | -0.12009 | 24.4792
14 | -0.062319 | -0.015683 | 0.062447 | 0.015732 | 0.00012857 | 4.9151e-05 | 0.094011 | 0.09401 | 0.094011 | 0.98663 | -0.093007 | 0.98873 | -0.078258 | 34.8187
15 | 0.01363 | 0.0034158 | -0.01362 | -0.0034126 | 9.5503e-06 | 3.211e-06 | 0.020556 | 0.020556 | 0.020556 | 0.98663 | -0.093007 | 0.98592 | -0.098072 | 7.6134
16 | -0.040735 | -0.010254 | 0.040833 | 0.010291 | 9.7532e-05 | 3.6972e-05 | 0.061159 | 0.061158 | 0.061159 | 0.99137 | -0.059851 | 0.99382 | -0.042749 | 22.6513
17 | 0.040235 | 0.010129 | -0.040058 | -0.010062 | 0.00017661 | 6.693e-05 | 0.060407 | 0.060407 | 0.060407 | 0.99137 | -0.059851 | 0.98688 | -0.091417 | 22.3731
18 | 0.072727 | 0.018355 | -0.072545 | -0.018285 | 0.00018189 | 6.964e-05 | 0.10894 | 0.10894 | 0.10894 | 0.99382 | -0.042749 | 0.99126 | -0.060609 | 40.3471
19 | -0.11531 | -0.029085 | 0.1155 | 0.029157 | 0.00018948 | 7.2349e-05 | 0.17272 | 0.17272 | 0.17272 | 0.99382 | -0.042749 | 0.9955 | -0.03105 | 31.985
20 | 0.039754 | 0.0099857 | -0.039736 | -0.0099787 | 1.8316e-05 | 6.9401e-06 | 0.059949 | 0.059949 | 0.059949 | 0.98688 | -0.091417 | 0.98641 | -0.094732 | 22.2035
21 | -0.013035 | -0.0032652 | 0.013038 | 0.0032664 | 3.5454e-06 | 1.1768e-06 | 0.019685 | 0.019684 | 0.019685 | 0.9853 | -0.10249 | 0.98558 | -0.10052 | 7.2906
22 | 0.00074131 | 0.0001842 | -0.00074128 | -0.00018473 | 3.352e-08 | -5.3341e-07 | 0.001119 | 0.0011192 | 0.0011192 | 0.9853 | -0.10249 | 0.98525 | -0.10282 | 0.41451
23 | -0.013616 | -0.0034111 | 0.01362 | 0.0034126 | 4.6168e-06 | 1.5525e-06 | 0.020556 | 0.020556 | 0.020556 | 0.98558 | -0.10052 | 0.98592 | -0.098072 | 7.6134
24 | 0.00074128 | 0.00018473 | -0.00074121 | -0.00018577 | 6.4942e-08 | -1.0327e-06 | 0.0011192 | 0.0011195 | 0.0011195 | 0.98525 | -0.10282 | 0.98517 | -0.10346 | 0.41465
25 | -0.06596 | -0.016613 | 0.066072 | 0.016656 | 0.00011218 | 4.2914e-05 | 0.099297 | 0.099297 | 0.099297 | 0.98873 | -0.078258 | 0.99047 | -0.066115 | 36.7766
26 | -0.069781 | -0.017585 | 0.069835 | 0.017606 | 5.3817e-05 | 2.0598e-05 | 0.10487 | 0.10487 | 0.10487 | 0.99047 | -0.066115 | 0.99126 | -0.060609 | 38.8405
27 | -0.0029375 | -0.0007362 | 0.0029377 | 0.00073605 | 2.4908e-07 | -1.5154e-07 | 0.0044848 | 0.0044847 | 0.0044848 | 0.97463 | -0.17842 | 0.97471 | -0.17781 | 1.661
28 | -0.0044435 | -0.0011134 | 0.0044436 | 0.0011134 | 1.1061e-07 | -5.4739e-09 | 0.0067834 | 0.0067834 | 0.0067834 | 0.97471 | -0.17781 | 0.97474 | -0.17763 | 2.5124
29 | -0.0058585 | -0.001468 | 0.0058588 | 0.0014681 | 2.7414e-07 | 3.697e-08 | 0.0089434 | 0.0089434 | 0.0089434 | 0.97474 | -0.17763 | 0.97478 | -0.17729 | 3.3124
30 | -0.0019174 | -0.00048054 | 0.0019175 | 0.00048036 | 8.5452e-08 | -1.7635e-07 | 0.0028915 | 0.0028915 | 0.0028915 | 0.9867 | -0.092602 | 0.98674 | -0.09228 | 1.0709
31 | 0.051617 | 0.012992 | -0.051532 | -0.012959 | 8.5283e-05 | 3.2513e-05 | 0.077859 | 0.077859 | 0.077859 | 0.98674 | -0.09228 | 0.98506 | -0.10413 | 28.8367
32 | -0.053535 | -0.013472 | 0.053567 | 0.013484 | 3.2524e-05 | 1.2407e-05 | 0.08075 | 0.08075 | 0.08075 | 0.98674 | -0.09228 | 0.98736 | -0.08793 | 29.9075
33 | -0.0072683 | -0.0018213 | 0.0072687 | 0.0018214 | 4.705e-07 | 1.046e-07 | 0.011095 | 0.011095 | 0.011095 | 0.97478 | -0.17729 | 0.97485 | -0.17683 | 4.1092
34 | 0.049092 | 0.012348 | -0.049087 | -0.012346 | 5.224e-06 | 1.9899e-06 | 0.074173 | 0.074173 | 0.074173 | 0.98506 | -0.10413 | 0.98495 | -0.1049 | 27.4715
35 | -0.0093954 | -0.0023544 | 0.0093959 | 0.0023546 | 4.7322e-07 | 1.3603e-07 | 0.014341 | 0.014341 | 0.014341 | 0.97485 | -0.17683 | 0.9749 | -0.17646 | 5.3115
36 | 0.046141 | 0.011608 | -0.046057 | -0.011575 | 8.459e-05 | 3.218e-05 | 0.069724 | 0.069724 | 0.069724 | 0.98495 | -0.1049 | 0.98309 | -0.11807 | 25.8236
37 | 0.021075 | 0.0052852 | -0.021061 | -0.0052803 | 1.3491e-05 | 4.9204e-06 | 0.031924 | 0.031924 | 0.031924 | 0.98234 | -0.12362 | 0.9817 | -0.12824 | 11.8239
38 | -0.028964 | -0.0072625 | 0.028971 | 0.0072651 | 6.8944e-06 | 2.579e-06 | 0.043875 | 0.043875 | 0.043875 | 0.98234 | -0.12362 | 0.98259 | -0.1219 | 16.25
39 | 0.019916 | 0.0049932 | -0.019902 | -0.0049881 | 1.3873e-05 | 5.0277e-06 | 0.030188 | 0.030188 | 0.030188 | 0.9817 | -0.12824 | 0.98099 | -0.13327 | 11.1808
40 | -0.032844 | -0.0082358 | 0.032856 | 0.00824 | 1.1245e-05 | 4.2327e-06 | 0.049741 | 0.049741 | 0.049741 | 0.98259 | -0.1219 | 0.98293 | -0.11943 | 18.4224
41 | 0.019336 | 0.0048464 | -0.019329 | -0.0048439 | 6.699e-06 | 2.419e-06 | 0.02933 | 0.02933 | 0.02933 | 0.98099 | -0.13327 | 0.98064 | -0.13578 | 10.8629
42 | -0.033449 | -0.0083888 | 0.03349 | 0.0084042 | 4.0865e-05 | 1.5393e-05 | 0.050639 | 0.050639 | 0.050639 | 0.98293 | -0.11943 | 0.98417 | -0.11063 | 18.7552
43 | 0.018142 | 0.0045464 | -0.018126 | -0.0045405 | 1.6413e-05 | 5.8751e-06 | 0.027528 | 0.027528 | 0.027528 | 0.98064 | -0.13578 | 0.97972 | -0.14232 | 10.1957
44 | 0.0052145 | 0.001305 | -0.0052134 | -0.0013049 | 1.0972e-06 | 6.2564e-08 | 0.0078834 | 0.0078836 | 0.0078836 | 0.98417 | -0.11063 | 0.98396 | -0.11215 | 2.9198
45 | -0.038704 | -0.0097092 | 0.03879 | 0.0097416 | 8.5536e-05 | 3.2389e-05 | 0.058522 | 0.058522 | 0.058522 | 0.98417 | -0.11063 | 0.98641 | -0.094732 | 21.6749
46 | 0.017365 | 0.0043498 | -0.017358 | -0.0043473 | 6.9191e-06 | 2.4605e-06 | 0.026373 | 0.026373 | 0.026373 | 0.97972 | -0.14232 | 0.97932 | -0.1452 | 9.7677
47 | 0.0052134 | 0.0013049 | -0.0052119 | -0.0013049 | 1.4986e-06 | 8.5728e-08 | 0.0078836 | 0.0078837 | 0.0078837 | 0.98396 | -0.11215 | 0.98367 | -0.11424 | 2.9199
48 | 0.042233 | 0.010617 | -0.042225 | -0.010614 | 7.3202e-06 | 2.7791e-06 | 0.063935 | 0.063936 | 0.063936 | 0.98309 | -0.11807 | 0.98291 | -0.11931 | 23.6798
49 | 0.03928 | 0.009876 | -0.039217 | -0.0098522 | 6.2836e-05 | 2.3808e-05 | 0.059477 | 0.059477 | 0.059477 | 0.98291 | -0.11931 | 0.98129 | -0.13081 | 22.0284
50 | 0.036867 | 0.0092633 | -0.036859 | -0.00926 | 8.7146e-06 | 3.2953e-06 | 0.055914 | 0.055914 | 0.055914 | 0.98129 | -0.13081 | 0.98105 | -0.13251 | 20.7088
51 | 0.034302 | 0.0086192 | -0.034282 | -0.0086115 | 2.0607e-05 | 7.772e-06 | 0.052036 | 0.052036 | 0.052036 | 0.98105 | -0.13251 | 0.98045 | -0.13683 | 19.2726
52 | 0.0020859 | 0.00052258 | -0.0020858 | -0.00052275 | 1.0471e-07 | -1.6991e-07 | 0.0031693 | 0.0031694 | 0.0031694 | 0.97932 | -0.1452 | 0.97927 | -0.14556 | 1.1738
53 | 0.015272 | 0.0038248 | -0.01527 | -0.0038241 | 1.8562e-06 | 6.4442e-07 | 0.023204 | 0.023204 | 0.023204 | 0.97932 | -0.1452 | 0.9792 | -0.14608 | 8.5939
54 | 0.043311 | 0.010898 | -0.043269 | -0.010882 | 4.2038e-05 | 1.597e-05 | 0.065591 | 0.065591 | 0.065591 | 0.98279 | -0.12009 | 0.98181 | -0.12705 | 24.2929
55 | 0.040963 | 0.010304 | -0.040937 | -0.010294 | 2.6293e-05 | 9.9745e-06 | 0.062096 | 0.062096 | 0.062096 | 0.98181 | -0.12705 | 0.98116 | -0.13166 | 22.9986
56 | 0.040521 | 0.01019 | -0.040491 | -0.010179 | 2.9402e-05 | 1.1151e-05 | 0.061466 | 0.061466 | 0.061466 | 0.98116 | -0.13166 | 0.98042 | -0.13687 | 22.7651
57 | 0.038237 | 0.0096136 | -0.038207 | -0.0096021 | 3.0379e-05 | 1.1502e-05 | 0.058045 | 0.058045 | 0.058045 | 0.98042 | -0.13687 | 0.97962 | -0.14257 | 21.4982
58 | 0.037828 | 0.0095071 | -0.037808 | -0.0094996 | 1.9768e-05 | 7.4826e-06 | 0.057469 | 0.057469 | 0.057469 | 0.97962 | -0.14257 | 0.97909 | -0.14633 | 21.2849
59 | 0.0017582 | 0.00044048 | -0.0017582 | -0.00044064 | 6.8284e-08 | -1.6319e-07 | 0.0026836 | 0.0026837 | 0.0026837 | 0.9749 | -0.1765 | 0.97486 | -0.17678 | 0.99395
60 | -0.0037509 | -0.00093989 | 0.0037511 | 0.00093985 | 1.7329e-07 | -3.9001e-08 | 0.0057251 | 0.005725 | 0.0057251 | 0.9749 | -0.1765 | 0.97494 | -0.17617 | 2.1204
61 | 0.0076742 | 0.0019231 | -0.0076736 | -0.001923 | 5.9979e-07 | 1.4332e-07 | 0.011713 | 0.011713 | 0.011713 | 0.97494 | -0.17617 | 0.97486 | -0.17673 | 4.3381
62 | -0.011425 | -0.002863 | 0.011428 | 0.0028638 | 2.6315e-06 | 8.3911e-07 | 0.017438 | 0.017438 | 0.017438 | 0.97494 | -0.17617 | 0.97517 | -0.17451 | 6.4584
63 | 0.0058008 | 0.0014536 | -0.0058001 | -0.0014535 | 7.3831e-07 | 9.5822e-08 | 0.0088542 | 0.0088543 | 0.0088543 | 0.97486 | -0.17673 | 0.97473 | -0.17765 | 3.2794
64 | -0.013265 | -0.0033242 | 0.013265 | 0.0033243 | 1.1552e-07 | 3.8795e-08 | 0.020241 | 0.020241 | 0.020241 | 0.97517 | -0.17451 | 0.97518 | -0.17444 | 7.4966
65 | 0.0039771 | 0.00099666 | -0.0039771 | -0.00099666 | 1.4106e-08 | -2.2188e-09 | 0.0060714 | 0.0060714 | 0.0060714 | 0.97473 | -0.17765 | 0.97473 | -0.17768 | 2.2487
66 | -0.015048 | -0.0037712 | 0.015053 | 0.0037728 | 4.618e-06 | 1.601e-06 | 0.022962 | 0.022962 | 0.022962 | 0.97518 | -0.17444 | 0.97549 | -0.17223 | 8.5044
67 | 0.0020806 | 0.00052137 | -0.0020806 | -0.00052145 | 4.8372e-08 | -7.7168e-08 | 0.0031763 | 0.0031763 | 0.0031763 | 0.97473 | -0.17768 | 0.97471 | -0.17785 | 1.1764
68 | -0.027228 | -0.0068242 | 0.027239 | 0.0068284 | 1.1295e-05 | 4.2131e-06 | 0.041533 | 0.041533 | 0.041533 | 0.97549 | -0.17223 | 0.97591 | -0.16923 | 15.3827
69 | 0.012175 | 0.0030514 | -0.012173 | -0.003051 | 1.2681e-06 | 4.1419e-07 | 0.018571 | 0.018571 | 0.018571 | 0.97549 | -0.17223 | 0.97539 | -0.17298 | 6.8783
70 | 0.0036373 | 0.00091021 | -0.0036361 | -0.00091055 | 1.1825e-06 | -3.3963e-07 | 0.0055017 | 0.005502 | 0.005502 | 0.98367 | -0.11424 | 0.98334 | -0.11659 | 2.0378
71 | 0.011246 | 0.0028185 | -0.011243 | -0.0028176 | 2.7261e-06 | 8.6329e-07 | 0.017156 | 0.017156 | 0.017156 | 0.97539 | -0.17298 | 0.97514 | -0.17473 | 6.3541
72 | 0.010287 | 0.0025779 | -0.010284 | -0.0025772 | 2.4669e-06 | 7.4868e-07 | 0.015697 | 0.015697 | 0.015697 | 0.97514 | -0.17473 | 0.9749 | -0.17646 | 5.8137
73 | -0.028163 | -0.00706 | 0.028191 | 0.0070704 | 2.7784e-05 | 1.0384e-05 | 0.042942 | 0.042942 | 0.042942 | 0.97591 | -0.16923 | 0.9769 | -0.16212 | 15.9045
74 | -0.031484 | -0.0078955 | 0.031503 | 0.0079027 | 1.9304e-05 | 7.2561e-06 | 0.047958 | 0.047958 | 0.047958 | 0.9769 | -0.16212 | 0.97752 | -0.15769 | 17.7621
75 | 0.0021397 | 0.00053603 | -0.0021396 | -0.00053618 | 1.0177e-07 | -1.5308e-07 | 0.0032591 | 0.0032592 | 0.0032592 | 0.9769 | -0.16212 | 0.97685 | -0.16246 | 1.2071
76 | -0.03248 | -0.0081476 | 0.032502 | 0.0081559 | 2.2041e-05 | 8.296e-06 | 0.049445 | 0.049445 | 0.049445 | 0.97752 | -0.15769 | 0.9782 | -0.1528 | 18.3131
77 | 0.0011565 | 0.0002898 | -0.0011565 | -0.00028985 | 7.9139e-09 | -4.8115e-08 | 0.0017617 | 0.0017617 | 0.0017617 | 0.97685 | -0.16246 | 0.97685 | -0.16251 | 0.65247
78 | 0.034322 | 0.0086258 | -0.03429 | -0.0086138 | 3.1935e-05 | 1.2047e-05 | 0.05217 | 0.052171 | 0.052171 | 0.97909 | -0.14633 | 0.97815 | -0.15302 | 19.3224
79 | 0.0008307 | 0.00020795 | -0.00083068 | -0.00020819 | 1.9481e-08 | -2.3868e-07 | 0.0012626 | 0.0012627 | 0.0012627 | 0.97891 | -0.14815 | 0.97889 | -0.14832 | 0.46768
80 | -0.001366 | -0.00034211 | 0.0013661 | 0.00034163 | 1.1042e-07 | -4.7364e-07 | 0.0020763 | 0.0020761 | 0.0020763 | 0.97891 | -0.14815 | 0.97899 | -0.14757 | 0.76901
81 | 0.0017147 | 0.00042926 | -0.0017147 | -0.00042939 | 4.7308e-08 | -1.2215e-07 | 0.0026061 | 0.0026062 | 0.0026062 | 0.97899 | -0.14757 | 0.97896 | -0.14777 | 0.96525
82 | -0.0030808 | -0.00077089 | 0.0030811 | 0.00077077 | 2.303e-07 | -1.2312e-07 | 0.0046823 | 0.0046822 | 0.0046823 | 0.97899 | -0.14757 | 0.97907 | -0.14703 | 1.7342
83 | 0.0011959 | 0.00029936 | -0.0011958 | -0.0002997 | 5.9505e-08 | -3.3999e-07 | 0.0018176 | 0.0018177 | 0.0018177 | 0.97896 | -0.14777 | 0.97891 | -0.14813 | 0.67323
84 | -0.0046999 | -0.0011765 | 0.0047005 | 0.0011765 | 6.1505e-07 | -6.4496e-09 | 0.0071425 | 0.0071425 | 0.0071425 | 0.97907 | -0.14703 | 0.9792 | -0.14608 | 2.6454
85 | 0.010569 | 0.0026476 | -0.010565 | -0.0026464 | 4.1227e-06 | 1.2636e-06 | 0.016061 | 0.016061 | 0.016061 | 0.9792 | -0.14608 | 0.9788 | -0.1489 | 5.9486
86 | 0.0087372 | 0.0021882 | -0.0087364 | -0.002188 | 7.9957e-07 | 2.1624e-07 | 0.013282 | 0.013282 | 0.013282 | 0.9788 | -0.1489 | 0.97871 | -0.14956 | 4.9193
87 | 0.034282 | 0.0086115 | -0.034206 | -0.0085828 | 7.5995e-05 | 2.8663e-05 | 0.052036 | 0.052036 | 0.052036 | 0.98045 | -0.13683 | 0.9782 | -0.1528 | 19.2726
88 | -0.0050523 | -0.0012662 | 0.0050533 | 0.0012663 | 9.8861e-07 | 4.4712e-08 | 0.0076927 | 0.0076926 | 0.0076927 | 0.97727 | -0.15986 | 0.97747 | -0.15845 | 2.8491
89 | -0.0050533 | -0.0012663 | 0.0050547 | 0.0012663 | 1.3911e-06 | 6.2667e-08 | 0.0076926 | 0.0076924 | 0.0076926 | 0.97747 | -0.15845 | 0.97775 | -0.15646 | 2.8491
90 | -0.0053951 | -0.0013516 | 0.0053957 | 0.0013517 | 6.2937e-07 | 5.439e-08 | 0.0082105 | 0.0082104 | 0.0082105 | 0.97775 | -0.15646 | 0.97787 | -0.15562 | 3.0409
91 | -0.0059388 | -0.0014878 | 0.0059407 | 0.0014881 | 1.9576e-06 | 2.7082e-07 | 0.0090368 | 0.0090366 | 0.0090368 | 0.97787 | -0.15562 | 0.9782 | -0.15323 | 3.3469
92 | 0.0012693 | 0.00031747 | -0.0012693 | -0.00031773 | 5.3562e-08 | -2.6847e-07 | 0.0019306 | 0.0019307 | 0.0019307 | 0.9782 | -0.15323 | 0.97816 | -0.15354 | 0.71508
93 | -0.00721 | -0.0018055 | 0.0072126 | 0.0018061 | 2.5634e-06 | 5.5701e-07 | 0.010967 | 0.010967 | 0.010967 | 0.9782 | -0.15323 | 0.97856 | -0.15066 | 4.0619
94 | 0.12287 | 0.03107 | -0.12276 | -0.031027 | 0.00011011 | 4.2072e-05 | 0.18299 | 0.18299 | 0.18299 | 0.99971 | -0.0019867 | 0.99879 | -0.0083507 | 33.8869
95 | 0.12088 | 0.030555 | -0.12069 | -0.030484 | 0.00018624 | 7.1148e-05 | 0.18018 | 0.18018 | 0.18018 | 0.99879 | -0.0083507 | 0.9972 | -0.019307 | 33.3667
96 | 0.1183 | 0.029883 | -0.1181 | -0.029809 | 0.00019506 | 7.4502e-05 | 0.1766 | 0.1766 | 0.1766 | 0.9972 | -0.019307 | 0.9955 | -0.03105 | 32.7045
97 | 0.0023966 | 0.00060043 | -0.0023965 | -0.00060059 | 1.3285e-07 | -1.6608e-07 | 0.0035761 | 0.0035762 | 0.0035762 | 0.9972 | -0.019307 | 0.99714 | -0.019708 | 1.3245
98 | 0.00067521 | 0.00016921 | -0.00067521 | -0.00016922 | 8.672e-10 | -1.7523e-08 | 0.0010076 | 0.0010076 | 0.0010076 | 0.99714 | -0.019708 | 0.99714 | -0.019717 | 0.37319
99 | 0.0016571 | 0.00041456 | -0.0016569 | -0.00041496 | 1.3905e-07 | -3.9612e-07 | 0.0025073 | 0.0025074 | 0.0025074 | 0.98334 | -0.11659 | 0.98325 | -0.1172 | 0.92867
100 | 0.00038634 | 9.6519e-05 | -0.00038633 | -9.6824e-05 | 5.1521e-09 | -3.0442e-07 | 0.00058456 | 0.00058467 | 0.00058467 | 0.98325 | -0.1172 | 0.98324 | -0.11729 | 0.21654
101 | 0.031042 | 0.0077997 | -0.031027 | -0.0077943 | 1.4483e-05 | 5.44e-06 | 0.047229 | 0.047229 | 0.047229 | 0.97815 | -0.15302 | 0.97768 | -0.15637 | 17.4924
102 | 0.027459 | 0.0069 | -0.027433 | -0.0068904 | 2.5701e-05 | 9.5898e-06 | 0.041799 | 0.041799 | 0.041799 | 0.97768 | -0.15637 | 0.97674 | -0.16311 | 15.481
103 | 0.027433 | 0.0068904 | -0.027362 | -0.0068637 | 7.1542e-05 | 2.6697e-05 | 0.041799 | 0.041799 | 0.041799 | 0.97674 | -0.16311 | 0.97411 | -0.18191 | 15.4811
104 | 0.0075426 | 0.0018888 | -0.0075415 | -0.0018885 | 1.1459e-06 | 2.6525e-07 | 0.011467 | 0.011467 | 0.011467 | 0.97871 | -0.14956 | 0.97856 | -0.15066 | 4.2471
105 | 0.00091154 | 0.00022808 | -0.00091151 | -0.00022844 | 3.5808e-08 | -3.6085e-07 | 0.0013865 | 0.0013867 | 0.0013867 | 0.97816 | -0.15354 | 0.97812 | -0.15382 | 0.51358
106 | 0.010811 | 0.0027095 | -0.010809 | -0.0027087 | 2.489e-06 | 7.7714e-07 | 0.016557 | 0.016557 | 0.016557 | 0.97164 | -0.19969 | 0.9714 | -0.20136 | 6.1323
107 | -0.01674 | -0.0041953 | 0.016748 | 0.0041983 | 8.3024e-06 | 2.9424e-06 | 0.025637 | 0.025637 | 0.025637 | 0.97164 | -0.19969 | 0.97213 | -0.19611 | 9.495
108 | 0.0069759 | 0.0017481 | -0.0069758 | -0.001748 | 6.3175e-08 | 1.3322e-08 | 0.010686 | 0.010686 | 0.010686 | 0.9714 | -0.20136 | 0.9714 | -0.20142 | 3.9577
109 | -0.020277 | -0.0050826 | 0.020284 | 0.0050851 | 6.7691e-06 | 2.4638e-06 | 0.031038 | 0.031038 | 0.031038 | 0.97213 | -0.19611 | 0.97247 | -0.1937 | 11.4954
110 | 0.0032555 | 0.00081565 | -0.0032551 | -0.00081581 | 3.821e-07 | -1.5782e-07 | 0.0049868 | 0.0049869 | 0.0049869 | 0.9714 | -0.20142 | 0.97128 | -0.20227 | 1.847
111 | -0.023634 | -0.0059248 | 0.023661 | 0.0059347 | 2.697e-05 | 9.9624e-06 | 0.036164 | 0.036164 | 0.036164 | 0.97247 | -0.1937 | 0.97361 | -0.18547 | 13.3941
112 | -0.025505 | -0.006397 | 0.025518 | 0.0064017 | 1.2612e-05 | 4.6854e-06 | 0.038983 | 0.038983 | 0.038983 | 0.97361 | -0.18547 | 0.97411 | -0.18191 | 14.4381

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.20051 | 0.0505

## res_load
| p_mw | q_mvar
0 | 0.0013241 | 0.00033185
1 | 0.00089781 | 0.00022501
2 | 0.0010957 | 0.00027461
3 | 0.0013382 | 0.0003354
4 | 0.0039407 | 0.00098764
5 | 0.00089799 | 0.00022506
6 | 0.0047924 | 0.0012011
7 | 0.00089798 | 0.00022506
8 | 0.0017702 | 0.00044366
9 | 0.00043805 | 0.00010979
10 | 0.00037047 | 9.2849e-05
11 | 0.00053072 | 0.00013301
12 | 0.0035389 | 0.00088692
13 | 0.00050064 | 0.00012547
14 | 0.0017521 | 0.00043913
15 | 0.00030376 | 7.6129e-05
16 | 0.012293 | 0.003081
17 | 0.00057743 | 0.00014472
18 | 0.00074121 | 0.00018577
19 | 0.0035126 | 0.00088035
20 | 0.0037094 | 0.00092966
21 | 0.0029375 | 0.0007362
22 | 0.0015057 | 0.00037737
23 | 0.0014149 | 0.00035461
24 | 0.0019174 | 0.00048054
25 | 0.0014095 | 0.00035325
26 | 0.0024401 | 0.00061154
27 | 0.0035199 | 0.00088217
28 | 0.0021267 | 0.000533
29 | 0.0029452 | 0.00073813
30 | 0.0078894 | 0.0019773
31 | 0.0011457 | 0.00028713
32 | 0.0038733 | 0.00097074
33 | 0.00056574 | 0.00014179
34 | 0.00059351 | 0.00014875
35 | 0.0011873 | 0.00029757
36 | 0.00076088 | 0.00019069
37 | 0.00094618 | 0.00023714
38 | 0.0038241 | 0.00095842
39 | 0.0029454 | 0.00073818
40 | 0.0023497 | 0.00058889
41 | 0.0025566 | 0.00064075
42 | 0.00033227 | 8.3275e-05
43 | 0.0023058 | 0.00057788
44 | 0.00041583 | 0.00010422
45 | 0.0022539 | 0.00056487
46 | 0.00037907 | 9.5005e-05
47 | 0.0019927 | 0.00049941
48 | 0.0017582 | 0.00044064
49 | 0.0018728 | 0.00046936
50 | 0.0018371 | 0.00046041
51 | 0.001823 | 0.00045688
52 | 0.0017832 | 0.00044692
53 | 0.0018964 | 0.00047529
54 | 0.0015747 | 0.00039465
55 | 0.00092776 | 0.00023252
56 | 0.00095632 | 0.00023968
57 | 0.00088832 | 0.00022263
58 | 0.00092405 | 0.00023159
59 | 0.0011532 | 0.00028903
60 | 0.00097731 | 0.00024494
61 | 0.00098309 | 0.00024638
62 | 0.0034865 | 0.0008738
63 | 0.00053529 | 0.00013416
64 | 0.00083068 | 0.00020819
65 | 0.0005188 | 0.00013002
66 | 0.0016188 | 0.00040572
67 | 0.0011958 | 0.0002997
68 | 0.0018281 | 0.00045817
69 | 0.0020806 | 0.00052145
70 | 0.0017032 | 0.00042685
71 | 0.0050523 | 0.0012662
72 | 0.00034041 | 8.5314e-05
73 | 0.00054306 | 0.0001361
74 | 0.0019375 | 0.00048558
75 | 0.0018858 | 0.00047262
76 | 0.0025994 | 0.00065148
77 | 0.0017212 | 0.00043139
78 | 0.0020858 | 0.00052275
79 | 0.0027098 | 0.00067914
80 | 0.001979 | 0.00049599
81 | 0.0011565 | 0.00028985
82 | 0.0012706 | 0.00031844
83 | 0.00038633 | 9.6824e-05
84 | 0.00067521 | 0.00016922
85 | 0.0032481 | 0.00081406
86 | 0.0035683 | 0.00089429
87 | 0.0011938 | 0.0002992
88 | 0.00032888 | 8.2425e-05
89 | 0.00035771 | 8.9651e-05
90 | 0.0059287 | 0.0014859
91 | 0.003833 | 0.00096064
92 | 0.0035286 | 0.00088434
93 | 0.0037203 | 0.00093239
94 | 0.0033503 | 0.00083966
95 | 0.0032551 | 0.00081581
96 | 0.0018445 | 0.00046228
97 | 0.0018435 | 0.00046204
98 | 0.00091151 | 0.00022844

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1