## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1041-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1041-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1041-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1041-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1041-1_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1041-1_0_4_node_124 | 0.4 | n |  | TRUE
6 | bus_LV_1041-1_0_4_node_39 | 0.4 | n |  | TRUE
7 | bus_LV_1041-1_0_4_node_76 | 0.4 | n |  | TRUE
8 | bus_LV_1041-1_0_4_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_1041-1_0_4_node_41 | 0.4 | n |  | TRUE
10 | bus_LV_1041-1_0_4_node_38 | 0.4 | n |  | TRUE
11 | bus_LV_1041-1_0_4_node_77 | 0.4 | n |  | TRUE
12 | bus_LV_1041-1_0_4_node_75 | 0.4 | n |  | TRUE
13 | bus_LV_1041-1_0_4_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_1041-1_0_4_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_1041-1_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_1041-1_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1041-1_0_4_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_1041-1_0_4_node_42 | 0.4 | n |  | TRUE
19 | bus_LV_1041-1_0_4_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_1041-1_0_4_node_43 | 0.4 | n |  | TRUE
21 | bus_LV_1041-1_0_4_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_1041-1_0_4_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_1041-1_0_4_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1041-1_0_4_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_1041-1_0_4_node_10 | 0.4 | n |  | TRUE
26 | bus_LV_1041-1_0_4_node_11 | 0.4 | n |  | TRUE
27 | bus_LV_1041-1_0_4_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_1041-1_0_4_node_13 | 0.4 | n |  | TRUE
29 | bus_LV_1041-1_0_4_node_14 | 0.4 | n |  | TRUE
30 | bus_LV_1041-1_0_4_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_1041-1_0_4_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_1041-1_0_4_node_61 | 0.4 | n |  | TRUE
33 | bus_LV_1041-1_0_4_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_1041-1_0_4_node_62 | 0.4 | n |  | TRUE
35 | bus_LV_1041-1_0_4_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_1041-1_0_4_node_98 | 0.4 | n |  | TRUE
37 | bus_LV_1041-1_0_4_node_102 | 0.4 | n |  | TRUE
38 | bus_LV_1041-1_0_4_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_1041-1_0_4_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_1041-1_0_4_node_64 | 0.4 | n |  | TRUE
41 | bus_LV_1041-1_0_4_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_1041-1_0_4_node_65 | 0.4 | n |  | TRUE
43 | bus_LV_1041-1_0_4_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_1041-1_0_4_node_123 | 0.4 | n |  | TRUE
45 | bus_LV_1041-1_0_4_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_1041-1_0_4_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_1041-1_0_4_node_28 | 0.4 | n |  | TRUE
48 | bus_LV_1041-1_0_4_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_1041-1_0_4_node_122 | 0.4 | n |  | TRUE
50 | bus_LV_1041-1_0_4_node_108 | 0.4 | n |  | TRUE
51 | bus_LV_1041-1_0_4_node_100 | 0.4 | n |  | TRUE
52 | bus_LV_1041-1_0_4_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_1041-1_0_4_node_103 | 0.4 | n |  | TRUE
54 | bus_LV_1041-1_0_4_node_95 | 0.4 | n |  | TRUE
55 | bus_LV_1041-1_0_4_node_45 | 0.4 | n |  | TRUE
56 | bus_LV_1041-1_0_4_node_30 | 0.4 | n |  | TRUE
57 | bus_LV_1041-1_0_4_node_31 | 0.4 | n |  | TRUE
58 | bus_LV_1041-1_0_4_node_32 | 0.4 | n |  | TRUE
59 | bus_LV_1041-1_0_4_node_34 | 0.4 | n |  | TRUE
60 | bus_LV_1041-1_0_4_node_33 | 0.4 | n |  | TRUE
61 | bus_LV_1041-1_0_4_node_104 | 0.4 | n |  | TRUE
62 | bus_LV_1041-1_0_4_node_63 | 0.4 | n |  | TRUE
63 | bus_LV_1041-1_0_4_node_88 | 0.4 | n |  | TRUE
64 | bus_LV_1041-1_0_4_node_96 | 0.4 | n |  | TRUE
65 | bus_LV_1041-1_0_4_node_44 | 0.4 | n |  | TRUE
66 | bus_LV_1041-1_0_4_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_1041-1_0_4_node_40 | 0.4 | n |  | TRUE
68 | bus_LV_1041-1_0_4_node_119 | 0.4 | n |  | TRUE
69 | bus_LV_1041-1_0_4_node_105 | 0.4 | n |  | TRUE
70 | bus_LV_1041-1_0_4_node_106 | 0.4 | n |  | TRUE
71 | bus_LV_1041-1_0_4_node_107 | 0.4 | n |  | TRUE
72 | bus_LV_1041-1_0_4_node_109 | 0.4 | n |  | TRUE
73 | bus_LV_1041-1_0_4_node_110 | 0.4 | n |  | TRUE
74 | bus_LV_1041-1_0_4_node_121 | 0.4 | n |  | TRUE
75 | bus_LV_1041-1_0_4_node_115 | 0.4 | n |  | TRUE
76 | bus_LV_1041-1_0_4_node_111 | 0.4 | n |  | TRUE
77 | bus_LV_1041-1_0_4_node_112 | 0.4 | n |  | TRUE
78 | bus_LV_1041-1_0_4_node_113 | 0.4 | n |  | TRUE
79 | bus_LV_1041-1_0_4_node_114 | 0.4 | n |  | TRUE
80 | bus_LV_1041-1_0_4_node_116 | 0.4 | n |  | TRUE
81 | bus_LV_1041-1_0_4_node_117 | 0.4 | n |  | TRUE
82 | bus_LV_1041-1_0_4_node_131 | 0.4 | n |  | TRUE
83 | bus_LV_1041-1_0_4_node_120 | 0.4 | n |  | TRUE
84 | bus_LV_1041-1_0_4_node_78 | 0.4 | n |  | TRUE
85 | bus_LV_1041-1_0_4_node_46 | 0.4 | n |  | TRUE
86 | bus_LV_1041-1_0_4_node_48 | 0.4 | n |  | TRUE
87 | bus_LV_1041-1_0_4_node_90 | 0.4 | n |  | TRUE
88 | bus_LV_1041-1_0_4_node_49 | 0.4 | n |  | TRUE
89 | bus_LV_1041-1_0_4_node_50 | 0.4 | n |  | TRUE
90 | bus_LV_1041-1_0_4_node_51 | 0.4 | n |  | TRUE
91 | bus_LV_1041-1_0_4_node_52 | 0.4 | n |  | TRUE
92 | bus_LV_1041-1_0_4_node_53 | 0.4 | n |  | TRUE
93 | bus_LV_1041-1_0_4_node_54 | 0.4 | n |  | TRUE
94 | bus_LV_1041-1_0_4_node_55 | 0.4 | n |  | TRUE
95 | bus_LV_1041-1_0_4_node_101 | 0.4 | n |  | TRUE
96 | bus_LV_1041-1_0_4_node_72 | 0.4 | n |  | TRUE
97 | bus_LV_1041-1_0_4_node_126 | 0.4 | n |  | TRUE
98 | bus_LV_1041-1_0_4_node_58 | 0.4 | n |  | TRUE
99 | bus_LV_1041-1_0_4_node_59 | 0.4 | n |  | TRUE
100 | bus_LV_1041-1_0_4_node_60 | 0.4 | n |  | TRUE
101 | bus_LV_1041-1_0_4_node_66 | 0.4 | n |  | TRUE
102 | bus_LV_1041-1_0_4_node_67 | 0.4 | n |  | TRUE
103 | bus_LV_1041-1_0_4_node_87 | 0.4 | n |  | TRUE
104 | bus_LV_1041-1_0_4_node_97 | 0.4 | n |  | TRUE
105 | bus_LV_1041-1_0_4_node_68 | 0.4 | n |  | TRUE
106 | bus_LV_1041-1_0_4_node_69 | 0.4 | n |  | TRUE
107 | bus_LV_1041-1_0_4_node_70 | 0.4 | n |  | TRUE
108 | bus_LV_1041-1_0_4_node_71 | 0.4 | n |  | TRUE
109 | bus_LV_1041-1_0_4_node_89 | 0.4 | n |  | TRUE
110 | bus_LV_1041-1_0_4_node_127 | 0.4 | n |  | TRUE
111 | bus_LV_1041-1_0_4_node_125 | 0.4 | n |  | TRUE
112 | bus_LV_1041-1_0_4_node_80 | 0.4 | n |  | TRUE
113 | bus_LV_1041-1_0_4_node_132 | 0.4 | n |  | TRUE
114 | bus_LV_1041-1_0_4_node_81 | 0.4 | n |  | TRUE
115 | bus_LV_1041-1_0_4_node_82 | 0.4 | n |  | TRUE
116 | bus_LV_1041-1_0_4_node_83 | 0.4 | n |  | TRUE
117 | bus_LV_1041-1_0_4_node_84 | 0.4 | n |  | TRUE
118 | bus_LV_1041-1_0_4_node_92 | 0.4 | n |  | TRUE
119 | bus_LV_1041-1_0_4_node_99 | 0.4 | n |  | TRUE
120 | bus_LV_1041-1_0_4_node_91 | 0.4 | n |  | TRUE
121 | bus_LV_1041-1_0_4_node_85 | 0.4 | n |  | TRUE
122 | bus_LV_1041-1_0_4_node_86 | 0.4 | n |  | TRUE
123 | bus_LV_1041-1_0_4_node_93 | 0.4 | n |  | TRUE
124 | bus_LV_1041-1_0_4_node_94 | 0.4 | n |  | TRUE
125 | bus_LV_1041-1_0_4_node_128 | 0.4 | n |  | TRUE
126 | bus_LV_1041-1_0_4_node_129 | 0.4 | n |  | TRUE
127 | bus_LV_1041-1_0_4_node_130 | 0.4 | n |  | TRUE
128 | bus_MV_470_0_node_93 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1041-1_0_4_load_0 | 0 | 0.00094437 | 0.00023668 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1041-1_0_4_load_1 | 1 | 0.0014696 | 0.00036831 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1041-1_0_4_load_2 | 2 | 0.0016539 | 0.0004145 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1041-1_0_4_load_3 | 3 | 0.0001398 | 3.5037e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1041-1_0_4_load_124 | 5 | 0.00028116 | 7.0465e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1041-1_0_4_load_41 | 9 | 0.0010034 | 0.00025147 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1041-1_0_4_load_38 | 10 | 0.00091107 | 0.00022834 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1041-1_0_4_load_77 | 11 | 0.0012439 | 0.00031176 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1041-1_0_4_load_75 | 12 | 0.0012393 | 0.00031061 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1041-1_0_4_load_5 | 13 | 0.024132 | 0.006048 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1041-1_0_4_load_7 | 15 | 0.0011424 | 0.00028632 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1041-1_0_4_load_8 | 16 | 0.003711 | 0.00093005 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1041-1_0_4_load_25 | 17 | 0.0027216 | 0.00068209 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1041-1_0_4_load_42 | 18 | 0.0010448 | 0.00026186 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1041-1_0_4_load_26 | 19 | 0.0062384 | 0.0015635 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1041-1_0_4_load_43 | 20 | 0.00044172 | 0.0001107 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1041-1_0_4_load_9 | 21 | 0.014344 | 0.003595 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1041-1_0_4_load_20 | 22 | 0.0031282 | 0.000784 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1041-1_0_4_load_21 | 23 | 0.0053946 | 0.001352 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1041-1_0_4_load_22 | 24 | 0.0043633 | 0.0010936 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1041-1_0_4_load_10 | 25 | 0.0015397 | 0.0003859 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1041-1_0_4_load_11 | 26 | 0.00064096 | 0.00016064 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1041-1_0_4_load_15 | 30 | 0.00070349 | 0.00017631 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1041-1_0_4_load_16 | 31 | 0.0017222 | 0.00043162 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1041-1_0_4_load_61 | 32 | 0.00070952 | 0.00017782 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1041-1_0_4_load_17 | 33 | 0.00066882 | 0.00016762 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1041-1_0_4_load_18 | 35 | 0.00029346 | 7.3549e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1041-1_0_4_load_98 | 36 | 0.00030021 | 7.5241e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1041-1_0_4_load_23 | 38 | 0.0048723 | 0.0012211 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1041-1_0_4_load_24 | 39 | 0.0094295 | 0.0023632 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1041-1_0_4_load_64 | 40 | 0.0031913 | 0.00079982 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1041-1_0_4_load_36 | 41 | 0.028133 | 0.0070507 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1041-1_0_4_load_65 | 42 | 0.0028386 | 0.00071142 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1041-1_0_4_load_37 | 43 | 0.011416 | 0.0028612 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1041-1_0_4_load_123 | 44 | 0.0050262 | 0.0012597 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1041-1_0_4_load_27 | 46 | 0.00014283 | 3.5797e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1041-1_0_4_load_28 | 47 | 0.00026614 | 6.6702e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1041-1_0_4_load_122 | 49 | 0.0015122 | 0.00037899 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1041-1_0_4_load_108 | 50 | 0.00064876 | 0.00016259 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1041-1_0_4_load_47 | 52 | 0.00027563 | 6.9079e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1041-1_0_4_load_103 | 53 | 0.00059229 | 0.00014844 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1041-1_0_4_load_45 | 55 | 0.00042566 | 0.00010668 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1041-1_0_4_load_30 | 56 | 0.0019455 | 0.0004876 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1041-1_0_4_load_31 | 57 | 0.0032196 | 0.00080691 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1041-1_0_4_load_34 | 59 | 0.0053989 | 0.0013531 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1041-1_0_4_load_33 | 60 | 0.0051475 | 0.0012901 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1041-1_0_4_load_104 | 61 | 0.00075555 | 0.00018936 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1041-1_0_4_load_96 | 64 | 0.0017573 | 0.00044042 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1041-1_0_4_load_56 | 66 | 0.0061509 | 0.0015416 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1041-1_0_4_load_40 | 67 | 0.00202 | 0.00050625 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1041-1_0_4_load_119 | 68 | 0.0024637 | 0.00061747 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1041-1_0_4_load_105 | 69 | 0.00095414 | 0.00023913 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1041-1_0_4_load_106 | 70 | 0.00063928 | 0.00016022 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1041-1_0_4_load_110 | 73 | 0.0019251 | 0.00048247 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1041-1_0_4_load_121 | 74 | 0.0021513 | 0.00053918 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1041-1_0_4_load_111 | 76 | 0.00020693 | 5.1863e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1041-1_0_4_load_112 | 77 | 0.00016801 | 4.2108e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1041-1_0_4_load_114 | 79 | 0.00022159 | 5.5537e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1041-1_0_4_load_117 | 81 | 0.00080267 | 0.00020117 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1041-1_0_4_load_131 | 82 | 0.00030392 | 7.6171e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1041-1_0_4_load_120 | 83 | 0.00072022 | 0.0001805 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1041-1_0_4_load_78 | 84 | 0.0031727 | 0.00079516 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1041-1_0_4_load_46 | 85 | 7.9759e-05 | 1.9989e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1041-1_0_4_load_48 | 86 | 0.00035769 | 8.9646e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1041-1_0_4_load_90 | 87 | 0.0001233 | 3.0901e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1041-1_0_4_load_49 | 88 | 0.0028626 | 0.00071743 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1041-1_0_4_load_50 | 89 | 0.004511 | 0.0011306 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1041-1_0_4_load_51 | 90 | 0.0035541 | 0.00089073 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1041-1_0_4_load_53 | 92 | 0.002007 | 0.00050301 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1041-1_0_4_load_54 | 93 | 0.00057568 | 0.00014428 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1041-1_0_4_load_55 | 94 | 0.0031781 | 0.00079651 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1041-1_0_4_load_101 | 95 | 0.0025832 | 0.0006474 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1041-1_0_4_load_58 | 98 | 0.0011317 | 0.00028364 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1041-1_0_4_load_59 | 99 | 0.0019067 | 0.00047785 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1041-1_0_4_load_60 | 100 | 0.0020281 | 0.00050828 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1041-1_0_4_load_66 | 101 | 0.00058982 | 0.00014782 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1041-1_0_4_load_67 | 102 | 0.0011487 | 0.00028788 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1041-1_0_4_load_97 | 104 | 0.0023514 | 0.00058932 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1041-1_0_4_load_68 | 105 | 0.0027565 | 0.00069084 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1041-1_0_4_load_69 | 106 | 0.00094705 | 0.00023735 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1041-1_0_4_load_71 | 108 | 0.0018734 | 0.00046952 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1041-1_0_4_load_127 | 110 | 0.0014659 | 0.00036739 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1041-1_0_4_load_125 | 111 | 0.00097564 | 0.00024452 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1041-1_0_4_load_80 | 112 | 0.00072525 | 0.00018177 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1041-1_0_4_load_132 | 113 | 0.00022131 | 5.5465e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1041-1_0_4_load_83 | 116 | 0.0011008 | 0.00027589 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1041-1_0_4_load_92 | 118 | 0.00044381 | 0.00011123 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1041-1_0_4_load_99 | 119 | 0.0002204 | 5.5237e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1041-1_0_4_load_91 | 120 | 8.7208e-05 | 2.1856e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1041-1_0_4_load_85 | 121 | 0.0019364 | 0.00048531 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1041-1_0_4_load_86 | 122 | 0.00066137 | 0.00016576 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1041-1_0_4_load_94 | 124 | 0.0005853 | 0.00014669 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1041-1_0_4_load_128 | 125 | 0.00066338 | 0.00016626 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1041-1_0_4_load_129 | 126 | 0.0015454 | 0.00038732 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1041-1_0_4_load_130 | 127 | 0.001168 | 0.00029274 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1041-1_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0024746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1041-1_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.022952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1041-1_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.017688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1041-1_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0049956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1041-1_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.012229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1041-1_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.028048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1041-1_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.011087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1041-1_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.016506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1041-1_0_4_line_8 | NAYY 4x150 SE | 6 | 9 | 0.01286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1041-1_0_4_line_9 | NAYY 4x150 SE | 6 | 10 | 0.018561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1041-1_0_4_line_10 | NAYY 4x150 SE | 7 | 11 | 0.033297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1041-1_0_4_line_11 | NAYY 4x150 SE | 7 | 12 | 0.002537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1041-1_0_4_line_12 | NAYY 4x150 SE | 8 | 28 | 0.006811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1041-1_0_4_line_13 | NAYY 4x150 SE | 10 | 67 | 0.027075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1041-1_0_4_line_14 | NAYY 4x150 SE | 13 | 14 | 0.042239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1041-1_0_4_line_15 | NAYY 4x150 SE | 14 | 15 | 0.023451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1041-1_0_4_line_16 | NAYY 4x150 SE | 14 | 16 | 0.0061116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_1041-1_0_4_line_17 | NAYY 4x150 SE | 15 | 17 | 0.024562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1041-1_0_4_line_18 | NAYY 4x150 SE | 16 | 18 | 0.024598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1041-1_0_4_line_19 | NAYY 4x150 SE | 17 | 19 | 0.024974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1041-1_0_4_line_20 | NAYY 4x150 SE | 18 | 20 | 0.011518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1041-1_0_4_line_21 | NAYY 4x150 SE | 19 | 44 | 0.012065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1041-1_0_4_line_22 | NAYY 4x150 SE | 20 | 65 | 0.00067279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1041-1_0_4_line_23 | NAYY 4x150 SE | 21 | 22 | 0.042477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1041-1_0_4_line_24 | NAYY 4x150 SE | 22 | 23 | 0.014319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1041-1_0_4_line_25 | NAYY 4x150 SE | 22 | 24 | 0.012518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1041-1_0_4_line_26 | NAYY 4x150 SE | 23 | 38 | 0.010612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1041-1_0_4_line_27 | NAYY 4x150 SE | 24 | 39 | 0.03767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1041-1_0_4_line_28 | NAYY 4x150 SE | 25 | 26 | 0.025878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1041-1_0_4_line_29 | NAYY 4x150 SE | 25 | 27 | 0.030216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1041-1_0_4_line_30 | NAYY 4x150 SE | 26 | 28 | 0.021696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1041-1_0_4_line_31 | NAYY 4x150 SE | 27 | 29 | 0.044242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1041-1_0_4_line_32 | NAYY 4x150 SE | 27 | 30 | 0.00197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1041-1_0_4_line_33 | NAYY 4x150 SE | 28 | 31 | 0.036756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1041-1_0_4_line_34 | NAYY 4x150 SE | 29 | 32 | 0.013404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1041-1_0_4_line_35 | NAYY 4x150 SE | 31 | 33 | 0.018422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1041-1_0_4_line_36 | NAYY 4x150 SE | 32 | 34 | 0.0090419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1041-1_0_4_line_37 | NAYY 4x150 SE | 33 | 35 | 0.020581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1041-1_0_4_line_38 | NAYY 4x150 SE | 34 | 62 | 0.021632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1041-1_0_4_line_39 | NAYY 4x150 SE | 34 | 60 | 0.025304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1041-1_0_4_line_40 | NAYY 4x150 SE | 35 | 36 | 0.029359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1041-1_0_4_line_41 | NAYY 4x150 SE | 36 | 37 | 0.023444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1041-1_0_4_line_42 | NAYY 4x150 SE | 37 | 53 | 0.020835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1041-1_0_4_line_43 | NAYY 4x150 SE | 38 | 40 | 0.0085824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1041-1_0_4_line_44 | NAYY 4x150 SE | 39 | 41 | 0.021048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1041-1_0_4_line_45 | NAYY 4x150 SE | 40 | 42 | 0.013217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1041-1_0_4_line_46 | NAYY 4x150 SE | 41 | 43 | 0.028955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1041-1_0_4_line_47 | NAYY 4x150 SE | 42 | 105 | 0.0011978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1041-1_0_4_line_48 | NAYY 4x150 SE | 43 | 65 | 0.042107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1041-1_0_4_line_49 | NAYY 4x150 SE | 44 | 45 | 0.015434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1041-1_0_4_line_50 | NAYY 4x150 SE | 45 | 62 | 0.022172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1041-1_0_4_line_51 | NAYY 4x150 SE | 45 | 58 | 0.024855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1041-1_0_4_line_52 | NAYY 4x150 SE | 46 | 47 | 0.032206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1041-1_0_4_line_53 | NAYY 4x150 SE | 47 | 48 | 0.055126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1041-1_0_4_line_54 | NAYY 4x150 SE | 48 | 51 | 0.008457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1041-1_0_4_line_55 | NAYY 4x150 SE | 48 | 52 | 0.024406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1041-1_0_4_line_56 | NAYY 4x150 SE | 49 | 50 | 0.046966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1041-1_0_4_line_57 | NAYY 4x150 SE | 50 | 70 | 0.028021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1041-1_0_4_line_58 | NAYY 4x150 SE | 51 | 53 | 0.032719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1041-1_0_4_line_59 | NAYY 4x150 SE | 51 | 54 | 0.009881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1041-1_0_4_line_60 | NAYY 4x150 SE | 52 | 55 | 0.027428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1041-1_0_4_line_61 | NAYY 4x150 SE | 54 | 123 | 0.0052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1041-1_0_4_line_62 | NAYY 4x150 SE | 55 | 85 | 0.0010457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1041-1_0_4_line_63 | NAYY 4x150 SE | 56 | 57 | 0.021964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1041-1_0_4_line_64 | NAYY 4x150 SE | 56 | 58 | 0.014987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1041-1_0_4_line_65 | NAYY 4x150 SE | 58 | 59 | 0.065188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1041-1_0_4_line_66 | NAYY 4x150 SE | 59 | 61 | 0.066091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1041-1_0_4_line_67 | NAYY 4x150 SE | 62 | 63 | 0.067226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1041-1_0_4_line_68 | NAYY 4x150 SE | 62 | 64 | 0.039242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1041-1_0_4_line_69 | NAYY 4x150 SE | 63 | 103 | 0.008169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1041-1_0_4_line_70 | NAYY 4x150 SE | 63 | 95 | 0.0019215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1041-1_0_4_line_71 | NAYY 4x150 SE | 64 | 104 | 0.0045559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1041-1_0_4_line_72 | NAYY 4x150 SE | 65 | 66 | 0.02105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1041-1_0_4_line_73 | NAYY 4x150 SE | 66 | 84 | 0.0037155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1041-1_0_4_line_74 | NAYY 4x150 SE | 67 | 68 | 0.22868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1041-1_0_4_line_75 | NAYY 4x150 SE | 68 | 83 | 0.023827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1041-1_0_4_line_76 | NAYY 4x150 SE | 69 | 70 | 0.021269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1041-1_0_4_line_77 | NAYY 4x150 SE | 69 | 71 | 0.024956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1041-1_0_4_line_78 | NAYY 4x150 SE | 71 | 72 | 0.002714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1041-1_0_4_line_79 | NAYY 4x150 SE | 71 | 73 | 0.035849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1041-1_0_4_line_80 | NAYY 4x150 SE | 72 | 74 | 0.082873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1041-1_0_4_line_81 | NAYY 4x150 SE | 73 | 75 | 0.043239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1041-1_0_4_line_82 | NAYY 4x150 SE | 74 | 83 | 0.022496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1041-1_0_4_line_83 | NAYY 4x150 SE | 75 | 78 | 0.024499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1041-1_0_4_line_84 | NAYY 4x150 SE | 76 | 77 | 0.0091666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1041-1_0_4_line_85 | NAYY 4x150 SE | 76 | 78 | 0.018771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1041-1_0_4_line_86 | NAYY 4x150 SE | 77 | 79 | 0.0095932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1041-1_0_4_line_87 | NAYY 4x150 SE | 78 | 80 | 0.013217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1041-1_0_4_line_88 | NAYY 4x150 SE | 79 | 81 | 0.024693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1041-1_0_4_line_89 | NAYY 4x150 SE | 80 | 82 | 0.015821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1041-1_0_4_line_90 | NAYY 4x150 SE | 85 | 86 | 0.01933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1041-1_0_4_line_91 | NAYY 4x150 SE | 86 | 87 | 0.0099057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1041-1_0_4_line_92 | NAYY 4x150 SE | 88 | 89 | 0.024277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1041-1_0_4_line_93 | NAYY 4x150 SE | 88 | 90 | 0.042476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1041-1_0_4_line_94 | NAYY 4x150 SE | 89 | 91 | 0.0088363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1041-1_0_4_line_95 | NAYY 4x150 SE | 90 | 92 | 0.028692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1041-1_0_4_line_96 | NAYY 4x150 SE | 91 | 93 | 0.018693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1041-1_0_4_line_97 | NAYY 4x150 SE | 91 | 94 | 0.023214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1041-1_0_4_line_98 | NAYY 4x150 SE | 93 | 95 | 0.017357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1041-1_0_4_line_99 | NAYY 4x150 SE | 94 | 96 | 0.034252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1041-1_0_4_line_100 | NAYY 4x150 SE | 96 | 97 | 0.001365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1041-1_0_4_line_101 | NAYY 4x150 SE | 97 | 110 | 0.033319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1041-1_0_4_line_102 | NAYY 4x150 SE | 97 | 111 | 0.013706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1041-1_0_4_line_103 | NAYY 4x150 SE | 98 | 99 | 0.023094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1041-1_0_4_line_104 | NAYY 4x150 SE | 99 | 100 | 0.020381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1041-1_0_4_line_105 | NAYY 4x150 SE | 100 | 101 | 0.013177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1041-1_0_4_line_106 | NAYY 4x150 SE | 101 | 102 | 0.013413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1041-1_0_4_line_107 | NAYY 4x150 SE | 102 | 104 | 0.024239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1041-1_0_4_line_108 | NAYY 4x150 SE | 103 | 109 | 0.014765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1041-1_0_4_line_109 | NAYY 4x150 SE | 103 | 121 | 0.010273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1041-1_0_4_line_110 | NAYY 4x150 SE | 106 | 107 | 0.014423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1041-1_0_4_line_111 | NAYY 4x150 SE | 107 | 108 | 0.010083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1041-1_0_4_line_112 | NAYY 4x150 SE | 108 | 109 | 0.030192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1041-1_0_4_line_113 | NAYY 4x150 SE | 110 | 125 | 0.013567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1041-1_0_4_line_114 | NAYY 4x150 SE | 112 | 113 | 0.1752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1041-1_0_4_line_115 | NAYY 4x150 SE | 112 | 114 | 0.16061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1041-1_0_4_line_116 | NAYY 4x150 SE | 114 | 115 | 0.064128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1041-1_0_4_line_117 | NAYY 4x150 SE | 114 | 116 | 0.066759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1041-1_0_4_line_118 | NAYY 4x150 SE | 115 | 117 | 0.004887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1041-1_0_4_line_119 | NAYY 4x150 SE | 115 | 118 | 0.044378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1041-1_0_4_line_120 | NAYY 4x150 SE | 117 | 119 | 0.035238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1041-1_0_4_line_121 | NAYY 4x150 SE | 118 | 120 | 0.019502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_1041-1_0_4_line_122 | NAYY 4x150 SE | 120 | 123 | 0.025076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_1041-1_0_4_line_123 | NAYY 4x150 SE | 121 | 122 | 0.013572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_1041-1_0_4_line_124 | NAYY 4x150 SE | 123 | 124 | 0.013265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_1041-1_0_4_line_125 | NAYY 4x150 SE | 125 | 126 | 0.010469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_1041-1_0_4_line_126 | NAYY 4x150 SE | 126 | 127 | 0.026592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1041-1_0_4_trafo_25 | 0.25 MVA 20/0.4 kV | 128 | 17 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2662382.3325 | 1235461.0979 | 2662382.3325 | 1235461.0979 | 2662380.0121 | 1235461.9578
1 | 2662382.3325 | 1235461.0979 | 2662405.2119 | 1235459.2746
2 | 2662380.0121 | 1235461.9578 | 2662375.768 | 1235463.5306 | 2662371.306 | 1235468.9874 | 2662370.3797 | 1235475.0296
3 | 2662410.1917 | 1235458.8778 | 2662405.2119 | 1235459.2746
4 | 2662368.5264 | 1235487.1172 | 2662370.3797 | 1235475.0296
5 | 2662410.1917 | 1235458.8778 | 2662412.4909 | 1235430.9278
6 | 2662410.1917 | 1235458.8778 | 2662421.2955 | 1235459.4725
7 | 2662366.025 | 1235503.4326 | 2662368.5264 | 1235487.1172
8 | 2662412.4909 | 1235430.9278 | 2662425.3069 | 1235431.9888
9 | 2662412.4909 | 1235430.9278 | 2662413.2275 | 1235412.3815
10 | 2662421.2955 | 1235459.4725 | 2662419.7654 | 1235492.7341
11 | 2662421.2955 | 1235459.4725 | 2662423.8314 | 1235459.5468
12 | 2662366.025 | 1235503.4326 | 2662359.2199 | 1235502.8386
13 | 2662414.3021 | 1235385.3278 | 2662413.2275 | 1235412.3815
14 | 2662549.1054 | 1235601.2545 | 2662543.696 | 1235624.8021 | 2662539.1671 | 1235636.6067 | 2662537.0952 | 1235641.6309
15 | 2662549.1054 | 1235601.2545 | 2662536.2387 | 1235598.4729 | 2662526.1452 | 1235596.4844
16 | 2662549.1054 | 1235601.2545 | 2662555.042 | 1235602.7061
17 | 2662526.1452 | 1235596.4844 | 2662515.2507 | 1235594.3382 | 2662502.2285 | 1235590.9394
18 | 2662578.9381 | 1235608.5422 | 2662561.9833 | 1235604.4033 | 2662555.042 | 1235602.7061
19 | 2662502.2285 | 1235590.9394 | 2662494.2993 | 1235588.8698 | 2662486.1121 | 1235585.1368 | 2662479.4365 | 1235581.1398
20 | 2662578.9381 | 1235608.5422 | 2662590.1276 | 1235611.2738
21 | 2662470.2535 | 1235573.3687 | 2662477.5686 | 1235580.0214 | 2662479.4365 | 1235581.1398
22 | 2662590.7812 | 1235611.4333 | 2662590.1276 | 1235611.2738
23 | 2662541.9627 | 1235743.3155 | 2662500.235 | 1235735.3738
24 | 2662541.9627 | 1235743.3155 | 2662538.613 | 1235757.2371
25 | 2662544.8911 | 1235731.1447 | 2662541.9627 | 1235743.3155
26 | 2662536.1305 | 1235767.5547 | 2662538.613 | 1235757.2371
27 | 2662544.8911 | 1235731.1447 | 2662546.5145 | 1235724.3978 | 2662552.0233 | 1235702.1744 | 2662554.3224 | 1235694.685
28 | 2662357.6306 | 1235547.5404 | 2662356.2289 | 1235546.247 | 2662352.9524 | 1235540.431 | 2662352.149 | 1235534.7744 | 2662353.5351 | 1235528.9073 | 2662355.7654 | 1235523.8215
29 | 2662385.9536 | 1235552.9968 | 2662380.953 | 1235549.2084 | 2662378.0856 | 1235549.1227 | 2662371.7042 | 1235550.7124 | 2662363.9651 | 1235549.6972 | 2662357.6306 | 1235547.5404
30 | 2662359.2199 | 1235502.8386 | 2662359.648 | 1235512.5272 | 2662358.544 | 1235517.4856 | 2662355.7654 | 1235523.8215
31 | 2662411.3606 | 1235517.6178 | 2662403.5891 | 1235530.4892 | 2662395.2571 | 1235536.9282 | 2662389.6785 | 1235544.2189 | 2662385.9536 | 1235552.9968
32 | 2662385.9536 | 1235552.9968 | 2662385.3088 | 1235554.8583
33 | 2662359.2199 | 1235502.8386 | 2662348.8343 | 1235503.0409 | 2662322.5704 | 1235505.3878
34 | 2662411.3606 | 1235517.6178 | 2662422.6051 | 1235524.9134
35 | 2662322.5704 | 1235505.3878 | 2662304.222 | 1235507.0274
36 | 2662430.1903 | 1235529.8348 | 2662422.6051 | 1235524.9134
37 | 2662304.222 | 1235507.0274 | 2662283.723 | 1235508.8591
38 | 2662445.8889 | 1235544.7318 | 2662434.2878 | 1235533.1356 | 2662430.1903 | 1235529.8348
39 | 2662430.1903 | 1235529.8348 | 2662420.6961 | 1235553.2899
40 | 2662254.4808 | 1235511.4722 | 2662283.723 | 1235508.8591
41 | 2662231.1302 | 1235513.5588 | 2662254.4808 | 1235511.4722
42 | 2662231.1302 | 1235513.5588 | 2662224.8276 | 1235514.1265 | 2662210.3979 | 1235515.62
43 | 2662536.1305 | 1235767.5547 | 2662534.1228 | 1235775.8989
44 | 2662560.499 | 1235674.564 | 2662554.3224 | 1235694.685
45 | 2662531.0308 | 1235788.7496 | 2662534.1228 | 1235775.8989
46 | 2662570.8156 | 1235647.5526 | 2662563.7707 | 1235663.906 | 2662560.499 | 1235674.564
47 | 2662530.7506 | 1235789.9142 | 2662531.0308 | 1235788.7496
48 | 2662590.7812 | 1235611.4333 | 2662587.042 | 1235625.1364 | 2662580.0193 | 1235633.001 | 2662573.5454 | 1235641.216 | 2662570.8156 | 1235647.5526
49 | 2662459.8752 | 1235561.9679 | 2662467.9583 | 1235571.2813 | 2662470.2535 | 1235573.3687
50 | 2662445.8889 | 1235544.7318 | 2662451.2744 | 1235551.4928 | 2662459.8752 | 1235561.9679
51 | 2662459.8752 | 1235561.9679 | 2662455.8725 | 1235565.4838 | 2662448.1008 | 1235583.414
52 | 2662186.471 | 1235464.1399 | 2662193.6707 | 1235444.6322 | 2662197.0302 | 1235433.7255
53 | 2662175.7612 | 1235517.2262 | 2662174.7777 | 1235508.5213 | 2662175.4519 | 1235493.9965 | 2662186.471 | 1235464.1399
54 | 2662179.1995 | 1235524.9562 | 2662175.7612 | 1235517.2262
55 | 2662175.7612 | 1235517.2262 | 2662159.0781 | 1235509.5577 | 2662153.3778 | 1235507.5452
56 | 2662233.0844 | 1235079.0325 | 2662220.3892 | 1235069.3636 | 2662209.7611 | 1235060.124 | 2662194.0001 | 1235057.5129 | 2662193.0778 | 1235057.2861
57 | 2662233.0844 | 1235079.0325 | 2662233.2818 | 1235079.1828 | 2662243.0646 | 1235080.9642 | 2662248.7667 | 1235087.1836 | 2662248.0693 | 1235096.5488
58 | 2662179.1995 | 1235524.9562 | 2662194.9988 | 1235518.7285 | 2662205.1889 | 1235516.2334 | 2662209.1218 | 1235515.7521 | 2662210.3979 | 1235515.62
59 | 2662179.1995 | 1235524.9562 | 2662170.6408 | 1235529.9366
60 | 2662127.2733 | 1235500.2766 | 2662132.7308 | 1235502.5665 | 2662139.1189 | 1235502.511 | 2662153.3778 | 1235507.5452
61 | 2662172.748 | 1235534.684 | 2662172.1083 | 1235532.8984 | 2662170.6408 | 1235529.9366
62 | 2662127.2733 | 1235500.2766 | 2662126.3091 | 1235499.872
63 | 2662416.228 | 1235580.8886 | 2662419.7915 | 1235581.7155 | 2662421.8123 | 1235580.258 | 2662423.4155 | 1235577.4952 | 2662424.7381 | 1235575.5078 | 2662427.6295 | 1235574.7487 | 2662434.2995 | 1235577.5721
64 | 2662448.1008 | 1235583.414 | 2662434.2995 | 1235577.5721
65 | 2662448.1008 | 1235583.414 | 2662434.4109 | 1235615.0244 | 2662430.4717 | 1235626.1905 | 2662428.5311 | 1235637.2997 | 2662428.0627 | 1235644.9078
66 | 2662428.0627 | 1235644.9078 | 2662362.2251 | 1235639.1206
67 | 2662445.8889 | 1235544.7318 | 2662471.0409 | 1235529.3192 | 2662491.3332 | 1235520.4822 | 2662499.7173 | 1235515.5782 | 2662503.0002 | 1235510.6984
68 | 2662445.8889 | 1235544.7318 | 2662450.6969 | 1235534.4421 | 2662447.2644 | 1235522.5982 | 2662447.9201 | 1235507.0591
69 | 2662511.1911 | 1235510.4955 | 2662503.0002 | 1235510.6984
70 | 2662503.0002 | 1235510.6984 | 2662503.5431 | 1235508.8552
71 | 2662447.9201 | 1235507.0591 | 2662448.1122 | 1235502.5073
72 | 2662590.7812 | 1235611.4333 | 2662611.4593 | 1235615.374
73 | 2662615.109 | 1235616.0695 | 2662611.4593 | 1235615.374
74 | 2662414.3021 | 1235385.3278 | 2662399.393 | 1235157.1389
75 | 2662399.393 | 1235157.1389 | 2662396.4566 | 1235156.1443 | 2662376.2014 | 1235151.7492
76 | 2662250.782 | 1235116.0554 | 2662248.9156 | 1235115.5928 | 2662247.102 | 1235109.5365 | 2662248.0693 | 1235096.5488
77 | 2662275.005 | 1235122.0592 | 2662250.782 | 1235116.0554
78 | 2662275.005 | 1235122.0592 | 2662274.3719 | 1235124.6988
79 | 2662275.005 | 1235122.0592 | 2662279.8186 | 1235096.8041 | 2662280.8057 | 1235086.7131
80 | 2662274.3719 | 1235124.6988 | 2662354.5583 | 1235145.6284
81 | 2662285.0152 | 1235043.679 | 2662280.8057 | 1235086.7131
82 | 2662376.2014 | 1235151.7492 | 2662374.2178 | 1235151.3188 | 2662354.5583 | 1235145.6284
83 | 2662285.0152 | 1235043.679 | 2662287.3976 | 1235019.2989
84 | 2662268.6381 | 1235019.9645 | 2662259.4773 | 1235020.2895
85 | 2662287.3976 | 1235019.2989 | 2662268.6381 | 1235019.9645
86 | 2662250.4052 | 1235023.3567 | 2662259.0951 | 1235020.3031 | 2662259.4773 | 1235020.2895
87 | 2662289.2227 | 1235006.2094 | 2662287.3976 | 1235019.2989
88 | 2662250.4052 | 1235023.3567 | 2662246.6516 | 1235024.6757 | 2662225.9722 | 1235025.8747
89 | 2662289.2227 | 1235006.2094 | 2662299.5744 | 1235007.163 | 2662303.2864 | 1235011.1712
90 | 2662126.3091 | 1235499.872 | 2662113.5993 | 1235494.539 | 2662111.9216 | 1235492.131 | 2662112.7476 | 1235489.6534
91 | 2662112.7476 | 1235489.6534 | 2662115.8805 | 1235480.2562
92 | 2662523.3243 | 1235442.8635 | 2662516.4134 | 1235457.9712 | 2662514.0099 | 1235465.2479
93 | 2662523.3243 | 1235442.8635 | 2662527.7465 | 1235433.1962 | 2662542.4907 | 1235407.2008 | 2662543.4518 | 1235405.4928
94 | 2662511.2384 | 1235473.6383 | 2662514.0099 | 1235465.2479
95 | 2662557.522 | 1235380.4876 | 2662543.4518 | 1235405.4928
96 | 2662511.2384 | 1235473.6383 | 2662507.2786 | 1235491.9067
97 | 2662511.2384 | 1235473.6383 | 2662533.1942 | 1235481.176
98 | 2662503.5431 | 1235508.8552 | 2662503.7772 | 1235508.0604 | 2662507.2786 | 1235491.9067
99 | 2662562.2802 | 1235478.4896 | 2662553.0679 | 1235487.999 | 2662533.1942 | 1235481.176
100 | 2662562.2802 | 1235478.4896 | 2662561.8473 | 1235477.1953
101 | 2662561.8473 | 1235477.1953 | 2662559.3313 | 1235469.6082 | 2662558.3523 | 1235459.091 | 2662558.4476 | 1235450.0415 | 2662560.1786 | 1235444.5973
102 | 2662561.8473 | 1235477.1953 | 2662572.2536 | 1235473.6025 | 2662574.9018 | 1235474.1134
103 | 2662461.1838 | 1235422.8926 | 2662462.3859 | 1235445.9556
104 | 2662463.4467 | 1235466.3088 | 2662462.3859 | 1235445.9556
105 | 2662463.4467 | 1235466.3088 | 2662463.4467 | 1235466.3088 | 2662450.2919 | 1235465.5439
106 | 2662449.1341 | 1235478.29 | 2662449.6734 | 1235465.5079 | 2662450.2919 | 1235465.5439
107 | 2662449.1341 | 1235478.29 | 2662448.1122 | 1235502.5073
108 | 2662511.1911 | 1235510.4955 | 2662511.3655 | 1235511.8983 | 2662511.7634 | 1235515.0824 | 2662513.0122 | 1235525.1466
109 | 2662511.1911 | 1235510.4955 | 2662517.9269 | 1235510.4775 | 2662521.4136 | 1235509.8796
110 | 2662552.1236 | 1235528.0822 | 2662566.5016 | 1235526.9421
111 | 2662552.1236 | 1235528.0822 | 2662550.8508 | 1235528.9361 | 2662542.586 | 1235531.1283
112 | 2662513.0122 | 1235525.1466 | 2662515.3804 | 1235525.9276 | 2662519.595 | 1235526.728 | 2662542.586 | 1235531.1283
113 | 2662560.1786 | 1235444.5973 | 2662562.5805 | 1235437.0431 | 2662564.5291 | 1235431.75
114 | 2661885.9928 | 1235649.3877 | 2661993.7724 | 1235787.5153
115 | 2662025.4177 | 1235569.6679 | 2661885.9928 | 1235649.3877
116 | 2662089.5272 | 1235564.5561 | 2662038.7161 | 1235568.8172 | 2662025.4177 | 1235569.6679
117 | 2662025.4177 | 1235569.6679 | 2662028.414 | 1235581.3291 | 2662032.1808 | 1235588.7734 | 2662037.7741 | 1235593.0679 | 2662047.2839 | 1235597.7258 | 2662060.0295 | 1235602.6955 | 2662070.7933 | 1235607.5667 | 2662072.9071 | 1235610.0216
118 | 2662088.6769 | 1235559.744 | 2662089.5272 | 1235564.5561
119 | 2662089.5272 | 1235564.5561 | 2662110.2969 | 1235560.6594 | 2662118.3229 | 1235558.8421 | 2662132.255 | 1235553.2386
120 | 2662088.6769 | 1235559.744 | 2662106.905 | 1235556.4434 | 2662123.0862 | 1235552.2606
121 | 2662150.3343 | 1235545.9292 | 2662149.9543 | 1235546.1199 | 2662132.255 | 1235553.2386
122 | 2662172.748 | 1235534.684 | 2662150.3343 | 1235545.9292
123 | 2662521.4136 | 1235509.8796 | 2662526.4186 | 1235509.0214 | 2662531.2612 | 1235506.9598 | 2662533.8345 | 1235505.0069
124 | 2662172.748 | 1235534.684 | 2662176.6845 | 1235539.6396 | 2662183.6426 | 1235539.3566
125 | 2662564.5291 | 1235431.75 | 2662568.1458 | 1235421.9256
126 | 2662568.1458 | 1235421.9256 | 2662577.3324 | 1235396.9712

## bus_geodata
| x | y | coords
0 | 2662382.3325 | 1235461.0979
1 | 2662380.012 | 1235461.9578
2 | 2662405.2119 | 1235459.2746
3 | 2662370.3797 | 1235475.0296
4 | 2662410.1917 | 1235458.8778
5 | 2662368.5264 | 1235487.1172
6 | 2662412.4909 | 1235430.9278
7 | 2662421.2955 | 1235459.4725
8 | 2662366.025 | 1235503.4326
9 | 2662425.3069 | 1235431.9888
10 | 2662413.2275 | 1235412.3815
11 | 2662419.7654 | 1235492.734
12 | 2662423.8314 | 1235459.5468
13 | 2662537.0952 | 1235641.6309
14 | 2662549.1054 | 1235601.2545
15 | 2662526.1452 | 1235596.4844
16 | 2662555.042 | 1235602.7061
17 | 2662502.2285 | 1235590.9394
18 | 2662578.9381 | 1235608.5422
19 | 2662479.4365 | 1235581.1398
20 | 2662590.1276 | 1235611.2738
21 | 2662500.235 | 1235735.3738
22 | 2662541.9627 | 1235743.3155
23 | 2662538.613 | 1235757.2371
24 | 2662544.8911 | 1235731.1447
25 | 2662357.6306 | 1235547.5404
26 | 2662355.7654 | 1235523.8215
27 | 2662385.9536 | 1235552.9968
28 | 2662359.2199 | 1235502.8386
29 | 2662411.3606 | 1235517.6178
30 | 2662385.3088 | 1235554.8583
31 | 2662322.5704 | 1235505.3878
32 | 2662422.6051 | 1235524.9134
33 | 2662304.222 | 1235507.0274
34 | 2662430.1903 | 1235529.8348
35 | 2662283.723 | 1235508.8591
36 | 2662254.4808 | 1235511.4722
37 | 2662231.1302 | 1235513.5588
38 | 2662536.1305 | 1235767.5547
39 | 2662554.3224 | 1235694.685
40 | 2662534.1228 | 1235775.8989
41 | 2662560.499 | 1235674.564
42 | 2662531.0308 | 1235788.7496
43 | 2662570.8156 | 1235647.5526
44 | 2662470.2535 | 1235573.3687
45 | 2662459.8752 | 1235561.9679
46 | 2662197.0302 | 1235433.7255
47 | 2662186.471 | 1235464.1399
48 | 2662175.7612 | 1235517.2262
49 | 2662193.0778 | 1235057.2861
50 | 2662233.0844 | 1235079.0325
51 | 2662179.1995 | 1235524.9562
52 | 2662153.3778 | 1235507.5452
53 | 2662210.3979 | 1235515.62
54 | 2662170.6408 | 1235529.9366
55 | 2662127.2733 | 1235500.2766
56 | 2662434.2995 | 1235577.5721
57 | 2662416.228 | 1235580.8886
58 | 2662448.1008 | 1235583.414
59 | 2662428.0627 | 1235644.9078
60 | 2662420.6961 | 1235553.2899
61 | 2662362.2251 | 1235639.1206
62 | 2662445.8889 | 1235544.7318
63 | 2662503.0002 | 1235510.6984
64 | 2662447.9201 | 1235507.0591
65 | 2662590.7812 | 1235611.4333
66 | 2662611.4593 | 1235615.374
67 | 2662414.3021 | 1235385.3278
68 | 2662399.393 | 1235157.1389
69 | 2662250.782 | 1235116.0554
70 | 2662248.0693 | 1235096.5488
71 | 2662275.005 | 1235122.0592
72 | 2662274.3719 | 1235124.6988
73 | 2662280.8057 | 1235086.7131
74 | 2662354.5583 | 1235145.6284
75 | 2662285.0152 | 1235043.679
76 | 2662268.6381 | 1235019.9645
77 | 2662259.4773 | 1235020.2895
78 | 2662287.3976 | 1235019.2989
79 | 2662250.4052 | 1235023.3567
80 | 2662289.2227 | 1235006.2094
81 | 2662225.9722 | 1235025.8747
82 | 2662303.2864 | 1235011.1712
83 | 2662376.2014 | 1235151.7492
84 | 2662615.109 | 1235616.0695
85 | 2662126.3091 | 1235499.872
86 | 2662112.7476 | 1235489.6534
87 | 2662115.8805 | 1235480.2562
88 | 2662523.3243 | 1235442.8635
89 | 2662514.0099 | 1235465.2479
90 | 2662543.4518 | 1235405.4928
91 | 2662511.2384 | 1235473.6383
92 | 2662557.522 | 1235380.4876
93 | 2662507.2786 | 1235491.9067
94 | 2662533.1942 | 1235481.176
95 | 2662503.5431 | 1235508.8552
96 | 2662562.2802 | 1235478.4896
97 | 2662561.8473 | 1235477.1953
98 | 2662461.1838 | 1235422.8926
99 | 2662462.3859 | 1235445.9556
100 | 2662463.4467 | 1235466.3088
101 | 2662450.2919 | 1235465.5439
102 | 2662449.1341 | 1235478.29
103 | 2662511.1911 | 1235510.4955
104 | 2662448.1122 | 1235502.5073
105 | 2662530.7506 | 1235789.9142
106 | 2662566.5016 | 1235526.9421
107 | 2662552.1236 | 1235528.0822
108 | 2662542.586 | 1235531.1283
109 | 2662513.0122 | 1235525.1466
110 | 2662560.1786 | 1235444.5973
111 | 2662574.9018 | 1235474.1134
112 | 2661885.9928 | 1235649.3877
113 | 2661993.7724 | 1235787.5153
114 | 2662025.4177 | 1235569.6679
115 | 2662089.5272 | 1235564.5561
116 | 2662072.9071 | 1235610.0216
117 | 2662088.6769 | 1235559.744
118 | 2662132.255 | 1235553.2386
119 | 2662123.0862 | 1235552.2606
120 | 2662150.3343 | 1235545.9292
121 | 2662521.4136 | 1235509.8796
122 | 2662533.8345 | 1235505.0069
123 | 2662172.748 | 1235534.684
124 | 2662183.6426 | 1235539.3566
125 | 2662564.5291 | 1235431.75
126 | 2662568.1458 | 1235421.9256
127 | 2662577.3324 | 1235396.9712
128 | 2662549.1054 | 1235601.2545

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98126 | -0.13179 | 0.00094437 | 0.00023668
1 | 0.98133 | -0.13123 | 0.0014696 | 0.00036831
2 | 0.98056 | -0.13676 | 0.0016539 | 0.0004145
3 | 0.98193 | -0.12696 | 0.0001398 | 3.5037e-05
4 | 0.98042 | -0.13775 | 0 | 0
5 | 0.98235 | -0.124 | 0.00028116 | 7.0465e-05
6 | 0.97974 | -0.14263 | 0 | 0
7 | 0.98038 | -0.13804 | 0 | 0
8 | 0.98292 | -0.11996 | 0 | 0
9 | 0.97972 | -0.14276 | 0.0010034 | 0.00025147
10 | 0.97931 | -0.14566 | 0.00091107 | 0.00022834
11 | 0.98032 | -0.13847 | 0.0012439 | 0.00031176
12 | 0.98038 | -0.13807 | 0.0012393 | 0.00031061
13 | 0.99404 | -0.041363 | 0.024132 | 0.006048
14 | 0.99551 | -0.031082 | 0 | 0
15 | 0.99769 | -0.015934 | 0.0011424 | 0.00028632
16 | 0.99504 | -0.034296 | 0.003711 | 0.00093005
17 | 1 | 0 | -0.23901 | -0.060132
18 | 0.99144 | -0.059357 | 0.0010448 | 0.00026186
19 | 0.99811 | -0.013145 | 0.0062384 | 0.0015635
20 | 0.98977 | -0.071031 | 0.00044172 | 0.0001107
21 | 0.9755 | -0.17223 | 0.014344 | 0.003595
22 | 0.97639 | -0.16585 | 0.0031282 | 0.000784
23 | 0.97599 | -0.1687 | 0.0053946 | 0.001352
24 | 0.97706 | -0.16106 | 0.0043633 | 0.0010936
25 | 0.98542 | -0.10222 | 0.0015397 | 0.0003859
26 | 0.98417 | -0.11103 | 0.00064096 | 0.00016064
27 | 0.98693 | -0.091486 | 0 | 0
28 | 0.98315 | -0.11829 | 0 | 0
29 | 0.9892 | -0.075509 | 0 | 0
30 | 0.98693 | -0.0915 | 0.00070349 | 0.00017631
31 | 0.98269 | -0.1216 | 0.0017222 | 0.00043162
32 | 0.98988 | -0.070682 | 0.00070952 | 0.00017782
33 | 0.98251 | -0.12293 | 0.00066882 | 0.00016762
34 | 0.99035 | -0.067364 | 0 | 0
35 | 0.98232 | -0.12428 | 0.00029346 | 7.3549e-05
36 | 0.98207 | -0.12611 | 0.00030021 | 7.5241e-05
37 | 0.98188 | -0.1275 | 0 | 0
38 | 0.97578 | -0.17022 | 0.0048723 | 0.0012211
39 | 0.97931 | -0.14499 | 0.0094295 | 0.0023632
40 | 0.97567 | -0.17101 | 0.0031913 | 0.00079982
41 | 0.98085 | -0.13398 | 0.028133 | 0.0070507
42 | 0.97556 | -0.17179 | 0.0028386 | 0.00071142
43 | 0.98416 | -0.11049 | 0.011416 | 0.0028612
44 | 0.99638 | -0.025137 | 0.0050262 | 0.0012597
45 | 0.99429 | -0.039755 | 0 | 0
46 | 0.98141 | -0.13091 | 0.00014283 | 3.5797e-05
47 | 0.98141 | -0.13086 | 0.00026614 | 6.6702e-05
48 | 0.98145 | -0.13062 | 0 | 0
49 | 0.97245 | -0.19493 | 0.0015122 | 0.00037899
50 | 0.97256 | -0.19418 | 0.00064876 | 0.00016259
51 | 0.98147 | -0.13048 | 0 | 0
52 | 0.9814 | -0.13094 | 0.00027563 | 6.9079e-05
53 | 0.98171 | -0.12874 | 0.00059229 | 0.00014844
54 | 0.98142 | -0.13083 | 0 | 0
55 | 0.98136 | -0.13123 | 0.00042566 | 0.00010668
56 | 0.99378 | -0.043383 | 0.0019455 | 0.0004876
57 | 0.99367 | -0.044098 | 0.0032196 | 0.00080691
58 | 0.99389 | -0.042601 | 0 | 0
59 | 0.99331 | -0.046663 | 0.0053989 | 0.0013531
60 | 0.99017 | -0.06869 | 0.0051475 | 0.0012901
61 | 0.99324 | -0.04717 | 0.00075555 | 0.00018936
62 | 0.99164 | -0.058309 | 0 | 0
63 | 0.98868 | -0.079216 | 0 | 0
64 | 0.99103 | -0.062663 | 0.0017573 | 0.00044042
65 | 0.98967 | -0.071712 | 0 | 0
66 | 0.98939 | -0.073712 | 0.0061509 | 0.0015416
67 | 0.97873 | -0.14983 | 0.00202 | 0.00050625
68 | 0.97447 | -0.18039 | 0.0024637 | 0.00061747
69 | 0.97273 | -0.19291 | 0.00095414 | 0.00023913
70 | 0.97265 | -0.19354 | 0.00063928 | 0.00016022
71 | 0.97287 | -0.19192 | 0 | 0
72 | 0.9729 | -0.19171 | 0 | 0
73 | 0.97268 | -0.1933 | 0.0019251 | 0.00048247
74 | 0.9738 | -0.18523 | 0.0021513 | 0.00053918
75 | 0.97257 | -0.19408 | 0 | 0
76 | 0.97247 | -0.1948 | 0.00020693 | 5.1863e-05
77 | 0.97246 | -0.19492 | 0.00016801 | 4.2108e-05
78 | 0.97251 | -0.19452 | 0 | 0
79 | 0.97244 | -0.19502 | 0.00022159 | 5.5537e-05
80 | 0.97251 | -0.19457 | 0 | 0
81 | 0.97241 | -0.19523 | 0.00080267 | 0.00020117
82 | 0.9725 | -0.19462 | 0.00030392 | 7.6171e-05
83 | 0.97411 | -0.18297 | 0.00072022 | 0.0001805
84 | 0.98937 | -0.073832 | 0.0031727 | 0.00079516
85 | 0.98136 | -0.13123 | 7.9759e-05 | 1.9989e-05
86 | 0.98135 | -0.13133 | 0.00035769 | 8.9646e-05
87 | 0.98135 | -0.13134 | 0.0001233 | 3.0901e-05
88 | 0.987 | -0.091171 | 0.0028626 | 0.00071743
89 | 0.98729 | -0.089074 | 0.004511 | 0.0011306
90 | 0.98666 | -0.093594 | 0.0035541 | 0.00089073
91 | 0.98746 | -0.087903 | 0 | 0
92 | 0.98657 | -0.094184 | 0.002007 | 0.00050301
93 | 0.98805 | -0.083705 | 0.00057568 | 0.00014428
94 | 0.98716 | -0.090045 | 0.0031781 | 0.00079651
95 | 0.98861 | -0.079708 | 0.0025832 | 0.0006474
96 | 0.98687 | -0.09209 | 0 | 0
97 | 0.98686 | -0.092172 | 0 | 0
98 | 0.9904 | -0.067115 | 0.0011317 | 0.00028364
99 | 0.99044 | -0.066849 | 0.0019067 | 0.00047785
100 | 0.99052 | -0.066218 | 0.0020281 | 0.00050828
101 | 0.99062 | -0.065538 | 0.00058982 | 0.00014782
102 | 0.99073 | -0.064766 | 0.0011487 | 0.00028788
103 | 0.98862 | -0.079668 | 0 | 0
104 | 0.99097 | -0.063087 | 0.0023514 | 0.00058932
105 | 0.97555 | -0.17182 | 0.0027565 | 0.00069084
106 | 0.9884 | -0.081203 | 0.00094705 | 0.00023735
107 | 0.98842 | -0.081063 | 0 | 0
108 | 0.98844 | -0.080965 | 0.0018734 | 0.00046952
109 | 0.98856 | -0.080094 | 0 | 0
110 | 0.98662 | -0.093828 | 0.0014659 | 0.00036739
111 | 0.98684 | -0.092309 | 0.00097564 | 0.00024452
112 | 0.98066 | -0.13639 | 0.00072525 | 0.00018177
113 | 0.9806 | -0.1368 | 0.00022131 | 5.5465e-05
114 | 0.98088 | -0.13477 | 0 | 0
115 | 0.98107 | -0.13338 | 0 | 0
116 | 0.98077 | -0.13553 | 0.0011008 | 0.00027589
117 | 0.98107 | -0.13339 | 0 | 0
118 | 0.98121 | -0.13231 | 0.00044381 | 0.00011123
119 | 0.98105 | -0.13347 | 0.0002204 | 5.5237e-05
120 | 0.98129 | -0.13176 | 8.7208e-05 | 2.1856e-05
121 | 0.98858 | -0.079941 | 0.0019364 | 0.00048531
122 | 0.98857 | -0.080033 | 0.00066137 | 0.00016576
123 | 0.98139 | -0.13101 | 0 | 0
124 | 0.98138 | -0.13109 | 0.0005853 | 0.00014669
125 | 0.98656 | -0.094298 | 0.00066338 | 0.00016626
126 | 0.98652 | -0.09459 | 0.0015454 | 0.00038732
127 | 0.98647 | -0.094909 | 0.001168 | 0.00029274
128 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.021847 | -0.0054801 | 0.021849 | 0.0054807 | 1.695e-06 | 6.2068e-07 | 0.033132 | 0.033132 | 0.033132 | 0.98126 | -0.13179 | 0.98133 | -0.13123 | 12.2709
1 | 0.020903 | 0.0052434 | -0.020888 | -0.0052382 | 1.4392e-05 | 5.2455e-06 | 0.031699 | 0.0317 | 0.0317 | 0.98126 | -0.13179 | 0.98056 | -0.13676 | 11.7406
2 | -0.023318 | -0.0058491 | 0.023332 | 0.0058541 | 1.38e-05 | 5.084e-06 | 0.03536 | 0.03536 | 0.03536 | 0.98133 | -0.13123 | 0.98193 | -0.12696 | 13.0963
3 | 0.019234 | 0.0048237 | -0.019232 | -0.0048227 | 2.656e-06 | 9.5854e-07 | 0.02919 | 0.02919 | 0.02919 | 0.98056 | -0.13676 | 0.98042 | -0.13775 | 10.811
4 | -0.023472 | -0.0058892 | 0.023482 | 0.0058927 | 9.6556e-06 | 3.5589e-06 | 0.035572 | 0.035572 | 0.035572 | 0.98193 | -0.12696 | 0.98235 | -0.124 | 13.1747
5 | 0.016748 | 0.0042009 | -0.016737 | -0.0041969 | 1.131e-05 | 3.9966e-06 | 0.025421 | 0.025421 | 0.025421 | 0.98042 | -0.13775 | 0.97974 | -0.14263 | 9.4152
6 | 0.0024834 | 0.00062184 | -0.0024833 | -0.00062194 | 9.8278e-08 | -1.0201e-07 | 0.003769 | 0.003769 | 0.003769 | 0.98042 | -0.13775 | 0.98038 | -0.13804 | 1.3959
7 | -0.023763 | -0.0059632 | 0.023776 | 0.0059681 | 1.3347e-05 | 4.9242e-06 | 0.035997 | 0.035997 | 0.035997 | 0.98235 | -0.124 | 0.98292 | -0.11996 | 13.3324
8 | 0.0010034 | 0.00025131 | -0.0010034 | -0.00025147 | 1.8635e-08 | -1.5477e-07 | 0.0015239 | 0.0015239 | 0.0015239 | 0.97974 | -0.14263 | 0.97972 | -0.14276 | 0.56442
9 | 0.015734 | 0.0039456 | -0.015727 | -0.0039433 | 6.6142e-06 | 2.3103e-06 | 0.023897 | 0.023897 | 0.023897 | 0.97974 | -0.14263 | 0.97931 | -0.14566 | 8.8508
10 | 0.001244 | 0.00031137 | -0.0012439 | -0.00031176 | 7.4066e-08 | -3.9134e-07 | 0.001888 | 0.0018881 | 0.0018881 | 0.98038 | -0.13804 | 0.98032 | -0.13847 | 0.69931
11 | 0.0012393 | 0.00031058 | -0.0012393 | -0.00031061 | 5.6014e-09 | -2.9835e-08 | 0.0018811 | 0.0018811 | 0.0018811 | 0.98038 | -0.13804 | 0.98038 | -0.13807 | 0.69669
12 | -0.023776 | -0.0059681 | 0.023782 | 0.0059702 | 5.5073e-06 | 2.0318e-06 | 0.035997 | 0.035997 | 0.035997 | 0.98292 | -0.11996 | 0.98315 | -0.11829 | 13.3324
13 | 0.014816 | 0.0037149 | -0.014807 | -0.003712 | 8.5628e-06 | 2.9529e-06 | 0.022513 | 0.022513 | 0.022513 | 0.97931 | -0.14566 | 0.97873 | -0.14983 | 8.3381
14 | -0.024132 | -0.006048 | 0.024166 | 0.0060607 | 3.4394e-05 | 1.268e-05 | 0.036124 | 0.036123 | 0.036124 | 0.99404 | -0.041363 | 0.99551 | -0.031082 | 13.3791
15 | -0.1301 | -0.032815 | 0.13038 | 0.03292 | 0.00027692 | 0.0001059 | 0.19454 | 0.19454 | 0.19454 | 0.99551 | -0.031082 | 0.99769 | -0.015934 | 36.0265
16 | 0.10594 | 0.026754 | -0.10589 | -0.026736 | 4.7855e-05 | 1.8247e-05 | 0.15842 | 0.15842 | 0.15842 | 0.99551 | -0.031082 | 0.99504 | -0.034296 | 29.337
17 | -0.13152 | -0.033207 | 0.13182 | 0.03332 | 0.00029514 | 0.00011287 | 0.19625 | 0.19625 | 0.19625 | 0.99769 | -0.015934 | 1 | 0 | 36.342
18 | 0.10218 | 0.025806 | -0.10182 | -0.025668 | 0.0003587 | 0.00013765 | 0.15287 | 0.15287 | 0.15287 | 0.99504 | -0.034296 | 0.99144 | -0.059357 | 56.6186
19 | 0.10639 | 0.026812 | -0.10619 | -0.026737 | 0.00019541 | 7.4503e-05 | 0.15836 | 0.15836 | 0.15836 | 1 | 0 | 0.99811 | -0.013145 | 29.3264
20 | 0.10077 | 0.025406 | -0.10061 | -0.025343 | 0.00016453 | 6.3134e-05 | 0.1513 | 0.1513 | 0.1513 | 0.99144 | -0.059357 | 0.98977 | -0.071031 | 56.0378
21 | 0.099956 | 0.025174 | -0.099789 | -0.02511 | 0.00016728 | 6.4181e-05 | 0.14906 | 0.14906 | 0.14906 | 0.99811 | -0.013145 | 0.99638 | -0.025137 | 55.2082
22 | 0.10017 | 0.025232 | -0.10016 | -0.025229 | 9.5265e-06 | 3.6554e-06 | 0.15064 | 0.15064 | 0.15064 | 0.98977 | -0.071031 | 0.98967 | -0.071712 | 55.7919
23 | -0.014344 | -0.003595 | 0.014357 | 0.0035993 | 1.2689e-05 | 4.3498e-06 | 0.02188 | 0.02188 | 0.02188 | 0.9755 | -0.17223 | 0.97639 | -0.16585 | 8.1039
24 | 0.019065 | 0.0047792 | -0.019058 | -0.0047765 | 7.5434e-06 | 2.7223e-06 | 0.029056 | 0.029056 | 0.029056 | 0.97639 | -0.16585 | 0.97599 | -0.1687 | 10.7615
25 | -0.03655 | -0.0091626 | 0.036575 | 0.0091717 | 2.4238e-05 | 9.1655e-06 | 0.055704 | 0.055704 | 0.055704 | 0.97639 | -0.16585 | 0.97706 | -0.16106 | 20.631
26 | 0.013663 | 0.0034245 | -0.01366 | -0.0034235 | 2.8735e-06 | 9.7262e-07 | 0.020831 | 0.020831 | 0.020831 | 0.97599 | -0.1687 | 0.97578 | -0.17022 | 7.7153
27 | -0.040938 | -0.010265 | 0.041029 | 0.0103 | 9.1376e-05 | 3.4672e-05 | 0.062349 | 0.062349 | 0.062349 | 0.97706 | -0.16106 | 0.97931 | -0.14499 | 23.0921
28 | 0.033141 | 0.0083143 | -0.0331 | -0.008299 | 4.0445e-05 | 1.5227e-05 | 0.050047 | 0.050047 | 0.050047 | 0.98542 | -0.10222 | 0.98417 | -0.11103 | 18.5359
29 | -0.03468 | -0.0087002 | 0.034732 | 0.0087197 | 5.1715e-05 | 1.9505e-05 | 0.052372 | 0.052372 | 0.052372 | 0.98542 | -0.10222 | 0.98693 | -0.091486 | 19.397
30 | 0.032459 | 0.0081384 | -0.032427 | -0.0081261 | 3.2609e-05 | 1.2267e-05 | 0.049078 | 0.049078 | 0.049078 | 0.98417 | -0.11103 | 0.98315 | -0.11829 | 18.177
31 | -0.035436 | -0.008896 | 0.035515 | 0.0089257 | 7.8818e-05 | 2.9748e-05 | 0.053432 | 0.053432 | 0.053432 | 0.98693 | -0.091486 | 0.9892 | -0.075509 | 19.7898
32 | 0.00070349 | 0.00017629 | -0.00070349 | -0.00017631 | 1.383e-09 | -2.4643e-08 | 0.0010607 | 0.0010607 | 0.0010607 | 0.98693 | -0.091486 | 0.98693 | -0.0915 | 0.39284
33 | 0.0086451 | 0.002156 | -0.0086411 | -0.0021549 | 3.9244e-06 | 1.0435e-06 | 0.013081 | 0.013081 | 0.013081 | 0.98315 | -0.11829 | 0.98269 | -0.1216 | 4.8447
34 | -0.035515 | -0.0089257 | 0.035538 | 0.0089347 | 2.3879e-05 | 9.0122e-06 | 0.053432 | 0.053432 | 0.053432 | 0.9892 | -0.075509 | 0.98988 | -0.070682 | 19.7897
35 | 0.006919 | 0.0017233 | -0.0069177 | -0.0017231 | 1.2608e-06 | 2.5159e-07 | 0.010473 | 0.010473 | 0.010473 | 0.98269 | -0.1216 | 0.98251 | -0.12293 | 3.8789
36 | -0.036248 | -0.0091125 | 0.036265 | 0.0091189 | 1.6758e-05 | 6.329e-06 | 0.054499 | 0.054499 | 0.054499 | 0.98988 | -0.070682 | 0.99035 | -0.067364 | 20.1847
37 | 0.0062489 | 0.0015554 | -0.0062477 | -0.0015552 | 1.1493e-06 | 1.8146e-07 | 0.0094601 | 0.0094602 | 0.0094602 | 0.98251 | -0.12293 | 0.98232 | -0.12428 | 3.5038
38 | -0.041413 | -0.010409 | 0.041465 | 0.010429 | 5.228e-05 | 1.9829e-05 | 0.062234 | 0.062234 | 0.062234 | 0.99035 | -0.067364 | 0.99164 | -0.058309 | 23.0497
39 | 0.0051485 | 0.0012901 | -0.0051475 | -0.0012901 | 9.4485e-07 | 3.7869e-08 | 0.0077356 | 0.0077357 | 0.0077357 | 0.99035 | -0.067364 | 0.99017 | -0.06869 | 2.8651
40 | 0.0059543 | 0.0014817 | -0.0059528 | -0.0014815 | 1.4891e-06 | 2.0116e-07 | 0.0090157 | 0.0090158 | 0.0090158 | 0.98232 | -0.12428 | 0.98207 | -0.12611 | 3.3392
41 | 0.0056526 | 0.0014063 | -0.0056515 | -0.0014061 | 1.0722e-06 | 1.1579e-07 | 0.008561 | 0.0085611 | 0.0085611 | 0.98207 | -0.12611 | 0.98188 | -0.1275 | 3.1708
42 | 0.0056515 | 0.0014061 | -0.0056505 | -0.001406 | 9.5288e-07 | 1.0301e-07 | 0.0085611 | 0.0085612 | 0.0085612 | 0.98188 | -0.1275 | 0.98171 | -0.12874 | 3.1708
43 | 0.008788 | 0.0022024 | -0.008787 | -0.0022021 | 9.6179e-07 | 2.6273e-07 | 0.013401 | 0.013401 | 0.013401 | 0.97578 | -0.17022 | 0.97567 | -0.17101 | 4.9634
44 | -0.050459 | -0.012663 | 0.050536 | 0.012693 | 7.7217e-05 | 2.9434e-05 | 0.076676 | 0.076676 | 0.076676 | 0.97931 | -0.14499 | 0.98085 | -0.13398 | 28.3986
45 | 0.0055957 | 0.0014023 | -0.0055951 | -0.0014022 | 6.0069e-07 | 6.5984e-08 | 0.0085341 | 0.0085341 | 0.0085341 | 0.97567 | -0.17101 | 0.97556 | -0.17179 | 3.1608
46 | -0.078669 | -0.019743 | 0.078926 | 0.019842 | 0.00025739 | 9.863e-05 | 0.11936 | 0.11936 | 0.11936 | 0.98085 | -0.13398 | 0.98416 | -0.11049 | 44.2056
47 | 0.0027565 | 0.00069083 | -0.0027565 | -0.00069084 | 1.3213e-08 | -9.8737e-09 | 0.0042045 | 0.0042045 | 0.0042045 | 0.97556 | -0.17179 | 0.97555 | -0.17182 | 1.5572
48 | -0.090342 | -0.022703 | 0.090833 | 0.022891 | 0.00049038 | 0.00018807 | 0.13662 | 0.13662 | 0.13662 | 0.98416 | -0.11049 | 0.98967 | -0.071712 | 50.5985
49 | 0.094763 | 0.02385 | -0.09457 | -0.023776 | 0.00019299 | 7.4025e-05 | 0.14156 | 0.14156 | 0.14156 | 0.99638 | -0.025137 | 0.99429 | -0.039755 | 52.4281
50 | 0.083241 | 0.020938 | -0.083027 | -0.020856 | 0.00021481 | 8.2331e-05 | 0.1246 | 0.1246 | 0.1246 | 0.99429 | -0.039755 | 0.99164 | -0.058309 | 46.1492
51 | 0.011328 | 0.0028379 | -0.011324 | -0.0028365 | 4.4576e-06 | 1.3922e-06 | 0.016953 | 0.016953 | 0.016953 | 0.99429 | -0.039755 | 0.99389 | -0.042601 | 6.279
52 | -0.00014283 | -3.5797e-05 | 0.00014283 | 3.539e-05 | 9.4188e-10 | -4.066e-07 | 0.00021656 | 0.00021642 | 0.00021656 | 0.98141 | -0.13091 | 0.98141 | -0.13086 | 0.080208
53 | -0.00040898 | -0.00010209 | 0.00040899 | 0.0001014 | 1.3215e-08 | -6.9152e-07 | 0.00061994 | 0.00061969 | 0.00061994 | 0.98141 | -0.13086 | 0.98145 | -0.13062 | 0.22961
54 | -0.0016711 | -0.0004167 | 0.0016712 | 0.0004166 | 3.3856e-08 | -9.3852e-08 | 0.0025329 | 0.0025329 | 0.0025329 | 0.98145 | -0.13062 | 0.98147 | -0.13048 | 0.93812
55 | 0.0012621 | 0.0003153 | -0.0012621 | -0.00031558 | 5.575e-08 | -2.8697e-07 | 0.0019132 | 0.0019133 | 0.0019133 | 0.98145 | -0.13062 | 0.9814 | -0.13094 | 0.70864
56 | -0.0015122 | -0.00037899 | 0.0015124 | 0.00037847 | 1.569e-07 | -5.224e-07 | 0.0023139 | 0.0023137 | 0.0023139 | 0.97245 | -0.19493 | 0.97256 | -0.19418 | 0.85701
57 | -0.0021611 | -0.00054107 | 0.0021613 | 0.00054079 | 1.9113e-07 | -2.7423e-07 | 0.0033063 | 0.0033062 | 0.0033063 | 0.97256 | -0.19418 | 0.97265 | -0.19354 | 1.2246
58 | -0.005057 | -0.0012575 | 0.0050582 | 0.0012576 | 1.199e-06 | 4.7583e-08 | 0.0076635 | 0.0076634 | 0.0076635 | 0.98147 | -0.13048 | 0.98171 | -0.12874 | 2.8383
59 | 0.0033859 | 0.00084094 | -0.0033857 | -0.00084101 | 1.6231e-07 | -6.2439e-08 | 0.0051307 | 0.0051307 | 0.0051307 | 0.98147 | -0.13048 | 0.98142 | -0.13083 | 1.9003
60 | 0.00098645 | 0.00024651 | -0.00098641 | -0.00024684 | 3.8277e-08 | -3.3184e-07 | 0.0014954 | 0.0014955 | 0.0014955 | 0.9814 | -0.13094 | 0.98136 | -0.13123 | 0.5539
61 | 0.0033857 | 0.00084101 | -0.0033856 | -0.00084104 | 8.5417e-08 | -3.2854e-08 | 0.0051307 | 0.0051307 | 0.0051307 | 0.98142 | -0.13083 | 0.98139 | -0.13101 | 1.9003
62 | 0.00056075 | 0.00014016 | -0.00056075 | -0.00014017 | 4.7155e-10 | -1.3031e-08 | 0.00085012 | 0.00085013 | 0.00085013 | 0.98136 | -0.13123 | 0.98136 | -0.13123 | 0.31486
63 | 0.0032199 | 0.00080675 | -0.0032196 | -0.00080691 | 3.1858e-07 | -1.6201e-07 | 0.0048212 | 0.0048213 | 0.0048213 | 0.99378 | -0.043383 | 0.99367 | -0.044098 | 1.7857
64 | -0.0051655 | -0.0012943 | 0.005166 | 0.0012944 | 5.5942e-07 | 2.0965e-08 | 0.0077344 | 0.0077343 | 0.0077344 | 0.99378 | -0.043383 | 0.99389 | -0.042601 | 2.8646
65 | 0.0061579 | 0.0015421 | -0.0061545 | -0.0015416 | 3.4573e-06 | 4.8542e-07 | 0.009219 | 0.0092193 | 0.0092193 | 0.99389 | -0.042601 | 0.99331 | -0.046663 | 3.4146
66 | 0.0007556 | 0.00018852 | -0.00075555 | -0.00018936 | 5.2826e-08 | -8.3513e-07 | 0.0011316 | 0.0011319 | 0.0011319 | 0.99331 | -0.046663 | 0.99324 | -0.04717 | 0.41923
67 | 0.030637 | 0.0076898 | -0.030549 | -0.0076565 | 8.8676e-05 | 3.3242e-05 | 0.045977 | 0.045977 | 0.045977 | 0.99164 | -0.058309 | 0.98868 | -0.079216 | 17.0287
68 | 0.010924 | 0.0027373 | -0.010917 | -0.0027353 | 6.5792e-06 | 2.0245e-06 | 0.016392 | 0.016392 | 0.016392 | 0.99164 | -0.058309 | 0.99103 | -0.062663 | 6.071
69 | 0.0054192 | 0.001357 | -0.0054189 | -0.001357 | 3.3907e-07 | 2.5659e-08 | 0.0081558 | 0.0081558 | 0.0081558 | 0.98868 | -0.079216 | 0.98862 | -0.079668 | 3.0207
70 | 0.025129 | 0.0062995 | -0.025128 | -0.0062989 | 1.7152e-06 | 6.3505e-07 | 0.037822 | 0.037822 | 0.037822 | 0.98868 | -0.079216 | 0.98861 | -0.079708 | 14.008
71 | 0.0091598 | 0.0022949 | -0.0091593 | -0.0022947 | 5.3772e-07 | 1.4812e-07 | 0.013753 | 0.013753 | 0.013753 | 0.99103 | -0.062663 | 0.99097 | -0.063087 | 5.0938
72 | 0.0093263 | 0.0023374 | -0.0093237 | -0.0023367 | 2.5828e-06 | 7.2298e-07 | 0.014022 | 0.014023 | 0.014023 | 0.98967 | -0.071712 | 0.98939 | -0.073712 | 5.1935
73 | 0.0031728 | 0.00079513 | -0.0031727 | -0.00079516 | 5.279e-08 | -2.7411e-08 | 0.0047718 | 0.0047718 | 0.0047718 | 0.98939 | -0.073712 | 0.98937 | -0.073832 | 1.7673
74 | 0.012787 | 0.0032057 | -0.012734 | -0.0031879 | 5.3939e-05 | 1.7884e-05 | 0.019442 | 0.019443 | 0.019443 | 0.97873 | -0.14983 | 0.97447 | -0.18039 | 7.2011
75 | 0.01027 | 0.0025704 | -0.010266 | -0.0025693 | 3.6559e-06 | 1.1094e-06 | 0.015681 | 0.015681 | 0.015681 | 0.97447 | -0.18039 | 0.97411 | -0.18297 | 5.8077
76 | 0.0028008 | 0.00070084 | -0.0028006 | -0.00070101 | 2.4359e-07 | -1.7031e-07 | 0.0042841 | 0.0042842 | 0.0042842 | 0.97273 | -0.19291 | 0.97265 | -0.19354 | 1.5867
77 | -0.003755 | -0.00093997 | 0.0037555 | 0.00093986 | 5.1373e-07 | -1.1225e-07 | 0.0057437 | 0.0057436 | 0.0057437 | 0.97273 | -0.19291 | 0.97287 | -0.19192 | 2.1273
78 | -0.0073848 | -0.0018472 | 0.007385 | 0.0018472 | 2.1601e-07 | 4.938e-08 | 0.011294 | 0.011294 | 0.011294 | 0.97287 | -0.19192 | 0.9729 | -0.19171 | 4.1829
79 | 0.0036293 | 0.00090732 | -0.0036286 | -0.0009075 | 6.8913e-07 | -1.8e-07 | 0.0055503 | 0.0055504 | 0.0055504 | 0.97287 | -0.19192 | 0.97268 | -0.1933 | 2.0557
80 | -0.007385 | -0.0018472 | 0.0073916 | 0.0018487 | 6.5957e-06 | 1.5068e-06 | 0.011294 | 0.011293 | 0.011294 | 0.9729 | -0.19171 | 0.9738 | -0.18523 | 4.1829
81 | 0.0017035 | 0.00042503 | -0.0017034 | -0.00042549 | 1.8317e-07 | -4.6619e-07 | 0.0026054 | 0.0026056 | 0.0026056 | 0.97268 | -0.1933 | 0.97257 | -0.19408 | 0.96503
82 | -0.009543 | -0.0023879 | 0.009546 | 0.0023888 | 2.9844e-06 | 8.6788e-07 | 0.014581 | 0.014581 | 0.014581 | 0.9738 | -0.18523 | 0.97411 | -0.18297 | 5.4003
83 | 0.0017034 | 0.00042549 | -0.0017032 | -0.00042576 | 1.0379e-07 | -2.6408e-07 | 0.0026056 | 0.0026057 | 0.0026057 | 0.97257 | -0.19408 | 0.97251 | -0.19452 | 0.96507
84 | 0.0011923 | 0.0002983 | -0.0011923 | -0.0002984 | 1.9035e-08 | -1.0641e-07 | 0.0018242 | 0.0018243 | 0.0018243 | 0.97247 | -0.1948 | 0.97246 | -0.19492 | 0.67566
85 | -0.0013993 | -0.00035016 | 0.0013993 | 0.00034995 | 5.3684e-08 | -2.1226e-07 | 0.0021409 | 0.0021408 | 0.0021409 | 0.97247 | -0.1948 | 0.97251 | -0.19452 | 0.79292
86 | 0.0010243 | 0.00025629 | -0.0010243 | -0.00025641 | 1.4703e-08 | -1.1336e-07 | 0.0015672 | 0.0015672 | 0.0015672 | 0.97246 | -0.19492 | 0.97244 | -0.19502 | 0.58046
87 | 0.00030393 | 7.5812e-05 | -0.00030393 | -7.5975e-05 | 1.7828e-09 | -1.6331e-07 | 0.0004649 | 0.00046496 | 0.00046496 | 0.97251 | -0.19452 | 0.97251 | -0.19457 | 0.17221
88 | 0.00080269 | 0.00020087 | -0.00080267 | -0.00020117 | 2.3243e-08 | -2.9739e-07 | 0.0012282 | 0.0012283 | 0.0012283 | 0.97244 | -0.19502 | 0.97241 | -0.19523 | 0.45491
89 | 0.00030393 | 7.5975e-05 | -0.00030392 | -7.6171e-05 | 2.1346e-09 | -1.9548e-07 | 0.00046496 | 0.00046503 | 0.00046503 | 0.97251 | -0.19457 | 0.9725 | -0.19462 | 0.17223
90 | 0.00048099 | 0.00012018 | -0.00048099 | -0.00012042 | 6.4142e-09 | -2.4176e-07 | 0.00072919 | 0.00072928 | 0.00072928 | 0.98136 | -0.13123 | 0.98135 | -0.13133 | 0.2701
91 | 0.0001233 | 3.0776e-05 | -0.0001233 | -3.0901e-05 | 2.1599e-10 | -1.2507e-07 | 0.00018691 | 0.00018695 | 0.00018695 | 0.98135 | -0.13133 | 0.98135 | -0.13134 | 0.069242
92 | -0.0084257 | -0.002111 | 0.0084282 | 0.0021117 | 2.4443e-06 | 6.2976e-07 | 0.012703 | 0.012702 | 0.012703 | 0.987 | -0.091171 | 0.98729 | -0.089074 | 4.7047
93 | 0.0055631 | 0.0013936 | -0.0055613 | -0.0013934 | 1.8644e-06 | 1.7441e-07 | 0.0083869 | 0.0083871 | 0.0083871 | 0.987 | -0.091171 | 0.98666 | -0.093594 | 3.1063
94 | -0.012939 | -0.0032422 | 0.012941 | 0.0032429 | 2.0969e-06 | 6.9349e-07 | 0.019501 | 0.019501 | 0.019501 | 0.98729 | -0.089074 | 0.98746 | -0.087903 | 7.2227
95 | 0.0020072 | 0.00050271 | -0.002007 | -0.00050301 | 1.6406e-07 | -3.0331e-07 | 0.003027 | 0.0030271 | 0.0030271 | 0.98666 | -0.093594 | 0.98657 | -0.094184 | 1.1212
96 | -0.021944 | -0.0054979 | 0.021956 | 0.0055026 | 1.2754e-05 | 4.666e-06 | 0.033067 | 0.033067 | 0.033067 | 0.98746 | -0.087903 | 0.98805 | -0.083705 | 12.2469
97 | 0.0090024 | 0.002255 | -0.0089997 | -0.0022543 | 2.6656e-06 | 7.2838e-07 | 0.013565 | 0.013566 | 0.013566 | 0.98746 | -0.087903 | 0.98716 | -0.090045 | 5.0243
98 | -0.022532 | -0.0056469 | 0.022545 | 0.0056515 | 1.2472e-05 | 4.5744e-06 | 0.033934 | 0.033934 | 0.033934 | 0.98805 | -0.083705 | 0.98861 | -0.079708 | 12.568
99 | 0.0058216 | 0.0014578 | -0.00582 | -0.0014576 | 1.6458e-06 | 1.9522e-07 | 0.0087749 | 0.0087751 | 0.0087751 | 0.98716 | -0.090045 | 0.98687 | -0.09209 | 3.25
100 | 0.00582 | 0.0014576 | -0.0058199 | -0.0014576 | 6.5587e-08 | 7.7856e-09 | 0.0087751 | 0.0087751 | 0.0087751 | 0.98687 | -0.09209 | 0.98686 | -0.092172 | 3.25
101 | 0.0048443 | 0.0012132 | -0.0048431 | -0.0012132 | 1.1092e-06 | 1.01e-09 | 0.007304 | 0.0073042 | 0.0073042 | 0.98686 | -0.092172 | 0.98662 | -0.093828 | 2.7052
102 | 0.00097566 | 0.00024435 | -0.00097564 | -0.00024452 | 1.8509e-08 | -1.68e-07 | 0.0014711 | 0.0014711 | 0.0014711 | 0.98686 | -0.092172 | 0.98684 | -0.092309 | 0.54486
103 | -0.0011317 | -0.00028364 | 0.0011318 | 0.00028336 | 4.1662e-08 | -2.8118e-07 | 0.0017003 | 0.0017002 | 0.0017003 | 0.9904 | -0.067115 | 0.99044 | -0.066849 | 0.62976
104 | -0.0030384 | -0.00076121 | 0.0030387 | 0.00076105 | 2.6499e-07 | -1.6039e-07 | 0.0045648 | 0.0045647 | 0.0045648 | 0.99044 | -0.066849 | 0.99052 | -0.066218 | 1.6907
105 | -0.0050668 | -0.0012693 | 0.0050672 | 0.0012693 | 4.7634e-07 | 1.3581e-08 | 0.0076114 | 0.0076113 | 0.0076114 | 0.99052 | -0.066218 | 0.99062 | -0.065538 | 2.819
106 | -0.005657 | -0.0014172 | 0.0056577 | 0.0014172 | 6.0432e-07 | 5.9727e-08 | 0.0084973 | 0.0084972 | 0.0084973 | 0.99062 | -0.065538 | 0.99073 | -0.064766 | 3.1471
107 | -0.0068063 | -0.0017051 | 0.0068079 | 0.0017054 | 1.5805e-06 | 2.9569e-07 | 0.010222 | 0.010222 | 0.010222 | 0.99073 | -0.064766 | 0.99097 | -0.063087 | 3.7861
108 | 0.002821 | 0.00070619 | -0.0028208 | -0.00070632 | 1.6609e-07 | -1.2543e-07 | 0.0042457 | 0.0042458 | 0.0042458 | 0.98862 | -0.079668 | 0.98856 | -0.080094 | 1.5725
109 | 0.0025979 | 0.0006508 | -0.0025978 | -0.00065089 | 9.8012e-08 | -9.4027e-08 | 0.0039101 | 0.0039101 | 0.0039101 | 0.98862 | -0.079668 | 0.98858 | -0.079941 | 1.4482
110 | -0.00094705 | -0.00023735 | 0.00094707 | 0.00023718 | 1.8294e-08 | -1.7782e-07 | 0.0014258 | 0.0014257 | 0.0014258 | 0.9884 | -0.081203 | 0.98842 | -0.081063 | 0.52806
111 | -0.00094707 | -0.00023718 | 0.00094708 | 0.00023705 | 1.2789e-08 | -1.2432e-07 | 0.0014257 | 0.0014257 | 0.0014257 | 0.98842 | -0.081063 | 0.98844 | -0.080965 | 0.52804
112 | -0.0028205 | -0.00070658 | 0.0028208 | 0.00070632 | 3.3963e-07 | -2.5641e-07 | 0.0042459 | 0.0042458 | 0.0042459 | 0.98844 | -0.080965 | 0.98856 | -0.080094 | 1.5726
113 | 0.0033772 | 0.00084582 | -0.003377 | -0.00084591 | 2.1962e-07 | -8.878e-08 | 0.0050933 | 0.0050934 | 0.0050934 | 0.98662 | -0.093828 | 0.98656 | -0.094298 | 1.8864
114 | 0.00022132 | 5.326e-05 | -0.00022131 | -5.5465e-05 | 1.2301e-08 | -2.2056e-06 | 0.00033505 | 0.00033583 | 0.00033583 | 0.98066 | -0.13639 | 0.9806 | -0.1368 | 0.12438
115 | -0.00094657 | -0.00023502 | 0.00094678 | 0.00023308 | 2.0642e-07 | -1.9474e-06 | 0.0014355 | 0.0014348 | 0.0014355 | 0.98066 | -0.13639 | 0.98088 | -0.13477 | 0.53167
116 | -0.0020477 | -0.00050817 | 0.0020481 | 0.00050751 | 3.8567e-07 | -6.6127e-07 | 0.0031046 | 0.0031043 | 0.0031046 | 0.98088 | -0.13477 | 0.98107 | -0.13338 | 1.1499
117 | 0.0011009 | 0.00027509 | -0.0011008 | -0.00027589 | 1.1618e-07 | -7.9787e-07 | 0.0016698 | 0.0016701 | 0.0016701 | 0.98088 | -0.13477 | 0.98077 | -0.13553 | 0.61857
118 | 0.0002204 | 5.4731e-05 | -0.0002204 | -5.4793e-05 | 3.4046e-10 | -6.1578e-08 | 0.00033411 | 0.00033413 | 0.00033413 | 0.98107 | -0.13338 | 0.98107 | -0.13339 | 0.12375
119 | -0.0022685 | -0.00056224 | 0.0022688 | 0.00056181 | 3.2738e-07 | -4.3454e-07 | 0.0034385 | 0.0034383 | 0.0034385 | 0.98107 | -0.13338 | 0.98121 | -0.13231 | 1.2735
120 | 0.0002204 | 5.4793e-05 | -0.0002204 | -5.5237e-05 | 2.456e-09 | -4.44e-07 | 0.00033413 | 0.00033429 | 0.00033429 | 0.98107 | -0.13339 | 0.98105 | -0.13347 | 0.12381
121 | -0.0027126 | -0.00067303 | 0.0027128 | 0.00067287 | 2.0569e-07 | -1.6724e-07 | 0.0041113 | 0.0041112 | 0.0041113 | 0.98121 | -0.13231 | 0.98129 | -0.13176 | 1.5227
122 | -0.0028 | -0.00069472 | 0.0028003 | 0.00069451 | 2.8176e-07 | -2.0845e-07 | 0.0042434 | 0.0042433 | 0.0042434 | 0.98129 | -0.13176 | 0.98139 | -0.13101 | 1.5716
123 | 0.00066138 | 0.00016558 | -0.00066137 | -0.00016576 | 8.3923e-09 | -1.7078e-07 | 0.00099545 | 0.00099551 | 0.00099551 | 0.98858 | -0.079941 | 0.98857 | -0.080033 | 0.36871
124 | 0.00058531 | 0.00014653 | -0.0005853 | -0.00014669 | 6.5187e-09 | -1.651e-07 | 0.0008874 | 0.00088746 | 0.00088746 | 0.98139 | -0.13101 | 0.98138 | -0.13109 | 0.32869
125 | 0.0027136 | 0.00067965 | -0.0027135 | -0.00067974 | 1.0943e-07 | -9.1584e-08 | 0.0040928 | 0.0040928 | 0.0040928 | 0.98656 | -0.094298 | 0.98652 | -0.09459 | 1.5159
126 | 0.0011681 | 0.00029242 | -0.001168 | -0.00029274 | 5.1506e-08 | -3.1969e-07 | 0.0017618 | 0.0017619 | 0.0017619 | 0.98652 | -0.09459 | 0.98647 | -0.094909 | 0.65256

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24173 | 0.060814

## res_load
| p_mw | q_mvar
0 | 0.00094437 | 0.00023668
1 | 0.0014696 | 0.00036831
2 | 0.0016539 | 0.0004145
3 | 0.0001398 | 3.5037e-05
4 | 0.00028116 | 7.0465e-05
5 | 0.0010034 | 0.00025147
6 | 0.00091107 | 0.00022834
7 | 0.0012439 | 0.00031176
8 | 0.0012393 | 0.00031061
9 | 0.024132 | 0.006048
10 | 0.0011424 | 0.00028632
11 | 0.003711 | 0.00093005
12 | 0.0027216 | 0.00068209
13 | 0.0010448 | 0.00026186
14 | 0.0062384 | 0.0015635
15 | 0.00044172 | 0.0001107
16 | 0.014344 | 0.003595
17 | 0.0031282 | 0.000784
18 | 0.0053946 | 0.001352
19 | 0.0043633 | 0.0010936
20 | 0.0015397 | 0.0003859
21 | 0.00064096 | 0.00016064
22 | 0.00070349 | 0.00017631
23 | 0.0017222 | 0.00043162
24 | 0.00070952 | 0.00017782
25 | 0.00066882 | 0.00016762
26 | 0.00029346 | 7.3549e-05
27 | 0.00030021 | 7.5241e-05
28 | 0.0048723 | 0.0012211
29 | 0.0094295 | 0.0023632
30 | 0.0031913 | 0.00079982
31 | 0.028133 | 0.0070507
32 | 0.0028386 | 0.00071142
33 | 0.011416 | 0.0028612
34 | 0.0050262 | 0.0012597
35 | 0.00014283 | 3.5797e-05
36 | 0.00026614 | 6.6702e-05
37 | 0.0015122 | 0.00037899
38 | 0.00064876 | 0.00016259
39 | 0.00027563 | 6.9079e-05
40 | 0.00059229 | 0.00014844
41 | 0.00042566 | 0.00010668
42 | 0.0019455 | 0.0004876
43 | 0.0032196 | 0.00080691
44 | 0.0053989 | 0.0013531
45 | 0.0051475 | 0.0012901
46 | 0.00075555 | 0.00018936
47 | 0.0017573 | 0.00044042
48 | 0.0061509 | 0.0015416
49 | 0.00202 | 0.00050625
50 | 0.0024637 | 0.00061747
51 | 0.00095414 | 0.00023913
52 | 0.00063928 | 0.00016022
53 | 0.0019251 | 0.00048247
54 | 0.0021513 | 0.00053918
55 | 0.00020693 | 5.1863e-05
56 | 0.00016801 | 4.2108e-05
57 | 0.00022159 | 5.5537e-05
58 | 0.00080267 | 0.00020117
59 | 0.00030392 | 7.6171e-05
60 | 0.00072022 | 0.0001805
61 | 0.0031727 | 0.00079516
62 | 7.9759e-05 | 1.9989e-05
63 | 0.00035769 | 8.9646e-05
64 | 0.0001233 | 3.0901e-05
65 | 0.0028626 | 0.00071743
66 | 0.004511 | 0.0011306
67 | 0.0035541 | 0.00089073
68 | 0.002007 | 0.00050301
69 | 0.00057568 | 0.00014428
70 | 0.0031781 | 0.00079651
71 | 0.0025832 | 0.0006474
72 | 0.0011317 | 0.00028364
73 | 0.0019067 | 0.00047785
74 | 0.0020281 | 0.00050828
75 | 0.00058982 | 0.00014782
76 | 0.0011487 | 0.00028788
77 | 0.0023514 | 0.00058932
78 | 0.0027565 | 0.00069084
79 | 0.00094705 | 0.00023735
80 | 0.0018734 | 0.00046952
81 | 0.0014659 | 0.00036739
82 | 0.00097564 | 0.00024452
83 | 0.00072525 | 0.00018177
84 | 0.00022131 | 5.5465e-05
85 | 0.0011008 | 0.00027589
86 | 0.00044381 | 0.00011123
87 | 0.0002204 | 5.5237e-05
88 | 8.7208e-05 | 2.1856e-05
89 | 0.0019364 | 0.00048531
90 | 0.00066137 | 0.00016576
91 | 0.0005853 | 0.00014669
92 | 0.00066338 | 0.00016626
93 | 0.0015454 | 0.00038732
94 | 0.001168 | 0.00029274

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1