## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1081-13_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1081-13_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1081-13_0_2_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1081-13_0_2_node_42 | 0.4 | n |  | TRUE
4 | bus_LV_1081-13_0_2_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_1081-13_0_2_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1081-13_0_2_node_64 | 0.4 | n |  | TRUE
7 | bus_LV_1081-13_0_2_node_139 | 0.4 | n |  | TRUE
8 | bus_LV_1081-13_0_2_node_138 | 0.4 | n |  | TRUE
9 | bus_LV_1081-13_0_2_node_23 | 0.4 | n |  | TRUE
10 | bus_LV_1081-13_0_2_node_144 | 0.4 | n |  | TRUE
11 | bus_LV_1081-13_0_2_node_145 | 0.4 | n |  | TRUE
12 | bus_LV_1081-13_0_2_node_147 | 0.4 | n |  | TRUE
13 | bus_LV_1081-13_0_2_node_148 | 0.4 | n |  | TRUE
14 | bus_LV_1081-13_0_2_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_1081-13_0_2_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_1081-13_0_2_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_1081-13_0_2_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_1081-13_0_2_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_1081-13_0_2_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_1081-13_0_2_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_1081-13_0_2_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_1081-13_0_2_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_1081-13_0_2_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_1081-13_0_2_node_151 | 0.4 | n |  | TRUE
25 | bus_LV_1081-13_0_2_node_36 | 0.4 | n |  | TRUE
26 | bus_LV_1081-13_0_2_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_1081-13_0_2_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_1081-13_0_2_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_1081-13_0_2_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_1081-13_0_2_node_33 | 0.4 | n |  | TRUE
31 | bus_LV_1081-13_0_2_node_34 | 0.4 | n |  | TRUE
32 | bus_LV_1081-13_0_2_node_35 | 0.4 | n |  | TRUE
33 | bus_LV_1081-13_0_2_node_37 | 0.4 | n |  | TRUE
34 | bus_LV_1081-13_0_2_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_1081-13_0_2_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_1081-13_0_2_node_41 | 0.4 | n |  | TRUE
37 | bus_LV_1081-13_0_2_node_54 | 0.4 | n |  | TRUE
38 | bus_LV_1081-13_0_2_node_55 | 0.4 | n |  | TRUE
39 | bus_LV_1081-13_0_2_node_56 | 0.4 | n |  | TRUE
40 | bus_LV_1081-13_0_2_node_57 | 0.4 | n |  | TRUE
41 | bus_LV_1081-13_0_2_node_58 | 0.4 | n |  | TRUE
42 | bus_LV_1081-13_0_2_node_59 | 0.4 | n |  | TRUE
43 | bus_LV_1081-13_0_2_node_60 | 0.4 | n |  | TRUE
44 | bus_LV_1081-13_0_2_node_61 | 0.4 | n |  | TRUE
45 | bus_LV_1081-13_0_2_node_62 | 0.4 | n |  | TRUE
46 | bus_LV_1081-13_0_2_node_150 | 0.4 | n |  | TRUE
47 | bus_LV_1081-13_0_2_node_149 | 0.4 | n |  | TRUE
48 | bus_MV_0_node_33 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1081-13_0_2_load_0 | 0 | 0.0076226 | 0.0019104 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1081-13_0_2_load_42 | 3 | 0.010922 | 0.0027373 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1081-13_0_2_load_64 | 6 | 0.00054191 | 0.00013582 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1081-13_0_2_load_139 | 7 | 0.00021738 | 5.4481e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1081-13_0_2_load_138 | 8 | 0.00059339 | 0.00014872 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1081-13_0_2_load_144 | 10 | 0.00032831 | 8.2283e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1081-13_0_2_load_148 | 13 | 0.0031535 | 0.00079035 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1081-13_0_2_load_18 | 14 | 0.00035525 | 8.9034e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1081-13_0_2_load_19 | 15 | 0.00097899 | 0.00024536 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1081-13_0_2_load_21 | 17 | 0.00013536 | 3.3925e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1081-13_0_2_load_28 | 20 | 0.00010144 | 2.5423e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1081-13_0_2_load_27 | 21 | 5.8758e-05 | 1.4726e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1081-13_0_2_load_25 | 23 | 0.00022139 | 5.5486e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1081-13_0_2_load_151 | 24 | 0.00255 | 0.00063908 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1081-13_0_2_load_29 | 26 | 0.00091772 | 0.00023 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1081-13_0_2_load_30 | 27 | 0.0015325 | 0.00038407 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1081-13_0_2_load_31 | 28 | 0.00017738 | 4.4456e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1081-13_0_2_load_32 | 29 | 0.00024871 | 6.2333e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1081-13_0_2_load_33 | 30 | 9.5299e-05 | 2.3884e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1081-13_0_2_load_34 | 31 | 0.0014271 | 0.00035766 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1081-13_0_2_load_35 | 32 | 0.00018874 | 4.7303e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1081-13_0_2_load_37 | 33 | 0.0035742 | 0.00089578 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1081-13_0_2_load_38 | 35 | 0.0016868 | 0.00042274 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1081-13_0_2_load_41 | 36 | 0.0010598 | 0.0002656 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1081-13_0_2_load_54 | 37 | 0.00031037 | 7.7786e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1081-13_0_2_load_55 | 38 | 0.00011925 | 2.9887e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1081-13_0_2_load_56 | 39 | 0.00018179 | 4.5561e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1081-13_0_2_load_57 | 40 | 7.8105e-05 | 1.9575e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1081-13_0_2_load_58 | 41 | 8.4792e-05 | 2.1251e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1081-13_0_2_load_60 | 43 | 0.00023718 | 5.9443e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1081-13_0_2_load_61 | 44 | 4.5356e-05 | 1.1367e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1081-13_0_2_load_62 | 45 | 0.00061656 | 0.00015453 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1081-13_0_2_load_150 | 46 | 0.00050579 | 0.00012676 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1081-13_0_2_load_149 | 47 | 0.00057217 | 0.0001434 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1081-13_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.024078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1081-13_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.043959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1081-13_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.042538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1081-13_0_2_line_3 | NAYY 4x150 SE | 3 | 30 | 0.29997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1081-13_0_2_line_4 | NAYY 4x150 SE | 4 | 5 | 0.34497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1081-13_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.21876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1081-13_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.030856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1081-13_0_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.018919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1081-13_0_2_line_8 | NAYY 4x150 SE | 6 | 44 | 0.017499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1081-13_0_2_line_9 | NAYY 4x150 SE | 8 | 9 | 0.064017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1081-13_0_2_line_10 | NAYY 4x150 SE | 9 | 16 | 0.25013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1081-13_0_2_line_11 | NAYY 4x150 SE | 10 | 11 | 0.013817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1081-13_0_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.005025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1081-13_0_2_line_13 | NAYY 4x150 SE | 11 | 13 | 0.014394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1081-13_0_2_line_14 | NAYY 4x150 SE | 12 | 46 | 0.051966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1081-13_0_2_line_15 | NAYY 4x150 SE | 12 | 47 | 0.018913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1081-13_0_2_line_16 | NAYY 4x150 SE | 13 | 24 | 0.015781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1081-13_0_2_line_17 | NAYY 4x150 SE | 14 | 15 | 0.004237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1081-13_0_2_line_18 | NAYY 4x150 SE | 14 | 16 | 0.069474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1081-13_0_2_line_19 | NAYY 4x150 SE | 15 | 17 | 0.048062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1081-13_0_2_line_20 | NAYY 4x150 SE | 16 | 18 | 0.064862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1081-13_0_2_line_21 | NAYY 4x150 SE | 17 | 19 | 0.01882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1081-13_0_2_line_22 | NAYY 4x150 SE | 18 | 20 | 0.19254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1081-13_0_2_line_23 | NAYY 4x150 SE | 18 | 21 | 0.015138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1081-13_0_2_line_24 | NAYY 4x150 SE | 19 | 22 | 0.071179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1081-13_0_2_line_25 | NAYY 4x150 SE | 20 | 25 | 0.037388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1081-13_0_2_line_26 | NAYY 4x150 SE | 21 | 23 | 0.036491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1081-13_0_2_line_27 | NAYY 4x150 SE | 22 | 24 | 0.66516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1081-13_0_2_line_28 | NAYY 4x150 SE | 25 | 33 | 0.019958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1081-13_0_2_line_29 | NAYY 4x150 SE | 25 | 32 | 0.023134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1081-13_0_2_line_30 | NAYY 4x150 SE | 26 | 27 | 0.0054443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1081-13_0_2_line_31 | NAYY 4x150 SE | 26 | 28 | 0.10348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1081-13_0_2_line_32 | NAYY 4x150 SE | 27 | 29 | 0.035398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1081-13_0_2_line_33 | NAYY 4x150 SE | 28 | 30 | 0.017022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1081-13_0_2_line_34 | NAYY 4x150 SE | 29 | 31 | 0.010895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1081-13_0_2_line_35 | NAYY 4x150 SE | 31 | 32 | 0.011542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1081-13_0_2_line_36 | NAYY 4x150 SE | 33 | 34 | 0.011492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1081-13_0_2_line_37 | NAYY 4x150 SE | 34 | 36 | 0.047647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1081-13_0_2_line_38 | NAYY 4x150 SE | 34 | 35 | 0.012627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1081-13_0_2_line_39 | NAYY 4x150 SE | 37 | 38 | 0.028224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1081-13_0_2_line_40 | NAYY 4x150 SE | 38 | 39 | 0.0057933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1081-13_0_2_line_41 | NAYY 4x150 SE | 39 | 40 | 0.0040071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1081-13_0_2_line_42 | NAYY 4x150 SE | 40 | 41 | 0.0085267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1081-13_0_2_line_43 | NAYY 4x150 SE | 41 | 42 | 0.006399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1081-13_0_2_line_44 | NAYY 4x150 SE | 42 | 43 | 0.030247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1081-13_0_2_line_45 | NAYY 4x150 SE | 42 | 44 | 0.036529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1081-13_0_2_line_46 | NAYY 4x150 SE | 43 | 45 | 0.049611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1081-13_0_2_trafo_33 | 0.25 MVA 20/0.4 kV | 48 | 30 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26
0 | 2659247.1623 | 1223584.5981 | 2659249.376 | 1223591.5245 | 2659242.5121 | 1223606.8658
1 | 2659284.0887 | 1223608.614 | 2659247.1623 | 1223584.5981
2 | 2659284.0887 | 1223608.614 | 2659294.4487 | 1223619.146 | 2659308.5795 | 1223630.2381 | 2659316.1814 | 1223636.4239
3 | 2659535.8732 | 1223834.2794 | 2659520.5914 | 1223826.599 | 2659503.5816 | 1223819.1354 | 2659465.1457 | 1223797.6602 | 2659437.7363 | 1223773.0489 | 2659415.7925 | 1223753.1507 | 2659393.2579 | 1223728.5994 | 2659372.5343 | 1223702.6542 | 2659355.2354 | 1223683.8255 | 2659341.1938 | 1223663.8174 | 2659324.7221 | 1223643.3738 | 2659316.1814 | 1223636.4239
4 | 2659025.3107 | 1224396.9404 | 2659064.3926 | 1224275.9182 | 2659075.7124 | 1224278.2764 | 2659098.0461 | 1224281.7335 | 2659277.6687 | 1224298.1179 | 2659280.9181 | 1224298.4616
5 | 2659025.3107 | 1224396.9404 | 2659008.7065 | 1224390.7386 | 2658885.0032 | 1224354.6358 | 2658823.3436 | 1224337.8158 | 2658815.4149 | 1224335.4921
6 | 2659280.9181 | 1224298.4616 | 2659279.7716 | 1224288.7218 | 2659277.3335 | 1224267.8177
7 | 2659280.9181 | 1224298.4616 | 2659299.734 | 1224300.4296
8 | 2658815.4149 | 1224335.4921 | 2658798.6224 | 1224330.5706
9 | 2659363.4039 | 1224307.0887 | 2659299.734 | 1224300.4296
10 | 2659363.4039 | 1224307.0887 | 2659386.6046 | 1224305.6969 | 2659405.5125 | 1224297.5915 | 2659420.0603 | 1224288.7533 | 2659434.9586 | 1224275.9494 | 2659460.8775 | 1224248.4019 | 2659496.4721 | 1224209.455 | 2659551.0094 | 1224152.2084
11 | 2659716.3154 | 1224848.2593 | 2659716.1768 | 1224862.0758
12 | 2659716.3154 | 1224848.2593 | 2659721.3467 | 1224848.5544
13 | 2659716.3154 | 1224848.2593 | 2659716.356 | 1224844.2127 | 2659709.5271 | 1224836.4393
14 | 2659750.1586 | 1224818.1908 | 2659749.0436 | 1224827.3076 | 2659745.2207 | 1224844.091 | 2659737.6378 | 1224849.4961 | 2659721.3467 | 1224848.5544
15 | 2659721.3467 | 1224848.5544 | 2659723.4899 | 1224841.2379 | 2659725.6111 | 1224832.3424 | 2659726.1033 | 1224830.2554
16 | 2659709.5271 | 1224836.4393 | 2659702.7556 | 1224822.1846 | 2659702.7556 | 1224822.1846
17 | 2659589.1697 | 1224207.2803 | 2659592.2739 | 1224210.1642
18 | 2659551.0094 | 1224152.2084 | 2659562.2058 | 1224162.3602 | 2659574.4655 | 1224176.8808 | 2659580.445 | 1224189.304 | 2659580.9556 | 1224199.649 | 2659589.1697 | 1224207.2803
19 | 2659592.2739 | 1224210.1642 | 2659599.4892 | 1224216.8676 | 2659616.8767 | 1224227.3816 | 2659623.3676 | 1224228.8586 | 2659631.2297 | 1224220.8296
20 | 2659598.14 | 1224107.7852 | 2659580.926 | 1224120.8101 | 2659551.0094 | 1224152.2084
21 | 2659645.7356 | 1224209.2146 | 2659639.1884 | 1224212.5956 | 2659632.2082 | 1224219.8303 | 2659631.2297 | 1224220.8296
22 | 2659598.14 | 1224107.7852 | 2659654.26 | 1224049.4214 | 2659668.9911 | 1224036.016 | 2659678.1723 | 1224024.056 | 2659684.8565 | 1224010.0697 | 2659690.057 | 1223993.5559 | 2659695.578 | 1223971.5529 | 2659703.1631 | 1223953.184 | 2659703.9055 | 1223952.2314
23 | 2659598.14 | 1224107.7852 | 2659603.3652 | 1224114.5195 | 2659607.7831 | 1224119.4424
24 | 2659711.354 | 1224237.2121 | 2659697.3774 | 1224230.6234 | 2659645.7356 | 1224209.2146
25 | 2659723.7419 | 1223920.781 | 2659715.9992 | 1223936.7134 | 2659703.9055 | 1223952.2314
26 | 2659621.3574 | 1224150.2178 | 2659624.024 | 1224142.8998 | 2659616.0308 | 1224128.633 | 2659607.7831 | 1224119.4424
27 | 2659711.354 | 1224237.2121 | 2659708.3655 | 1224239.5836 | 2659700.0119 | 1224269.5966 | 2659692.0761 | 1224306.3403 | 2659689.3794 | 1224331.0288 | 2659683.2181 | 1224377.5965 | 2659676.0388 | 1224444.0221 | 2659673.3375 | 1224469.9447 | 2659675.2549 | 1224482.1272 | 2659680.8672 | 1224490.2886 | 2659695.0283 | 1224497.3239 | 2659722.1374 | 1224511.3824 | 2659739.5379 | 1224520.4849 | 2659755.7219 | 1224529.1638 | 2659770.2597 | 1224539.4385 | 2659777.4732 | 1224550.4623 | 2659779.7805 | 1224563.0601 | 2659775.1773 | 1224575.9887 | 2659763.6275 | 1224592.083 | 2659735.1339 | 1224635.1799 | 2659723.8471 | 1224665.8861 | 2659715.7727 | 1224699.8599 | 2659706.4771 | 1224734.6443 | 2659699.6798 | 1224763.7612 | 2659698.5235 | 1224797.4042 | 2659699.0319 | 1224800.3779 | 2659702.7556 | 1224822.1846
28 | 2659723.7419 | 1223920.781 | 2659741.2808 | 1223930.3053
29 | 2659723.7419 | 1223920.781 | 2659712.0961 | 1223916.1057 | 2659702.293 | 1223912.1135
30 | 2659644.8037 | 1223885.7365 | 2659649.7661 | 1223887.976
31 | 2659551.2198 | 1223841.6349 | 2659577.6794 | 1223853.5312 | 2659616.5291 | 1223872.9767 | 2659644.8037 | 1223885.7365
32 | 2659681.6017 | 1223903.4516 | 2659650.5439 | 1223888.327 | 2659649.7661 | 1223887.976
33 | 2659535.8732 | 1223834.2794 | 2659544.4714 | 1223838.6008 | 2659551.2198 | 1223841.6349
34 | 2659691.6035 | 1223907.7602 | 2659684.5539 | 1223904.8892 | 2659681.6017 | 1223903.4516
35 | 2659691.6035 | 1223907.7602 | 2659702.293 | 1223912.1135
36 | 2659751.1278 | 1223936.221 | 2659744.1423 | 1223931.8593 | 2659741.2808 | 1223930.3053
37 | 2659751.1278 | 1223936.221 | 2659767.5075 | 1223942.1891 | 2659780.1443 | 1223945.5848 | 2659794.2966 | 1223955.2347
38 | 2659751.1278 | 1223936.221 | 2659749.973 | 1223944.7592 | 2659749.0874 | 1223948.671
39 | 2658744.3092 | 1224268.4972 | 2658753.0479 | 1224295.3343
40 | 2658754.8417 | 1224300.8429 | 2658753.0479 | 1224295.3343
41 | 2658754.8417 | 1224300.8429 | 2658756.0824 | 1224304.6532
42 | 2658756.0824 | 1224304.6532 | 2658760.6593 | 1224311.8473
43 | 2658765.3937 | 1224316.1523 | 2658760.6593 | 1224311.8473
44 | 2658765.3937 | 1224316.1523 | 2658770.0644 | 1224346.0367
45 | 2658765.3937 | 1224316.1523 | 2658780.3551 | 1224325.2168 | 2658798.6224 | 1224330.5706
46 | 2658770.0644 | 1224346.0367 | 2658770.3502 | 1224347.8656 | 2658776.7675 | 1224395.1921 | 2658776.7675 | 1224395.1921

## bus_geodata
| x | y | coords
0 | 2659242.5121 | 1223606.8658
1 | 2659247.1623 | 1223584.5981
2 | 2659284.0887 | 1223608.614
3 | 2659316.1814 | 1223636.4239
4 | 2659025.3107 | 1224396.9404
5 | 2659280.9181 | 1224298.4616
6 | 2658815.4149 | 1224335.4921
7 | 2659277.3335 | 1224267.8177
8 | 2659299.734 | 1224300.4296
9 | 2659363.4039 | 1224307.0887
10 | 2659716.1768 | 1224862.0758
11 | 2659716.3154 | 1224848.2593
12 | 2659721.3467 | 1224848.5544
13 | 2659709.5271 | 1224836.4393
14 | 2659589.1697 | 1224207.2803
15 | 2659592.2739 | 1224210.1642
16 | 2659551.0094 | 1224152.2084
17 | 2659631.2297 | 1224220.8296
18 | 2659598.14 | 1224107.7852
19 | 2659645.7356 | 1224209.2146
20 | 2659703.9055 | 1223952.2314
21 | 2659607.7831 | 1224119.4424
22 | 2659711.354 | 1224237.2121
23 | 2659621.3574 | 1224150.2178
24 | 2659702.7556 | 1224822.1846
25 | 2659723.7419 | 1223920.781
26 | 2659644.8037 | 1223885.7365
27 | 2659649.7661 | 1223887.976
28 | 2659551.2198 | 1223841.6349
29 | 2659681.6017 | 1223903.4516
30 | 2659535.8732 | 1223834.2794
31 | 2659691.6035 | 1223907.7602
32 | 2659702.293 | 1223912.1135
33 | 2659741.2808 | 1223930.3053
34 | 2659751.1278 | 1223936.221
35 | 2659749.0874 | 1223948.671
36 | 2659794.2966 | 1223955.2347
37 | 2658744.3092 | 1224268.4972
38 | 2658753.0479 | 1224295.3343
39 | 2658754.8417 | 1224300.8429
40 | 2658756.0824 | 1224304.6532
41 | 2658760.6593 | 1224311.8473
42 | 2658765.3937 | 1224316.1523
43 | 2658770.0644 | 1224346.0367
44 | 2658798.6224 | 1224330.5706
45 | 2658776.7675 | 1224395.1921
46 | 2659750.1586 | 1224818.1908
47 | 2659726.1033 | 1224830.2554
48 | 2659535.8732 | 1223834.2794

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99079 | -0.064608 | 0.0076226 | 0.0019104
1 | 0.99105 | -0.062742 | 0 | 0
2 | 0.99154 | -0.059337 | 0 | 0
3 | 0.992 | -0.056043 | 0.010922 | 0.0027373
4 | 0.98603 | -0.099515 | 0 | 0
5 | 0.98713 | -0.091484 | 0 | 0
6 | 0.98532 | -0.10456 | 0.00054191 | 0.00013582
7 | 0.98712 | -0.091553 | 0.00021738 | 5.4481e-05
8 | 0.9872 | -0.090998 | 0.00059339 | 0.00014872
9 | 0.98748 | -0.088963 | 0 | 0
10 | 0.97919 | -0.14791 | 0.00032831 | 8.2283e-05
11 | 0.9792 | -0.14786 | 0 | 0
12 | 0.97919 | -0.14792 | 0 | 0
13 | 0.97923 | -0.14765 | 0.0031535 | 0.00079035
14 | 0.9877 | -0.08714 | 0.00035525 | 8.9034e-05
15 | 0.98765 | -0.0875 | 0.00097899 | 0.00024536
16 | 0.98857 | -0.080983 | 0 | 0
17 | 0.98715 | -0.091107 | 0.00013536 | 3.3925e-05
18 | 0.98966 | -0.073169 | 0 | 0
19 | 0.98695 | -0.092493 | 0 | 0
20 | 0.99298 | -0.049495 | 0.00010144 | 2.5423e-05
21 | 0.98965 | -0.073213 | 5.8758e-05 | 1.4726e-05
22 | 0.98621 | -0.097739 | 0 | 0
23 | 0.98964 | -0.073296 | 0.00022139 | 5.5486e-05
24 | 0.97933 | -0.1469 | 0.00255 | 0.00063908
25 | 0.99363 | -0.044874 | 0 | 0
26 | 0.99606 | -0.027654 | 0.00091772 | 0.00023
27 | 0.99589 | -0.028857 | 0.0015325 | 0.00038407
28 | 0.99944 | -0.0039201 | 0.00017738 | 4.4456e-05
29 | 0.99486 | -0.036138 | 0.00024871 | 6.2333e-05
30 | 1 | 0 | -0.042569 | -0.010485
31 | 0.99455 | -0.038355 | 0.0014271 | 0.00035766
32 | 0.99424 | -0.040538 | 0.00018874 | 4.7303e-05
33 | 0.99345 | -0.046151 | 0.0035742 | 0.00089578
34 | 0.9934 | -0.046471 | 0 | 0
35 | 0.99337 | -0.046687 | 0.0016868 | 0.00042274
36 | 0.99333 | -0.046983 | 0.0010598 | 0.0002656
37 | 0.98516 | -0.10573 | 0.00031037 | 7.7786e-05
38 | 0.98517 | -0.10564 | 0.00011925 | 2.9887e-05
39 | 0.98518 | -0.10561 | 0.00018179 | 4.5561e-05
40 | 0.98518 | -0.10559 | 7.8105e-05 | 1.9575e-05
41 | 0.98519 | -0.10553 | 8.4792e-05 | 2.1251e-05
42 | 0.9852 | -0.10548 | 0 | 0
43 | 0.98516 | -0.10574 | 0.00023718 | 5.9443e-05
44 | 0.98528 | -0.10486 | 4.5356e-05 | 1.1367e-05
45 | 0.98511 | -0.10606 | 0.00061656 | 0.00015453
46 | 0.97915 | -0.14819 | 0.00050579 | 0.00012676
47 | 0.97918 | -0.14803 | 0.00057217 | 0.0001434
48 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0076226 | -0.0019104 | 0.0076246 | 0.0019109 | 1.9691e-06 | 4.4717e-07 | 0.011448 | 0.011448 | 0.011448 | 0.99079 | -0.064608 | 0.99105 | -0.062742 | 4.24
1 | -0.0076246 | -0.0019109 | 0.0076282 | 0.0019117 | 3.5948e-06 | 8.1591e-07 | 0.011448 | 0.011448 | 0.011448 | 0.99105 | -0.062742 | 0.99154 | -0.059337 | 4.24
2 | -0.0076282 | -0.0019117 | 0.0076317 | 0.0019125 | 3.4785e-06 | 7.8897e-07 | 0.011448 | 0.011448 | 0.011448 | 0.99154 | -0.059337 | 0.992 | -0.056043 | 4.2399
3 | -0.018554 | -0.0046498 | 0.018699 | 0.0047016 | 0.00014498 | 5.1856e-05 | 0.027831 | 0.027829 | 0.027831 | 0.992 | -0.056043 | 1 | 0 | 10.3077
4 | -0.0022171 | -0.00055074 | 0.0022195 | 0.00054726 | 2.4063e-06 | -3.4797e-06 | 0.0033441 | 0.0033426 | 0.0033441 | 0.98603 | -0.099515 | 0.98713 | -0.091484 | 1.2386
5 | 0.0022171 | 0.00055074 | -0.0022156 | -0.00055294 | 1.5271e-06 | -2.201e-06 | 0.0033441 | 0.0033451 | 0.0033451 | 0.98603 | -0.099515 | 0.98532 | -0.10456 | 1.2389
6 | 0.00021739 | 5.4088e-05 | -0.00021738 | -5.4481e-05 | 2.0667e-09 | -3.9366e-07 | 0.00032755 | 0.00032769 | 0.00032769 | 0.98713 | -0.091484 | 0.98712 | -0.091553 | 0.12137
7 | -0.0024369 | -0.00060135 | 0.0024371 | 0.00060117 | 1.5901e-07 | -1.8071e-07 | 0.0036702 | 0.0036701 | 0.0036702 | 0.98713 | -0.091484 | 0.9872 | -0.090998 | 1.3593
8 | 0.0016737 | 0.00041713 | -0.0016736 | -0.00041732 | 6.9716e-08 | -1.9606e-07 | 0.0025267 | 0.0025268 | 0.0025268 | 0.98532 | -0.10456 | 0.98528 | -0.10486 | 0.93586
9 | -0.0030305 | -0.00074989 | 0.0030313 | 0.00074939 | 8.3222e-07 | -4.9864e-07 | 0.0045645 | 0.0045642 | 0.0045645 | 0.9872 | -0.090998 | 0.98748 | -0.088963 | 1.6906
10 | -0.0030313 | -0.00074939 | 0.0030346 | 0.00074744 | 3.2507e-06 | -1.9532e-06 | 0.0045642 | 0.0045631 | 0.0045642 | 0.98748 | -0.088963 | 0.98857 | -0.080983 | 1.6904
11 | -0.00032831 | -8.2283e-05 | 0.00032832 | 8.211e-05 | 2.1459e-09 | -1.7298e-07 | 0.00049892 | 0.00049886 | 0.00049892 | 0.97919 | -0.14791 | 0.9792 | -0.14786 | 0.18478
12 | 0.001078 | 0.00026922 | -0.001078 | -0.00026928 | 8.4111e-09 | -5.9975e-08 | 0.0016378 | 0.0016378 | 0.0016378 | 0.9792 | -0.14786 | 0.97919 | -0.14792 | 0.6066
13 | -0.0014063 | -0.00035133 | 0.0014064 | 0.00035117 | 4.1003e-08 | -1.653e-07 | 0.0021367 | 0.0021366 | 0.0021367 | 0.9792 | -0.14786 | 0.97923 | -0.14765 | 0.79136
14 | 0.00050581 | 0.00012612 | -0.00050579 | -0.00012676 | 1.9153e-08 | -6.4629e-07 | 0.00076842 | 0.00076865 | 0.00076865 | 0.97919 | -0.14792 | 0.97915 | -0.14819 | 0.28468
15 | 0.00057217 | 0.00014316 | -0.00057217 | -0.0001434 | 8.9216e-09 | -2.3447e-07 | 0.00086941 | 0.0008695 | 0.0008695 | 0.97919 | -0.14792 | 0.97918 | -0.14803 | 0.32204
16 | -0.0045599 | -0.0011415 | 0.0045604 | 0.0011415 | 4.7274e-07 | -1.6726e-08 | 0.0069287 | 0.0069286 | 0.0069287 | 0.97923 | -0.14765 | 0.97933 | -0.1469 | 2.5662
17 | 0.0082837 | 0.0020723 | -0.0082833 | -0.0020722 | 4.1169e-07 | 1.0412e-07 | 0.012478 | 0.012478 | 0.012478 | 0.9877 | -0.08714 | 0.98765 | -0.0875 | 4.6216
18 | -0.0086389 | -0.0021614 | 0.0086463 | 0.0021633 | 7.3416e-06 | 1.9338e-06 | 0.013014 | 0.013013 | 0.013014 | 0.9877 | -0.08714 | 0.98857 | -0.080983 | 4.8199
19 | 0.0073043 | 0.0018269 | -0.0073007 | -0.0018261 | 3.6312e-06 | 7.8188e-07 | 0.011003 | 0.011004 | 0.011004 | 0.98765 | -0.0875 | 0.98715 | -0.091107 | 4.0754
20 | -0.011681 | -0.0029107 | 0.011693 | 0.0029147 | 1.2503e-05 | 3.9764e-06 | 0.017576 | 0.017576 | 0.017576 | 0.98857 | -0.080983 | 0.98966 | -0.073169 | 6.5098
21 | 0.0071653 | 0.0017921 | -0.0071639 | -0.0017919 | 1.3697e-06 | 2.8626e-07 | 0.0108 | 0.0108 | 0.0108 | 0.98715 | -0.091107 | 0.98695 | -0.092493 | 3.9999
22 | -0.011974 | -0.0029842 | 0.012012 | 0.0029967 | 3.8913e-05 | 1.2484e-05 | 0.017997 | 0.017996 | 0.017997 | 0.98966 | -0.073169 | 0.99298 | -0.049495 | 6.6656
23 | 0.00028016 | 6.9551e-05 | -0.00028015 | -6.9745e-05 | 1.6745e-09 | -1.9387e-07 | 0.000421 | 0.00042107 | 0.00042107 | 0.98966 | -0.073169 | 0.98965 | -0.073213 | 0.15595
24 | 0.0071639 | 0.0017919 | -0.0071588 | -0.0017908 | 5.1805e-06 | 1.0836e-06 | 0.0108 | 0.0108 | 0.0108 | 0.98695 | -0.092493 | 0.98621 | -0.097739 | 4
25 | -0.012114 | -0.0030222 | 0.012122 | 0.0030246 | 7.6839e-06 | 2.4714e-06 | 0.018148 | 0.018148 | 0.018148 | 0.99298 | -0.049495 | 0.99363 | -0.044874 | 6.7216
26 | 0.0002214 | 5.5019e-05 | -0.00022139 | -5.5486e-05 | 2.522e-09 | -4.679e-07 | 0.00033272 | 0.00033289 | 0.00033289 | 0.98965 | -0.073213 | 0.98964 | -0.073296 | 0.12329
27 | 0.0071588 | 0.0017908 | -0.0071103 | -0.0017806 | 4.8426e-05 | 1.0197e-05 | 0.0108 | 0.010803 | 0.010803 | 0.98621 | -0.097739 | 0.97933 | -0.1469 | 4.0011
28 | 0.0063221 | 0.0015835 | -0.006321 | -0.0015833 | 1.1163e-06 | 1.7087e-07 | 0.0094674 | 0.0094674 | 0.0094674 | 0.99363 | -0.044874 | 0.99345 | -0.046151 | 3.5065
29 | -0.018444 | -0.0046081 | 0.018455 | 0.004612 | 1.1009e-05 | 3.9343e-06 | 0.027615 | 0.027615 | 0.027615 | 0.99363 | -0.044874 | 0.99424 | -0.040538 | 10.2279
30 | 0.021887 | 0.0054763 | -0.021884 | -0.005475 | 3.6314e-06 | 1.3258e-06 | 0.032694 | 0.032694 | 0.032694 | 0.99606 | -0.027654 | 0.99589 | -0.028857 | 12.109
31 | -0.022805 | -0.0057063 | 0.02288 | 0.0057338 | 7.4928e-05 | 2.7467e-05 | 0.034065 | 0.034065 | 0.034065 | 0.99606 | -0.027654 | 0.99944 | -0.0039201 | 12.6168
32 | 0.020351 | 0.0050909 | -0.020331 | -0.0050835 | 2.042e-05 | 7.3936e-06 | 0.030405 | 0.030405 | 0.030405 | 0.99589 | -0.028857 | 0.99486 | -0.036138 | 11.261
33 | -0.023057 | -0.0057783 | 0.02307 | 0.0057829 | 1.2518e-05 | 4.5913e-06 | 0.034329 | 0.034329 | 0.034329 | 0.99944 | -0.0039201 | 1 | 0 | 12.7144
34 | 0.020082 | 0.0050212 | -0.020076 | -0.005019 | 6.1323e-06 | 2.2171e-06 | 0.030033 | 0.030033 | 0.030033 | 0.99486 | -0.036138 | 0.99455 | -0.038355 | 11.1233
35 | 0.018649 | 0.0046613 | -0.018643 | -0.0046593 | 5.6053e-06 | 2.0062e-06 | 0.027898 | 0.027898 | 0.027898 | 0.99455 | -0.038355 | 0.99424 | -0.040538 | 10.3325
36 | 0.0027468 | 0.00068751 | -0.0027467 | -0.00068761 | 1.2136e-07 | -1.0211e-07 | 0.0041139 | 0.0041139 | 0.0041139 | 0.99345 | -0.046151 | 0.9934 | -0.046471 | 1.5237
37 | 0.0010598 | 0.00026501 | -0.0010598 | -0.0002656 | 7.4921e-08 | -5.8802e-07 | 0.0015873 | 0.0015875 | 0.0015875 | 0.9934 | -0.046471 | 0.99333 | -0.046983 | 0.58797
38 | 0.0016868 | 0.0004226 | -0.0016868 | -0.00042274 | 5.03e-08 | -1.4412e-07 | 0.0025266 | 0.0025267 | 0.0025267 | 0.9934 | -0.046471 | 0.99337 | -0.046687 | 0.93581
39 | -0.00031037 | -7.7786e-05 | 0.00031038 | 7.7429e-05 | 3.8695e-09 | -3.5789e-07 | 0.00046879 | 0.00046867 | 0.00046879 | 0.98516 | -0.10573 | 0.98517 | -0.10564 | 0.17363
40 | -0.00042963 | -0.00010732 | 0.00042963 | 0.00010724 | 1.5216e-09 | -7.3182e-08 | 0.00064879 | 0.00064876 | 0.00064879 | 0.98517 | -0.10564 | 0.98518 | -0.10561 | 0.24029
41 | -0.00061142 | -0.0001528 | 0.00061142 | 0.00015275 | 2.1317e-09 | -5.0204e-08 | 0.00092334 | 0.00092332 | 0.00092334 | 0.98518 | -0.10561 | 0.98518 | -0.10559 | 0.34198
42 | -0.00068953 | -0.00017233 | 0.00068953 | 0.00017222 | 5.7688e-09 | -1.0635e-07 | 0.0010413 | 0.0010412 | 0.0010413 | 0.98518 | -0.10559 | 0.98519 | -0.10553 | 0.38566
43 | -0.00077432 | -0.00019347 | 0.00077433 | 0.00019339 | 5.4595e-09 | -7.9383e-08 | 0.0011693 | 0.0011693 | 0.0011693 | 0.98519 | -0.10553 | 0.9852 | -0.10548 | 0.43308
44 | 0.0008538 | 0.00021297 | -0.00085377 | -0.00021335 | 3.1373e-08 | -3.7308e-07 | 0.0012892 | 0.0012893 | 0.0012893 | 0.9852 | -0.10548 | 0.98516 | -0.10574 | 0.47753
45 | -0.0016281 | -0.00040637 | 0.0016283 | 0.00040596 | 1.3776e-07 | -4.122e-07 | 0.0024585 | 0.0024583 | 0.0024585 | 0.9852 | -0.10548 | 0.98528 | -0.10486 | 0.91055
46 | 0.00061659 | 0.0001539 | -0.00061656 | -0.00015453 | 2.6844e-08 | -6.2133e-07 | 0.0009311 | 0.00093132 | 0.00093132 | 0.98516 | -0.10574 | 0.98511 | -0.10606 | 0.34493

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.042664 | 0.010508

## res_load
| p_mw | q_mvar
0 | 0.0076226 | 0.0019104
1 | 0.010922 | 0.0027373
2 | 0.00054191 | 0.00013582
3 | 0.00021738 | 5.4481e-05
4 | 0.00059339 | 0.00014872
5 | 0.00032831 | 8.2283e-05
6 | 0.0031535 | 0.00079035
7 | 0.00035525 | 8.9034e-05
8 | 0.00097899 | 0.00024536
9 | 0.00013536 | 3.3925e-05
10 | 0.00010144 | 2.5423e-05
11 | 5.8758e-05 | 1.4726e-05
12 | 0.00022139 | 5.5486e-05
13 | 0.00255 | 0.00063908
14 | 0.00091772 | 0.00023
15 | 0.0015325 | 0.00038407
16 | 0.00017738 | 4.4456e-05
17 | 0.00024871 | 6.2333e-05
18 | 9.5299e-05 | 2.3884e-05
19 | 0.0014271 | 0.00035766
20 | 0.00018874 | 4.7303e-05
21 | 0.0035742 | 0.00089578
22 | 0.0016868 | 0.00042274
23 | 0.0010598 | 0.0002656
24 | 0.00031037 | 7.7786e-05
25 | 0.00011925 | 2.9887e-05
26 | 0.00018179 | 4.5561e-05
27 | 7.8105e-05 | 1.9575e-05
28 | 8.4792e-05 | 2.1251e-05
29 | 0.00023718 | 5.9443e-05
30 | 4.5356e-05 | 1.1367e-05
31 | 0.00061656 | 0.00015453
32 | 0.00050579 | 0.00012676
33 | 0.00057217 | 0.0001434

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1