## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1081-17_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1081-17_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1081-17_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1081-17_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1081-17_0_3_node_18 | 0.4 | n |  | TRUE
5 | bus_LV_1081-17_0_3_node_47 | 0.4 | n |  | TRUE
6 | bus_LV_1081-17_0_3_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_1081-17_0_3_node_60 | 0.4 | n |  | TRUE
8 | bus_LV_1081-17_0_3_node_59 | 0.4 | n |  | TRUE
9 | bus_LV_1081-17_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1081-17_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1081-17_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1081-17_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1081-17_0_3_node_81 | 0.4 | n |  | TRUE
14 | bus_LV_1081-17_0_3_node_82 | 0.4 | n |  | TRUE
15 | bus_LV_1081-17_0_3_node_83 | 0.4 | n |  | TRUE
16 | bus_LV_1081-17_0_3_node_84 | 0.4 | n |  | TRUE
17 | bus_LV_1081-17_0_3_node_85 | 0.4 | n |  | TRUE
18 | bus_LV_1081-17_0_3_node_66 | 0.4 | n |  | TRUE
19 | bus_LV_1081-17_0_3_node_86 | 0.4 | n |  | TRUE
20 | bus_LV_1081-17_0_3_node_8 | 0.4 | n |  | TRUE
21 | bus_LV_1081-17_0_3_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_1081-17_0_3_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_1081-17_0_3_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1081-17_0_3_node_42 | 0.4 | n |  | TRUE
25 | bus_LV_1081-17_0_3_node_43 | 0.4 | n |  | TRUE
26 | bus_LV_1081-17_0_3_node_44 | 0.4 | n |  | TRUE
27 | bus_LV_1081-17_0_3_node_45 | 0.4 | n |  | TRUE
28 | bus_LV_1081-17_0_3_node_61 | 0.4 | n |  | TRUE
29 | bus_LV_1081-17_0_3_node_57 | 0.4 | n |  | TRUE
30 | bus_LV_1081-17_0_3_node_62 | 0.4 | n |  | TRUE
31 | bus_LV_1081-17_0_3_node_63 | 0.4 | n |  | TRUE
32 | bus_LV_1081-17_0_3_node_64 | 0.4 | n |  | TRUE
33 | bus_LV_1081-17_0_3_node_65 | 0.4 | n |  | TRUE
34 | bus_LV_1081-17_0_3_node_67 | 0.4 | n |  | TRUE
35 | bus_LV_1081-17_0_3_node_68 | 0.4 | n |  | TRUE
36 | bus_LV_1081-17_0_3_node_69 | 0.4 | n |  | TRUE
37 | bus_LV_1081-17_0_3_node_93 | 0.4 | n |  | TRUE
38 | bus_LV_1081-17_0_3_node_108 | 0.4 | n |  | TRUE
39 | bus_LV_1081-17_0_3_node_14 | 0.4 | n |  | TRUE
40 | bus_LV_1081-17_0_3_node_13 | 0.4 | n |  | TRUE
41 | bus_LV_1081-17_0_3_node_90 | 0.4 | n |  | TRUE
42 | bus_LV_1081-17_0_3_node_109 | 0.4 | n |  | TRUE
43 | bus_LV_1081-17_0_3_node_107 | 0.4 | n |  | TRUE
44 | bus_LV_1081-17_0_3_node_106 | 0.4 | n |  | TRUE
45 | bus_LV_1081-17_0_3_node_131 | 0.4 | n |  | TRUE
46 | bus_LV_1081-17_0_3_node_15 | 0.4 | n |  | TRUE
47 | bus_LV_1081-17_0_3_node_133 | 0.4 | n |  | TRUE
48 | bus_LV_1081-17_0_3_node_16 | 0.4 | n |  | TRUE
49 | bus_LV_1081-17_0_3_node_130 | 0.4 | n |  | TRUE
50 | bus_LV_1081-17_0_3_node_129 | 0.4 | n |  | TRUE
51 | bus_LV_1081-17_0_3_node_104 | 0.4 | n |  | TRUE
52 | bus_LV_1081-17_0_3_node_55 | 0.4 | n |  | TRUE
53 | bus_LV_1081-17_0_3_node_56 | 0.4 | n |  | TRUE
54 | bus_LV_1081-17_0_3_node_52 | 0.4 | n |  | TRUE
55 | bus_LV_1081-17_0_3_node_51 | 0.4 | n |  | TRUE
56 | bus_LV_1081-17_0_3_node_46 | 0.4 | n |  | TRUE
57 | bus_LV_1081-17_0_3_node_48 | 0.4 | n |  | TRUE
58 | bus_LV_1081-17_0_3_node_49 | 0.4 | n |  | TRUE
59 | bus_LV_1081-17_0_3_node_50 | 0.4 | n |  | TRUE
60 | bus_LV_1081-17_0_3_node_53 | 0.4 | n |  | TRUE
61 | bus_LV_1081-17_0_3_node_54 | 0.4 | n |  | TRUE
62 | bus_LV_1081-17_0_3_node_58 | 0.4 | n |  | TRUE
63 | bus_LV_1081-17_0_3_node_19 | 0.4 | n |  | TRUE
64 | bus_LV_1081-17_0_3_node_20 | 0.4 | n |  | TRUE
65 | bus_LV_1081-17_0_3_node_21 | 0.4 | n |  | TRUE
66 | bus_LV_1081-17_0_3_node_22 | 0.4 | n |  | TRUE
67 | bus_LV_1081-17_0_3_node_23 | 0.4 | n |  | TRUE
68 | bus_LV_1081-17_0_3_node_25 | 0.4 | n |  | TRUE
69 | bus_LV_1081-17_0_3_node_24 | 0.4 | n |  | TRUE
70 | bus_LV_1081-17_0_3_node_135 | 0.4 | n |  | TRUE
71 | bus_LV_1081-17_0_3_node_132 | 0.4 | n |  | TRUE
72 | bus_LV_1081-17_0_3_node_26 | 0.4 | n |  | TRUE
73 | bus_LV_1081-17_0_3_node_34 | 0.4 | n |  | TRUE
74 | bus_LV_1081-17_0_3_node_27 | 0.4 | n |  | TRUE
75 | bus_LV_1081-17_0_3_node_28 | 0.4 | n |  | TRUE
76 | bus_LV_1081-17_0_3_node_29 | 0.4 | n |  | TRUE
77 | bus_LV_1081-17_0_3_node_30 | 0.4 | n |  | TRUE
78 | bus_LV_1081-17_0_3_node_31 | 0.4 | n |  | TRUE
79 | bus_LV_1081-17_0_3_node_32 | 0.4 | n |  | TRUE
80 | bus_LV_1081-17_0_3_node_33 | 0.4 | n |  | TRUE
81 | bus_LV_1081-17_0_3_node_35 | 0.4 | n |  | TRUE
82 | bus_LV_1081-17_0_3_node_36 | 0.4 | n |  | TRUE
83 | bus_LV_1081-17_0_3_node_37 | 0.4 | n |  | TRUE
84 | bus_LV_1081-17_0_3_node_38 | 0.4 | n |  | TRUE
85 | bus_LV_1081-17_0_3_node_39 | 0.4 | n |  | TRUE
86 | bus_LV_1081-17_0_3_node_41 | 0.4 | n |  | TRUE
87 | bus_LV_1081-17_0_3_node_40 | 0.4 | n |  | TRUE
88 | bus_LV_1081-17_0_3_node_70 | 0.4 | n |  | TRUE
89 | bus_LV_1081-17_0_3_node_72 | 0.4 | n |  | TRUE
90 | bus_LV_1081-17_0_3_node_73 | 0.4 | n |  | TRUE
91 | bus_LV_1081-17_0_3_node_74 | 0.4 | n |  | TRUE
92 | bus_LV_1081-17_0_3_node_110 | 0.4 | n |  | TRUE
93 | bus_LV_1081-17_0_3_node_111 | 0.4 | n |  | TRUE
94 | bus_LV_1081-17_0_3_node_80 | 0.4 | n |  | TRUE
95 | bus_LV_1081-17_0_3_node_76 | 0.4 | n |  | TRUE
96 | bus_LV_1081-17_0_3_node_78 | 0.4 | n |  | TRUE
97 | bus_LV_1081-17_0_3_node_75 | 0.4 | n |  | TRUE
98 | bus_LV_1081-17_0_3_node_77 | 0.4 | n |  | TRUE
99 | bus_LV_1081-17_0_3_node_79 | 0.4 | n |  | TRUE
100 | bus_LV_1081-17_0_3_node_88 | 0.4 | n |  | TRUE
101 | bus_LV_1081-17_0_3_node_89 | 0.4 | n |  | TRUE
102 | bus_LV_1081-17_0_3_node_91 | 0.4 | n |  | TRUE
103 | bus_LV_1081-17_0_3_node_92 | 0.4 | n |  | TRUE
104 | bus_LV_1081-17_0_3_node_113 | 0.4 | n |  | TRUE
105 | bus_LV_1081-17_0_3_node_95 | 0.4 | n |  | TRUE
106 | bus_LV_1081-17_0_3_node_94 | 0.4 | n |  | TRUE
107 | bus_LV_1081-17_0_3_node_96 | 0.4 | n |  | TRUE
108 | bus_LV_1081-17_0_3_node_98 | 0.4 | n |  | TRUE
109 | bus_LV_1081-17_0_3_node_100 | 0.4 | n |  | TRUE
110 | bus_LV_1081-17_0_3_node_99 | 0.4 | n |  | TRUE
111 | bus_LV_1081-17_0_3_node_105 | 0.4 | n |  | TRUE
112 | bus_LV_1081-17_0_3_node_102 | 0.4 | n |  | TRUE
113 | bus_LV_1081-17_0_3_node_101 | 0.4 | n |  | TRUE
114 | bus_LV_1081-17_0_3_node_122 | 0.4 | n |  | TRUE
115 | bus_LV_1081-17_0_3_node_121 | 0.4 | n |  | TRUE
116 | bus_LV_1081-17_0_3_node_125 | 0.4 | n |  | TRUE
117 | bus_LV_1081-17_0_3_node_124 | 0.4 | n |  | TRUE
118 | bus_LV_1081-17_0_3_node_103 | 0.4 | n |  | TRUE
119 | bus_LV_1081-17_0_3_node_123 | 0.4 | n |  | TRUE
120 | bus_LV_1081-17_0_3_node_120 | 0.4 | n |  | TRUE
121 | bus_LV_1081-17_0_3_node_126 | 0.4 | n |  | TRUE
122 | bus_LV_1081-17_0_3_node_112 | 0.4 | n |  | TRUE
123 | bus_LV_1081-17_0_3_node_114 | 0.4 | n |  | TRUE
124 | bus_LV_1081-17_0_3_node_115 | 0.4 | n |  | TRUE
125 | bus_LV_1081-17_0_3_node_116 | 0.4 | n |  | TRUE
126 | bus_LV_1081-17_0_3_node_117 | 0.4 | n |  | TRUE
127 | bus_LV_1081-17_0_3_node_118 | 0.4 | n |  | TRUE
128 | bus_LV_1081-17_0_3_node_119 | 0.4 | n |  | TRUE
129 | bus_LV_1081-17_0_3_node_127 | 0.4 | n |  | TRUE
130 | bus_LV_1081-17_0_3_node_128 | 0.4 | n |  | TRUE
131 | bus_MV_470_2_node_124 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1081-17_0_3_load_0 | 0 | 0.001634 | 0.00040953 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1081-17_0_3_load_1 | 1 | 0.00043942 | 0.00011013 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1081-17_0_3_load_4 | 3 | 0.0011201 | 0.00028072 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1081-17_0_3_load_18 | 4 | 0.016338 | 0.0040946 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1081-17_0_3_load_47 | 5 | 0.0048018 | 0.0012034 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1081-17_0_3_load_17 | 6 | 0.0040863 | 0.0010241 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1081-17_0_3_load_60 | 7 | 0.00098151 | 0.00024599 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1081-17_0_3_load_59 | 8 | 0.00064059 | 0.00016055 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1081-17_0_3_load_5 | 9 | 0.0057701 | 0.0014461 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1081-17_0_3_load_6 | 10 | 0.003504 | 0.00087819 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1081-17_0_3_load_7 | 11 | 0.0031343 | 0.00078553 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1081-17_0_3_load_9 | 12 | 0.00071314 | 0.00017873 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1081-17_0_3_load_81 | 13 | 0.0015586 | 0.00039061 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1081-17_0_3_load_82 | 14 | 0.00078735 | 0.00019733 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1081-17_0_3_load_83 | 15 | 0.00031929 | 8.0023e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1081-17_0_3_load_84 | 16 | 0.00041237 | 0.00010335 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1081-17_0_3_load_85 | 17 | 0.00098135 | 0.00024595 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1081-17_0_3_load_66 | 18 | 0.00063371 | 0.00015882 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1081-17_0_3_load_86 | 19 | 0.00046069 | 0.00011546 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1081-17_0_3_load_8 | 20 | 0.0017106 | 0.00042871 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1081-17_0_3_load_10 | 21 | 0.0014856 | 0.00037233 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1081-17_0_3_load_11 | 22 | 0.00045648 | 0.00011441 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1081-17_0_3_load_42 | 24 | 0.0088313 | 0.0022133 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1081-17_0_3_load_61 | 28 | 0.00068236 | 0.00017101 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1081-17_0_3_load_57 | 29 | 0.00047241 | 0.0001184 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1081-17_0_3_load_64 | 32 | 0.00051573 | 0.00012925 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1081-17_0_3_load_65 | 33 | 0.00021018 | 5.2676e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1081-17_0_3_load_67 | 34 | 0.00050057 | 0.00012545 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1081-17_0_3_load_68 | 35 | 0.00094623 | 0.00023715 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1081-17_0_3_load_69 | 36 | 0.00028287 | 7.0893e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1081-17_0_3_load_108 | 38 | 0.0013048 | 0.00032702 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1081-17_0_3_load_109 | 42 | 0.00023507 | 5.8913e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1081-17_0_3_load_106 | 44 | 0.0010808 | 0.00027086 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1081-17_0_3_load_131 | 45 | 0.0036366 | 0.00091142 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1081-17_0_3_load_133 | 47 | 0.0022568 | 0.0005656 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1081-17_0_3_load_16 | 48 | 0.0073677 | 0.0018465 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1081-17_0_3_load_130 | 49 | 0.0027675 | 0.00069361 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1081-17_0_3_load_129 | 50 | 0.017412 | 0.0043639 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1081-17_0_3_load_104 | 51 | 0.0010484 | 0.00026275 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1081-17_0_3_load_55 | 52 | 0.00040803 | 0.00010226 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1081-17_0_3_load_56 | 53 | 0.0025413 | 0.00063692 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1081-17_0_3_load_52 | 54 | 0.00025431 | 6.3736e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1081-17_0_3_load_46 | 56 | 0.0048019 | 0.0012035 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1081-17_0_3_load_48 | 57 | 0.00056628 | 0.00014192 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1081-17_0_3_load_49 | 58 | 0.00056639 | 0.00014195 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1081-17_0_3_load_50 | 59 | 0.00069316 | 0.00017372 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1081-17_0_3_load_53 | 60 | 0.00038709 | 9.7015e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1081-17_0_3_load_54 | 61 | 0.0016851 | 0.00042232 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1081-17_0_3_load_58 | 62 | 0.0005622 | 0.0001409 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1081-17_0_3_load_19 | 63 | 0.0017348 | 0.00043477 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1081-17_0_3_load_21 | 65 | 0.015146 | 0.003796 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1081-17_0_3_load_25 | 68 | 0.0049589 | 0.0012428 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1081-17_0_3_load_24 | 69 | 0.013894 | 0.0034823 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1081-17_0_3_load_135 | 70 | 0.005835 | 0.0014624 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1081-17_0_3_load_132 | 71 | 0.0052266 | 0.0013099 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1081-17_0_3_load_26 | 72 | 0.0074962 | 0.0018787 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1081-17_0_3_load_27 | 74 | 0.00099317 | 0.00024891 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1081-17_0_3_load_28 | 75 | 0.00028614 | 7.1714e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1081-17_0_3_load_31 | 78 | 0.00051413 | 0.00012885 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1081-17_0_3_load_32 | 79 | 0.00021467 | 5.3802e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1081-17_0_3_load_35 | 81 | 0.00024442 | 6.1257e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1081-17_0_3_load_36 | 82 | 0.00069264 | 0.00017359 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1081-17_0_3_load_37 | 83 | 0.00024222 | 6.0707e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1081-17_0_3_load_38 | 84 | 0.00016737 | 4.1947e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1081-17_0_3_load_40 | 87 | 0.00010565 | 2.6478e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1081-17_0_3_load_70 | 88 | 0.0015284 | 0.00038305 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1081-17_0_3_load_74 | 91 | 0.00018142 | 4.5468e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1081-17_0_3_load_111 | 93 | 0.00038032 | 9.5318e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1081-17_0_3_load_80 | 94 | 0.00017197 | 4.3101e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1081-17_0_3_load_76 | 95 | 0.00023796 | 5.964e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1081-17_0_3_load_78 | 96 | 0.00018646 | 4.6732e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1081-17_0_3_load_75 | 97 | 0.0001813 | 4.5437e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1081-17_0_3_load_77 | 98 | 0.0013506 | 0.0003385 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1081-17_0_3_load_79 | 99 | 0.00035647 | 8.934e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1081-17_0_3_load_88 | 100 | 0.0062055 | 0.0015552 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1081-17_0_3_load_89 | 101 | 0.0079502 | 0.0019925 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1081-17_0_3_load_113 | 104 | 0.0016726 | 0.0004192 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1081-17_0_3_load_95 | 105 | 0.0016726 | 0.0004192 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1081-17_0_3_load_94 | 106 | 0.0006868 | 0.00017213 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1081-17_0_3_load_96 | 107 | 0.0060448 | 0.001515 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1081-17_0_3_load_102 | 112 | 0.0034075 | 0.000854 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1081-17_0_3_load_122 | 114 | 0.0023576 | 0.00059087 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1081-17_0_3_load_121 | 115 | 0.0060218 | 0.0015092 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1081-17_0_3_load_124 | 117 | 0.0032078 | 0.00080394 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1081-17_0_3_load_103 | 118 | 0.0063211 | 0.0015842 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1081-17_0_3_load_123 | 119 | 0.0014237 | 0.00035681 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1081-17_0_3_load_120 | 120 | 0.0016444 | 0.00041213 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1081-17_0_3_load_126 | 121 | 0.0023927 | 0.00059966 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1081-17_0_3_load_112 | 122 | 0.00070606 | 0.00017696 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1081-17_0_3_load_114 | 123 | 0.0031539 | 0.00079045 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1081-17_0_3_load_115 | 124 | 0.0023708 | 0.00059418 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1081-17_0_3_load_116 | 125 | 0.0011823 | 0.00029632 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1081-17_0_3_load_117 | 126 | 0.0016402 | 0.00041107 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1081-17_0_3_load_118 | 127 | 0.0010442 | 0.00026171 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1081-17_0_3_load_119 | 128 | 0.00058731 | 0.00014719 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1081-17_0_3_load_127 | 129 | 0.0022357 | 0.00056033 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1081-17_0_3_load_128 | 130 | 0.0017115 | 0.00042894 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 49 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1081-17_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.045872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1081-17_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.24462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1081-17_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.021689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1081-17_0_3_line_3 | NAYY 4x150 SE | 3 | 7 | 0.013015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1081-17_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.097432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1081-17_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.019255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1081-17_0_3_line_6 | NAYY 4x150 SE | 5 | 56 | 0.0024126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1081-17_0_3_line_7 | NAYY 4x150 SE | 6 | 48 | 0.013002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1081-17_0_3_line_8 | NAYY 4x150 SE | 7 | 8 | 0.035185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1081-17_0_3_line_9 | NAYY 4x150 SE | 8 | 61 | 0.014517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1081-17_0_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.0015502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1081-17_0_3_line_11 | NAYY 4x150 SE | 9 | 11 | 0.045641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1081-17_0_3_line_12 | NAYY 4x150 SE | 11 | 12 | 0.015661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1081-17_0_3_line_13 | NAYY 4x150 SE | 12 | 23 | 0.023595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1081-17_0_3_line_14 | NAYY 4x150 SE | 13 | 14 | 0.026461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1081-17_0_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.010584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1081-17_0_3_line_16 | NAYY 4x150 SE | 14 | 16 | 0.027672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1081-17_0_3_line_17 | NAYY 4x150 SE | 15 | 17 | 0.012965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1081-17_0_3_line_18 | NAYY 4x150 SE | 16 | 18 | 0.17321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1081-17_0_3_line_19 | NAYY 4x150 SE | 17 | 19 | 0.0055587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1081-17_0_3_line_20 | NAYY 4x150 SE | 18 | 34 | 0.01632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1081-17_0_3_line_21 | NAYY 4x150 SE | 18 | 33 | 0.015143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1081-17_0_3_line_22 | NAYY 4x150 SE | 20 | 21 | 0.020951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1081-17_0_3_line_23 | NAYY 4x150 SE | 20 | 22 | 0.016078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1081-17_0_3_line_24 | NAYY 4x150 SE | 21 | 37 | 0.015344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1081-17_0_3_line_25 | NAYY 4x150 SE | 22 | 38 | 0.0091455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1081-17_0_3_line_26 | NAYY 4x150 SE | 23 | 39 | 0.0084093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1081-17_0_3_line_27 | NAYY 4x150 SE | 24 | 25 | 0.094417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1081-17_0_3_line_28 | NAYY 4x150 SE | 25 | 26 | 0.005338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1081-17_0_3_line_29 | NAYY 4x150 SE | 25 | 27 | 0.001942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1081-17_0_3_line_30 | NAYY 4x150 SE | 26 | 28 | 0.034354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1081-17_0_3_line_31 | NAYY 4x150 SE | 27 | 29 | 0.054123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1081-17_0_3_line_32 | NAYY 4x150 SE | 28 | 30 | 0.023204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1081-17_0_3_line_33 | NAYY 4x150 SE | 29 | 53 | 0.00048346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1081-17_0_3_line_34 | NAYY 4x150 SE | 30 | 31 | 0.02069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1081-17_0_3_line_35 | NAYY 4x150 SE | 31 | 32 | 0.088928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1081-17_0_3_line_36 | NAYY 4x150 SE | 32 | 33 | 0.011278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1081-17_0_3_line_37 | NAYY 4x150 SE | 34 | 35 | 0.011059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1081-17_0_3_line_38 | NAYY 4x150 SE | 35 | 36 | 0.013329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1081-17_0_3_line_39 | NAYY 4x150 SE | 37 | 40 | 0.032971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1081-17_0_3_line_40 | NAYY 4x150 SE | 37 | 41 | 0.075101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1081-17_0_3_line_41 | NAYY 4x150 SE | 38 | 42 | 0.026273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1081-17_0_3_line_42 | NAYY 4x150 SE | 39 | 45 | 0.027863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
43 | LV_1081-17_0_3_line_43 | NAYY 4x150 SE | 39 | 46 | 0.02491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
44 | LV_1081-17_0_3_line_44 | NAYY 4x150 SE | 39 | 47 | 0.023483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1081-17_0_3_line_45 | NAYY 4x150 SE | 40 | 43 | 0.00486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1081-17_0_3_line_46 | NAYY 4x150 SE | 40 | 44 | 0.033903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1081-17_0_3_line_47 | NAYY 4x150 SE | 41 | 103 | 0.019847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1081-17_0_3_line_48 | NAYY 4x150 SE | 42 | 92 | 0.040928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1081-17_0_3_line_49 | NAYY 4x150 SE | 43 | 49 | 0.033021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
50 | LV_1081-17_0_3_line_50 | NAYY 4x150 SE | 43 | 45 | 0.032004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
51 | LV_1081-17_0_3_line_51 | NAYY 4x150 SE | 43 | 50 | 0.030669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1081-17_0_3_line_52 | NAYY 4x150 SE | 44 | 51 | 0.02867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1081-17_0_3_line_53 | NAYY 4x150 SE | 46 | 48 | 0.018241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_1081-17_0_3_line_54 | NAYY 4x150 SE | 49 | 71 | 0.01432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1081-17_0_3_line_55 | NAYY 4x150 SE | 51 | 118 | 0.023323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1081-17_0_3_line_56 | NAYY 4x150 SE | 52 | 53 | 0.02285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1081-17_0_3_line_57 | NAYY 4x150 SE | 52 | 54 | 0.0060285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1081-17_0_3_line_58 | NAYY 4x150 SE | 54 | 55 | 0.032703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1081-17_0_3_line_59 | NAYY 4x150 SE | 55 | 60 | 0.016204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1081-17_0_3_line_60 | NAYY 4x150 SE | 55 | 61 | 0.028102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1081-17_0_3_line_61 | NAYY 4x150 SE | 55 | 59 | 0.05514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1081-17_0_3_line_62 | NAYY 4x150 SE | 56 | 57 | 0.024617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1081-17_0_3_line_63 | NAYY 4x150 SE | 57 | 58 | 0.0059309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1081-17_0_3_line_64 | NAYY 4x150 SE | 58 | 59 | 0.060241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1081-17_0_3_line_65 | NAYY 4x150 SE | 60 | 62 | 0.042244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1081-17_0_3_line_66 | NAYY 4x150 SE | 63 | 64 | 0.024607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1081-17_0_3_line_67 | NAYY 4x150 SE | 63 | 65 | 0.013896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1081-17_0_3_line_68 | NAYY 4x150 SE | 64 | 66 | 0.025253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1081-17_0_3_line_69 | NAYY 4x150 SE | 64 | 67 | 0.036475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1081-17_0_3_line_70 | NAYY 4x150 SE | 66 | 68 | 0.040364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1081-17_0_3_line_71 | NAYY 4x150 SE | 66 | 69 | 0.025755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1081-17_0_3_line_72 | NAYY 4x150 SE | 67 | 70 | 0.026184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1081-17_0_3_line_73 | NAYY 4x150 SE | 67 | 71 | 0.038185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1081-17_0_3_line_74 | NAYY 4x150 SE | 68 | 72 | 0.034662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1081-17_0_3_line_75 | NAYY 4x150 SE | 72 | 73 | 0.28911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1081-17_0_3_line_76 | NAYY 4x150 SE | 73 | 81 | 0.092949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1081-17_0_3_line_77 | NAYY 4x150 SE | 73 | 80 | 0.10555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1081-17_0_3_line_78 | NAYY 4x150 SE | 74 | 75 | 0.02891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1081-17_0_3_line_79 | NAYY 4x150 SE | 75 | 76 | 0.016662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1081-17_0_3_line_80 | NAYY 4x150 SE | 76 | 77 | 0.024043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1081-17_0_3_line_81 | NAYY 4x150 SE | 76 | 78 | 0.033148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1081-17_0_3_line_82 | NAYY 4x150 SE | 77 | 79 | 0.069228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1081-17_0_3_line_83 | NAYY 4x150 SE | 79 | 80 | 0.027027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1081-17_0_3_line_84 | NAYY 4x150 SE | 81 | 82 | 0.076204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1081-17_0_3_line_85 | NAYY 4x150 SE | 82 | 83 | 0.021853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1081-17_0_3_line_86 | NAYY 4x150 SE | 83 | 84 | 0.01735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1081-17_0_3_line_87 | NAYY 4x150 SE | 84 | 85 | 0.0083414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1081-17_0_3_line_88 | NAYY 4x150 SE | 85 | 86 | 0.081433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1081-17_0_3_line_89 | NAYY 4x150 SE | 86 | 87 | 0.064787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1081-17_0_3_line_90 | NAYY 4x150 SE | 88 | 89 | 0.046728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1081-17_0_3_line_91 | NAYY 4x150 SE | 89 | 90 | 0.068303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1081-17_0_3_line_92 | NAYY 4x150 SE | 89 | 91 | 0.049111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1081-17_0_3_line_93 | NAYY 4x150 SE | 90 | 94 | 0.023268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1081-17_0_3_line_94 | NAYY 4x150 SE | 90 | 92 | 0.11746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1081-17_0_3_line_95 | NAYY 4x150 SE | 91 | 95 | 0.0011666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1081-17_0_3_line_96 | NAYY 4x150 SE | 92 | 93 | 0.01953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1081-17_0_3_line_97 | NAYY 4x150 SE | 93 | 122 | 0.029531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1081-17_0_3_line_98 | NAYY 4x150 SE | 94 | 96 | 0.018836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1081-17_0_3_line_99 | NAYY 4x150 SE | 95 | 97 | 0.059627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1081-17_0_3_line_100 | NAYY 4x150 SE | 96 | 98 | 0.01204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1081-17_0_3_line_101 | NAYY 4x150 SE | 98 | 99 | 0.0046516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1081-17_0_3_line_102 | NAYY 4x150 SE | 100 | 101 | 0.00068991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1081-17_0_3_line_103 | NAYY 4x150 SE | 101 | 102 | 0.041135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1081-17_0_3_line_104 | NAYY 4x150 SE | 102 | 104 | 0.010691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1081-17_0_3_line_105 | NAYY 4x150 SE | 103 | 105 | 0.018333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1081-17_0_3_line_106 | NAYY 4x150 SE | 103 | 104 | 0.012414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1081-17_0_3_line_107 | NAYY 4x150 SE | 105 | 106 | 0.0074515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1081-17_0_3_line_108 | NAYY 4x150 SE | 107 | 108 | 0.017478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1081-17_0_3_line_109 | NAYY 4x150 SE | 108 | 109 | 0.004483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1081-17_0_3_line_110 | NAYY 4x150 SE | 109 | 113 | 0.033776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1081-17_0_3_line_111 | NAYY 4x150 SE | 109 | 114 | 0.0068612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1081-17_0_3_line_112 | NAYY 4x150 SE | 110 | 111 | 0.006384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1081-17_0_3_line_113 | NAYY 4x150 SE | 110 | 112 | 0.010034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1081-17_0_3_line_114 | NAYY 4x150 SE | 111 | 116 | 0.036506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1081-17_0_3_line_115 | NAYY 4x150 SE | 111 | 117 | 0.0051398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1081-17_0_3_line_116 | NAYY 4x150 SE | 112 | 118 | 0.020316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1081-17_0_3_line_117 | NAYY 4x150 SE | 113 | 115 | 0.027365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1081-17_0_3_line_118 | NAYY 4x150 SE | 114 | 119 | 0.014905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1081-17_0_3_line_119 | NAYY 4x150 SE | 115 | 120 | 0.028068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1081-17_0_3_line_120 | NAYY 4x150 SE | 116 | 121 | 0.018018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1081-17_0_3_line_121 | NAYY 4x150 SE | 117 | 119 | 0.00055585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_1081-17_0_3_line_122 | NAYY 4x150 SE | 120 | 128 | 0.0081825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_1081-17_0_3_line_123 | NAYY 4x150 SE | 121 | 129 | 0.00054215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_1081-17_0_3_line_124 | NAYY 4x150 SE | 123 | 124 | 0.012093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_1081-17_0_3_line_125 | NAYY 4x150 SE | 124 | 125 | 0.028711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_1081-17_0_3_line_126 | NAYY 4x150 SE | 125 | 126 | 0.026673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_1081-17_0_3_line_127 | NAYY 4x150 SE | 126 | 127 | 0.019422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_1081-17_0_3_line_128 | NAYY 4x150 SE | 127 | 128 | 0.017294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_1081-17_0_3_line_129 | NAYY 4x150 SE | 129 | 130 | 0.024198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1081-17_0_3_trafo_130 | 0.25 MVA 20/0.4 kV | 131 | 49 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2658643.9849 | 1226495.9799 | 2658639.1882 | 1226496.0757 | 2658620.4461 | 1226502.0171 | 2658605.5944 | 1226503.1382 | 2658601.0235 | 1226498.4902
1 | 2658559.4887 | 1226257.4175 | 2658601.0235 | 1226498.4902
2 | 2658559.4887 | 1226257.4175 | 2658540.9318 | 1226246.1909
3 | 2658540.9318 | 1226246.1909 | 2658538.2853 | 1226244.5898 | 2658531.1503 | 1226237.6953
4 | 2658456.3134 | 1225950.2089 | 2658471.0435 | 1226046.521
5 | 2658456.3134 | 1225950.2089 | 2658441.4826 | 1225949.0515 | 2658437.2959 | 1225950.3369
6 | 2658470.6803 | 1226048.9061 | 2658471.0435 | 1226046.521
7 | 2658424.6201 | 1225950.9268 | 2658431.9027 | 1225951.9926 | 2658437.2959 | 1225950.3369
8 | 2658504.4594 | 1226214.8774 | 2658518.0123 | 1226225.0003 | 2658531.1503 | 1226237.6953
9 | 2658504.4594 | 1226214.8774 | 2658501.7516 | 1226212.855 | 2658491.856 | 1226207.7447
10 | 2658334.1994 | 1225934.0345 | 2658333.1499 | 1225932.8935
11 | 2658334.1994 | 1225934.0345 | 2658338.193 | 1225938.3762 | 2658371.7283 | 1225950.7016 | 2658374.9506 | 1225948.3094
12 | 2658384.5022 | 1225935.8987 | 2658374.9506 | 1225948.3094 | 2658374.9506 | 1225948.3094
13 | 2658404.4008 | 1225925.8173 | 2658401.3999 | 1225925.7323 | 2658392.6785 | 1225927.6924 | 2658387.5197 | 1225931.9779 | 2658384.5022 | 1225935.8987
14 | 2658099.8212 | 1226285.1107 | 2658111.3062 | 1226289.4351 | 2658120.1067 | 1226293.279 | 2658124.692 | 1226293.3238
15 | 2658099.8212 | 1226285.1107 | 2658089.9157 | 1226281.381
16 | 2658150.2788 | 1226285.0574 | 2658134.5448 | 1226293.4201 | 2658124.692 | 1226293.3238
17 | 2658077.782 | 1226276.8124 | 2658089.9157 | 1226281.381
18 | 2658318.4814 | 1226326.3972 | 2658150.2788 | 1226285.0574
19 | 2658077.782 | 1226276.8124 | 2658072.5799 | 1226274.8536
20 | 2658314.6582 | 1226342.2627 | 2658318.4814 | 1226326.3972
21 | 2658322.029 | 1226311.6751 | 2658318.4814 | 1226326.3972
22 | 2658341.341 | 1225849.2395 | 2658362.0131 | 1225852.6447
23 | 2658341.341 | 1225849.2395 | 2658325.477 | 1225846.6278
24 | 2658377.1534 | 1225855.1387 | 2658362.0131 | 1225852.6447
25 | 2658316.453 | 1225845.1422 | 2658325.477 | 1225846.6278
26 | 2658410.189 | 1225923.0501 | 2658409.857 | 1225925.9821 | 2658404.4008 | 1225925.8173
27 | 2658363.3372 | 1226144.6421 | 2658385.686 | 1226052.9078
28 | 2658363.3372 | 1226144.6421 | 2658358.2913 | 1226142.8582
29 | 2658362.8715 | 1226146.5276 | 2658363.3372 | 1226144.6421
30 | 2658358.2913 | 1226142.8582 | 2658350.2127 | 1226176.2485
31 | 2658362.8715 | 1226146.5276 | 2658367.4876 | 1226148.085 | 2658407.9514 | 1226161.7905 | 2658414.0583 | 1226164.1005
32 | 2658344.5389 | 1226198.7477 | 2658349.2851 | 1226180.0824 | 2658350.2127 | 1226176.2485
33 | 2658414.5105 | 1226164.2715 | 2658414.0583 | 1226164.1005
34 | 2658344.5389 | 1226198.7477 | 2658349.8147 | 1226199.4999 | 2658345.9245 | 1226214.3601
35 | 2658345.9245 | 1226214.3601 | 2658326.7115 | 1226292.2434 | 2658324.6712 | 1226300.7105
36 | 2658324.6712 | 1226300.7105 | 2658322.029 | 1226311.6751
37 | 2658312.0674 | 1226353.0141 | 2658314.6582 | 1226342.2627
38 | 2658312.0674 | 1226353.0141 | 2658308.9448 | 1226365.9722
39 | 2658377.1534 | 1225855.1387 | 2658409.4362 | 1225862.2821
40 | 2658377.1534 | 1225855.1387 | 2658379.6797 | 1225808.5784 | 2658377.5141 | 1225801.3749 | 2658366.363 | 1225786.7229 | 2658364.247 | 1225785.2902
41 | 2658316.453 | 1225845.1422 | 2658290.5289 | 1225840.8744
42 | 2658410.189 | 1225923.0501 | 2658412.8697 | 1225895.5257 | 2658412.8783 | 1225895.3175
43 | 2658410.189 | 1225923.0501 | 2658409.857 | 1225925.9821 | 2658406.6722 | 1225947.709
44 | 2658410.189 | 1225923.0501 | 2658433.6692 | 1225922.6789
45 | 2658414.1939 | 1225863.3405 | 2658409.4362 | 1225862.2821
46 | 2658409.4362 | 1225862.2821 | 2658409.8474 | 1225828.3816
47 | 2658364.247 | 1225785.2902 | 2658359.9621 | 1225782.3908 | 2658345.5113 | 1225779.5585
48 | 2658250.1447 | 1225834.226 | 2658290.5289 | 1225840.8744
49 | 2658414.1939 | 1225863.3405 | 2658445.9958 | 1225872.2296
50 | 2658414.1939 | 1225863.3405 | 2658412.8783 | 1225895.3175
51 | 2658414.1939 | 1225863.3405 | 2658414.6929 | 1225837.9849 | 2658414.5391 | 1225832.6789
52 | 2658408.8242 | 1225799.7408 | 2658409.3559 | 1225807.1464 | 2658409.9134 | 1225822.9396 | 2658409.8474 | 1225828.3816
53 | 2658406.6722 | 1225947.709 | 2658417.0819 | 1225949.8236 | 2658424.6201 | 1225950.9268
54 | 2658445.9958 | 1225872.2296 | 2658459.7874 | 1225876.0845
55 | 2658404.7508 | 1225776.8253 | 2658408.3622 | 1225793.3056 | 2658408.8242 | 1225799.7408
56 | 2658435.8823 | 1226172.3555 | 2658414.5105 | 1226164.2715
57 | 2658435.8823 | 1226172.3555 | 2658437.4038 | 1226172.931 | 2658441.4042 | 1226174.7675
58 | 2658467.388 | 1226193.9721 | 2658452.1787 | 1226179.7137 | 2658441.4042 | 1226174.7675
59 | 2658467.388 | 1226193.9721 | 2658467.0351 | 1226210.1722
60 | 2658467.388 | 1226193.9721 | 2658477.5656 | 1226200.365 | 2658491.856 | 1226207.7447
61 | 2658467.388 | 1226193.9721 | 2658463.2038 | 1226138.9915
62 | 2658470.6803 | 1226048.9061 | 2658466.9749 | 1226073.2423
63 | 2658466.9749 | 1226073.2423 | 2658466.0822 | 1226079.1056
64 | 2658463.2038 | 1226138.9915 | 2658462.6284 | 1226131.4302 | 2658461.8458 | 1226106.9292 | 2658466.0822 | 1226079.1056
65 | 2658467.0351 | 1226210.1722 | 2658466.115 | 1226252.4063
66 | 2658533.046 | 1225886.4669 | 2658527.8007 | 1225876.4201 | 2658515.5335 | 1225871.3512
67 | 2658502.6905 | 1225866.0445 | 2658515.5335 | 1225871.3512
68 | 2658558.2997 | 1225884.5473 | 2658533.046 | 1225886.4669
69 | 2658496.5629 | 1225886.3638 | 2658516.1671 | 1225887.7573 | 2658533.046 | 1225886.4669
70 | 2658558.2997 | 1225884.5473 | 2658569.8709 | 1225878.0237 | 2658579.9796 | 1225866.0489 | 2658585.5188 | 1225856.0747
71 | 2658558.2997 | 1225884.5473 | 2658570.3593 | 1225890.0138 | 2658581.8365 | 1225895.0025
72 | 2658496.5629 | 1225886.3638 | 2658492.3904 | 1225912.2129
73 | 2658496.5629 | 1225886.3638 | 2658459.7874 | 1225876.0845
74 | 2658585.5188 | 1225856.0747 | 2658602.3476 | 1225825.7715
75 | 2658602.3476 | 1225825.7715 | 2658882.5382 | 1225897.0198
76 | 2658882.5382 | 1225897.0198 | 2658891.3083 | 1225842.6832 | 2658894.9963 | 1225816.2473 | 2658901.0626 | 1225806.8119
77 | 2658981.1076 | 1225858.5266 | 2658882.5382 | 1225897.0198
78 | 2659028.7824 | 1225927.0981 | 2659029.8865 | 1225918.1923 | 2659037.4617 | 1225912.5972 | 2659047.0271 | 1225908.2218
79 | 2659062.1796 | 1225901.2907 | 2659047.0271 | 1225908.2218
80 | 2659074.7543 | 1225880.7803 | 2659062.1796 | 1225901.2907
81 | 2659062.1796 | 1225901.2907 | 2659037.4617 | 1225912.5972 | 2659032.6623 | 1225916.1421
82 | 2659074.7543 | 1225880.7803 | 2659007.402 | 1225864.775
83 | 2658981.1076 | 1225858.5266 | 2659007.402 | 1225864.775
84 | 2658901.0626 | 1225806.8119 | 2658906.3753 | 1225798.5487 | 2658912.5407 | 1225788.3477 | 2658933.901 | 1225771.6485 | 2658940.3292 | 1225764.7633 | 2658952.7854 | 1225761.5624 | 2658957.8054 | 1225762.2557
85 | 2658979.5718 | 1225764.004 | 2658964.5796 | 1225763.1913 | 2658957.8054 | 1225762.2557
86 | 2658979.5718 | 1225764.004 | 2658984.1571 | 1225764.2526 | 2658994.697 | 1225757.0636
87 | 2659003.0324 | 1225757.3797 | 2658994.697 | 1225757.0636
88 | 2659050.3789 | 1225691.0515 | 2659019.3395 | 1225733.5373 | 2659003.0324 | 1225757.3797
89 | 2659050.3789 | 1225691.0515 | 2659037.437 | 1225695.8262 | 2659011.5829 | 1225704.6644 | 2658987.9976 | 1225702.6741
90 | 2658128.6102 | 1225967.5225 | 2658110.2523 | 1226010.4931
91 | 2658128.6102 | 1225967.5225 | 2658156.5161 | 1225905.1555
92 | 2658128.6102 | 1225967.5225 | 2658081.3056 | 1225954.3266
93 | 2658156.5161 | 1225905.1555 | 2658139.5016 | 1225900.164 | 2658134.0676 | 1225899.1015
94 | 2658250.1447 | 1225834.226 | 2658156.5161 | 1225905.1555
95 | 2658080.1819 | 1225954.0132 | 2658081.3056 | 1225954.3266
96 | 2658250.1447 | 1225834.226 | 2658251.0389 | 1225814.716
97 | 2658251.0389 | 1225814.716 | 2658252.3908 | 1225785.2164
98 | 2658134.0676 | 1225899.1015 | 2658115.5815 | 1225895.4869
99 | 2658040.8665 | 1225919.6804 | 2658041.8967 | 1225932.9213 | 2658047.4041 | 1225943.3705 | 2658056.7862 | 1225947.4868 | 2658080.1819 | 1225954.0132
100 | 2658103.7649 | 1225893.1765 | 2658115.5815 | 1225895.4869
101 | 2658103.7649 | 1225893.1765 | 2658099.1997 | 1225892.2839
102 | 2658345.1461 | 1225755.1481 | 2658345.8241 | 1225755.2757
103 | 2658322.8361 | 1225775.1224 | 2658328.0817 | 1225751.9369 | 2658345.1461 | 1225755.1481
104 | 2658322.8361 | 1225775.1224 | 2658333.3278 | 1225777.175
105 | 2658345.5113 | 1225779.5585 | 2658342.2411 | 1225797.5972
106 | 2658345.5113 | 1225779.5585 | 2658333.3278 | 1225777.175
107 | 2658340.9119 | 1225804.9292 | 2658342.2411 | 1225797.5972
108 | 2658403.301 | 1225718.9089 | 2658390.2211 | 1225718.4915 | 2658385.9824 | 1225717.3443
109 | 2658407.7949 | 1225719.0531 | 2658403.301 | 1225718.9089
110 | 2658407.8458 | 1225685.2878 | 2658407.5474 | 1225701.7842 | 2658407.7949 | 1225719.0531
111 | 2658407.7949 | 1225719.0531 | 2658408.0656 | 1225725.9089
112 | 2658408.9127 | 1225746.4925 | 2658402.513 | 1225746.6743
113 | 2658402.513 | 1225746.6743 | 2658402.1194 | 1225752.7966 | 2658402.4155 | 1225756.6841
114 | 2658408.9127 | 1225746.4925 | 2658409.7761 | 1225758.1639 | 2658412.6347 | 1225782.7965
115 | 2658408.9127 | 1225746.4925 | 2658408.7006 | 1225741.3571
116 | 2658402.4155 | 1225756.6841 | 2658403.5229 | 1225771.222 | 2658404.7508 | 1225776.8253
117 | 2658407.8458 | 1225685.2878 | 2658424.3212 | 1225685.0048 | 2658435.1663 | 1225684.0442
118 | 2658408.0656 | 1225725.9089 | 2658408.1349 | 1225727.6619 | 2658408.6777 | 1225740.8017
119 | 2658462.1072 | 1225676.3892 | 2658459.0076 | 1225677.5183 | 2658437.9933 | 1225683.7938 | 2658435.1663 | 1225684.0442
120 | 2658412.6347 | 1225782.7965 | 2658430.5593 | 1225780.9608
121 | 2658408.7006 | 1225741.3571 | 2658408.6777 | 1225740.8017
122 | 2658469.7955 | 1225673.5884 | 2658462.1072 | 1225676.3892
123 | 2658431.0986 | 1225780.9055 | 2658430.5593 | 1225780.9608
124 | 2658569.4503 | 1225645.7102 | 2658561.3894 | 1225646.0934 | 2658557.4204 | 1225646.7481
125 | 2658557.4204 | 1225646.7481 | 2658538.1702 | 1225649.9231 | 2658529.2358 | 1225652.1189
126 | 2658529.2358 | 1225652.1189 | 2658509.636 | 1225656.9359 | 2658503.7123 | 1225659.5861
127 | 2658503.7123 | 1225659.5861 | 2658485.9832 | 1225667.5176
128 | 2658469.7955 | 1225673.5884 | 2658483.908 | 1225668.446 | 2658485.9832 | 1225667.5176
129 | 2658447.9476 | 1225772.4365 | 2658448.4959 | 1225779.1239 | 2658431.0986 | 1225780.9055

## bus_geodata
| x | y | coords
0 | 2658643.9849 | 1226495.9799
1 | 2658601.0235 | 1226498.4902
2 | 2658559.4887 | 1226257.4175
3 | 2658540.9318 | 1226246.1909
4 | 2658456.3134 | 1225950.2089
5 | 2658471.0435 | 1226046.521
6 | 2658437.2959 | 1225950.3369
7 | 2658531.1503 | 1226237.6953
8 | 2658504.4594 | 1226214.8774
9 | 2658334.1994 | 1225934.0345
10 | 2658333.1499 | 1225932.8935
11 | 2658374.9506 | 1225948.3094
12 | 2658384.5022 | 1225935.8987
13 | 2658099.8212 | 1226285.1107
14 | 2658124.692 | 1226293.3238
15 | 2658089.9157 | 1226281.381
16 | 2658150.2788 | 1226285.0574
17 | 2658077.782 | 1226276.8124
18 | 2658318.4814 | 1226326.3972
19 | 2658072.5799 | 1226274.8536
20 | 2658341.341 | 1225849.2395
21 | 2658362.0131 | 1225852.6447
22 | 2658325.477 | 1225846.6278
23 | 2658404.4008 | 1225925.8173
24 | 2658385.686 | 1226052.9078
25 | 2658363.3372 | 1226144.6421
26 | 2658358.2913 | 1226142.8582
27 | 2658362.8715 | 1226146.5276
28 | 2658350.2127 | 1226176.2485
29 | 2658414.0583 | 1226164.1005
30 | 2658344.5389 | 1226198.7477
31 | 2658345.9245 | 1226214.3601
32 | 2658324.6712 | 1226300.7105
33 | 2658322.029 | 1226311.6751
34 | 2658314.6582 | 1226342.2627
35 | 2658312.0674 | 1226353.0141
36 | 2658308.9448 | 1226365.9722
37 | 2658377.1534 | 1225855.1387
38 | 2658316.453 | 1225845.1422
39 | 2658410.189 | 1225923.0501
40 | 2658409.4362 | 1225862.2821
41 | 2658364.247 | 1225785.2902
42 | 2658290.5289 | 1225840.8744
43 | 2658414.1939 | 1225863.3405
44 | 2658409.8474 | 1225828.3816
45 | 2658412.8783 | 1225895.3175
46 | 2658406.6722 | 1225947.709
47 | 2658433.6692 | 1225922.6789
48 | 2658424.6201 | 1225950.9268
49 | 2658445.9958 | 1225872.2296
50 | 2658414.5391 | 1225832.6789
51 | 2658408.8242 | 1225799.7408
52 | 2658435.8823 | 1226172.3555
53 | 2658414.5105 | 1226164.2715
54 | 2658441.4042 | 1226174.7675
55 | 2658467.388 | 1226193.9721
56 | 2658470.6803 | 1226048.9061
57 | 2658466.9749 | 1226073.2423
58 | 2658466.0822 | 1226079.1056
59 | 2658463.2038 | 1226138.9915
60 | 2658467.0351 | 1226210.1722
61 | 2658491.856 | 1226207.7447
62 | 2658466.115 | 1226252.4063
63 | 2658515.5335 | 1225871.3512
64 | 2658533.046 | 1225886.4669
65 | 2658502.6905 | 1225866.0445
66 | 2658558.2997 | 1225884.5473
67 | 2658496.5629 | 1225886.3638
68 | 2658585.5188 | 1225856.0747
69 | 2658581.8365 | 1225895.0025
70 | 2658492.3904 | 1225912.2129
71 | 2658459.7874 | 1225876.0845
72 | 2658602.3476 | 1225825.7715
73 | 2658882.5382 | 1225897.0198
74 | 2659028.7824 | 1225927.0981
75 | 2659047.0271 | 1225908.2218
76 | 2659062.1796 | 1225901.2907
77 | 2659074.7543 | 1225880.7803
78 | 2659032.6623 | 1225916.1421
79 | 2659007.402 | 1225864.775
80 | 2658981.1076 | 1225858.5266
81 | 2658901.0626 | 1225806.8119
82 | 2658957.8054 | 1225762.2557
83 | 2658979.5718 | 1225764.004
84 | 2658994.697 | 1225757.0636
85 | 2659003.0324 | 1225757.3797
86 | 2659050.3789 | 1225691.0515
87 | 2658987.9976 | 1225702.6741
88 | 2658110.2523 | 1226010.4931
89 | 2658128.6102 | 1225967.5225
90 | 2658156.5161 | 1225905.1555
91 | 2658081.3056 | 1225954.3266
92 | 2658250.1447 | 1225834.226
93 | 2658251.0389 | 1225814.716
94 | 2658134.0676 | 1225899.1015
95 | 2658080.1819 | 1225954.0132
96 | 2658115.5815 | 1225895.4869
97 | 2658040.8665 | 1225919.6804
98 | 2658103.7649 | 1225893.1765
99 | 2658099.1997 | 1225892.2839
100 | 2658345.8241 | 1225755.2757
101 | 2658345.1461 | 1225755.1481
102 | 2658322.8361 | 1225775.1224
103 | 2658345.5113 | 1225779.5585
104 | 2658333.3278 | 1225777.175
105 | 2658342.2411 | 1225797.5972
106 | 2658340.9119 | 1225804.9292
107 | 2658385.9824 | 1225717.3443
108 | 2658403.301 | 1225718.9089
109 | 2658407.7949 | 1225719.0531
110 | 2658402.513 | 1225746.6743
111 | 2658408.9127 | 1225746.4925
112 | 2658402.4155 | 1225756.6841
113 | 2658407.8458 | 1225685.2878
114 | 2658408.0656 | 1225725.9089
115 | 2658435.1663 | 1225684.0442
116 | 2658412.6347 | 1225782.7965
117 | 2658408.7006 | 1225741.3571
118 | 2658404.7508 | 1225776.8253
119 | 2658408.6777 | 1225740.8017
120 | 2658462.1072 | 1225676.3892
121 | 2658430.5593 | 1225780.9608
122 | 2658252.3908 | 1225785.2164
123 | 2658569.4503 | 1225645.7102
124 | 2658557.4204 | 1225646.7481
125 | 2658529.2358 | 1225652.1189
126 | 2658503.7123 | 1225659.5861
127 | 2658485.9832 | 1225667.5176
128 | 2658469.7955 | 1225673.5884
129 | 2658431.0986 | 1225780.9055
130 | 2658447.9476 | 1225772.4365
131 | 2658445.9958 | 1225872.2296

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97789 | -0.15582 | 0.001634 | 0.00040953
1 | 0.978 | -0.15504 | 0.00043942 | 0.00011013
2 | 0.97873 | -0.14971 | 0 | 0
3 | 0.9788 | -0.14924 | 0.0011201 | 0.00028072
4 | 0.98854 | -0.080114 | 0.016338 | 0.0040946
5 | 0.98572 | -0.099978 | 0.0048018 | 0.0012034
6 | 0.98932 | -0.074596 | 0.0040863 | 0.0010241
7 | 0.97886 | -0.1488 | 0.00098151 | 0.00024599
8 | 0.97907 | -0.14726 | 0.00064059 | 0.00016055
9 | 0.99051 | -0.066319 | 0.0057701 | 0.0014461
10 | 0.9905 | -0.066375 | 0.003504 | 0.00087819
11 | 0.99112 | -0.062015 | 0.0031343 | 0.00078553
12 | 0.9914 | -0.06004 | 0.00071314 | 0.00017873
13 | 0.9725 | -0.19447 | 0.0015586 | 0.00039061
14 | 0.97263 | -0.19354 | 0.00078735 | 0.00019733
15 | 0.97248 | -0.19467 | 0.00031929 | 8.0023e-05
16 | 0.9728 | -0.19234 | 0.00041237 | 0.00010335
17 | 0.97245 | -0.19486 | 0.00098135 | 0.00024595
18 | 0.97395 | -0.18407 | 0.00063371 | 0.00015882
19 | 0.97245 | -0.19489 | 0.00046069 | 0.00011546
20 | 0.99327 | -0.046989 | 0.0017106 | 0.00042871
21 | 0.99354 | -0.045074 | 0.0014856 | 0.00037233
22 | 0.9931 | -0.048182 | 0.00045648 | 0.00011441
23 | 0.99184 | -0.056896 | 0 | 0
24 | 0.97496 | -0.17674 | 0.0088313 | 0.0022133
25 | 0.97618 | -0.16799 | 0 | 0
26 | 0.97611 | -0.16846 | 0 | 0
27 | 0.97623 | -0.16764 | 0 | 0
28 | 0.9757 | -0.17146 | 0.00068236 | 0.00017101
29 | 0.97758 | -0.15792 | 0.00047241 | 0.0001184
30 | 0.97544 | -0.17332 | 0 | 0
31 | 0.97521 | -0.17498 | 0 | 0
32 | 0.97422 | -0.18212 | 0.00051573 | 0.00012925
33 | 0.9741 | -0.18297 | 0.00021018 | 5.2676e-05
34 | 0.9739 | -0.18436 | 0.00050057 | 0.00012545
35 | 0.97388 | -0.18451 | 0.00094623 | 0.00023715
36 | 0.97388 | -0.18455 | 0.00028287 | 7.0893e-05
37 | 0.99377 | -0.043441 | 0 | 0
38 | 0.99301 | -0.048818 | 0.0013048 | 0.00032702
39 | 0.992 | -0.055776 | 0 | 0
40 | 0.99513 | -0.033879 | 0 | 0
41 | 0.99181 | -0.057283 | 0 | 0
42 | 0.9928 | -0.050298 | 0.00023507 | 5.8913e-05
43 | 0.99567 | -0.030077 | 0 | 0
44 | 0.99274 | -0.050633 | 0.0010808 | 0.00027086
45 | 0.99367 | -0.044066 | 0.0036366 | 0.00091142
46 | 0.99078 | -0.064329 | 0 | 0
47 | 0.99192 | -0.056314 | 0.0022568 | 0.0005656
48 | 0.98989 | -0.070605 | 0.0073677 | 0.0018465
49 | 1 | 0 | -0.2427 | -0.060932
50 | 0.99491 | -0.035458 | 0.017412 | 0.0043639
51 | 0.99075 | -0.064549 | 0.0010484 | 0.00026275
52 | 0.97827 | -0.15301 | 0.00040803 | 0.00010226
53 | 0.97759 | -0.15783 | 0.0025413 | 0.00063692
54 | 0.97845 | -0.15172 | 0.00025431 | 6.3736e-05
55 | 0.97944 | -0.14461 | 0 | 0
56 | 0.9856 | -0.10085 | 0.0048019 | 0.0012035
57 | 0.98452 | -0.10849 | 0.00056628 | 0.00014192
58 | 0.98426 | -0.1103 | 0.00056639 | 0.00014195
59 | 0.98172 | -0.12838 | 0.00069316 | 0.00017372
60 | 0.97942 | -0.14477 | 0.00038709 | 9.7015e-05
61 | 0.97918 | -0.14652 | 0.0016851 | 0.00042232
62 | 0.97939 | -0.14502 | 0.0005622 | 0.0001409
63 | 0.99289 | -0.04987 | 0.0017348 | 0.00043477
64 | 0.99348 | -0.045667 | 0 | 0
65 | 0.99259 | -0.052002 | 0.015146 | 0.003796
66 | 0.9924 | -0.053313 | 0 | 0
67 | 0.99593 | -0.028448 | 0 | 0
68 | 0.99148 | -0.059869 | 0.0049589 | 0.0012428
69 | 0.99189 | -0.056942 | 0.013894 | 0.0034823
70 | 0.99571 | -0.029986 | 0.005835 | 0.0014624
71 | 0.99881 | -0.0082807 | 0.0052266 | 0.0013099
72 | 0.99093 | -0.06376 | 0.0074962 | 0.0018787
73 | 0.98949 | -0.074172 | 0 | 0
74 | 0.98879 | -0.079147 | 0.00099317 | 0.00024891
75 | 0.98884 | -0.078854 | 0.00028614 | 7.1714e-05
76 | 0.98887 | -0.078636 | 0 | 0
77 | 0.98893 | -0.078194 | 0 | 0
78 | 0.98884 | -0.07881 | 0.00051413 | 0.00012885
79 | 0.98911 | -0.076918 | 0.00021467 | 5.3802e-05
80 | 0.98919 | -0.076359 | 0 | 0
81 | 0.9893 | -0.075577 | 0.00024442 | 6.1257e-05
82 | 0.98916 | -0.076533 | 0.00069264 | 0.00017359
83 | 0.98915 | -0.076652 | 0.00024222 | 6.0707e-05
84 | 0.98914 | -0.076703 | 0.00016737 | 4.1947e-05
85 | 0.98914 | -0.076713 | 0 | 0
86 | 0.98913 | -0.076809 | 0 | 0
87 | 0.98912 | -0.076881 | 0.00010565 | 2.6478e-05
88 | 0.99147 | -0.059755 | 0.0015284 | 0.00038305
89 | 0.99158 | -0.059029 | 0 | 0
90 | 0.99179 | -0.05754 | 0 | 0
91 | 0.99153 | -0.059333 | 0.00018142 | 4.5468e-05
92 | 0.99249 | -0.052506 | 0 | 0
93 | 0.99246 | -0.052721 | 0.00038032 | 9.5318e-05
94 | 0.99172 | -0.058029 | 0.00017197 | 4.3101e-05
95 | 0.99153 | -0.059338 | 0.00023796 | 5.964e-05
96 | 0.99167 | -0.058392 | 0.00018646 | 4.6732e-05
97 | 0.99152 | -0.059449 | 0.0001813 | 4.5437e-05
98 | 0.99164 | -0.0586 | 0.0013506 | 0.0003385
99 | 0.99163 | -0.058617 | 0.00035647 | 8.934e-05
100 | 0.98994 | -0.070454 | 0.0062055 | 0.0015552
101 | 0.98995 | -0.070411 | 0.0079502 | 0.0019925
102 | 0.99078 | -0.064485 | 0 | 0
103 | 0.99129 | -0.060949 | 0 | 0
104 | 0.991 | -0.062946 | 0.0016726 | 0.0004192
105 | 0.99122 | -0.061389 | 0.0016726 | 0.0004192
106 | 0.99122 | -0.061441 | 0.0006868 | 0.00017213
107 | 0.98587 | -0.099071 | 0.0060448 | 0.001515
108 | 0.98602 | -0.097986 | 0 | 0
109 | 0.98606 | -0.097708 | 0 | 0
110 | 0.98745 | -0.087859 | 0 | 0
111 | 0.98711 | -0.09028 | 0 | 0
112 | 0.98799 | -0.084056 | 0.0034075 | 0.000854
113 | 0.9852 | -0.10384 | 0 | 0
114 | 0.9863 | -0.096038 | 0.0023576 | 0.00059087
115 | 0.9845 | -0.10881 | 0.0060218 | 0.0015092
116 | 0.98678 | -0.092654 | 0 | 0
117 | 0.98688 | -0.091897 | 0.0032078 | 0.00080394
118 | 0.98918 | -0.075661 | 0.0063211 | 0.0015842
119 | 0.98686 | -0.092054 | 0.0014237 | 0.00035681
120 | 0.98403 | -0.11217 | 0.0016444 | 0.00041213
121 | 0.98661 | -0.093826 | 0.0023927 | 0.00059966
122 | 0.99243 | -0.052933 | 0.00070606 | 0.00017696
123 | 0.98289 | -0.12025 | 0.0031539 | 0.00079045
124 | 0.98295 | -0.11985 | 0.0023708 | 0.00059418
125 | 0.98318 | -0.11821 | 0.0011823 | 0.00029632
126 | 0.98344 | -0.11637 | 0.0016402 | 0.00041107
127 | 0.98367 | -0.11469 | 0.0010442 | 0.00026171
128 | 0.98391 | -0.11302 | 0.00058731 | 0.00014719
129 | 0.98661 | -0.093848 | 0.0022357 | 0.00056033
130 | 0.98655 | -0.094273 | 0.0017115 | 0.00042894
131 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.001634 | -0.00040953 | 0.0016342 | 0.00040902 | 1.7695e-07 | -5.0749e-07 | 0.0024865 | 0.0024863 | 0.0024865 | 0.97789 | -0.15582 | 0.978 | -0.15504 | 0.92091
1 | -0.0020736 | -0.00051915 | 0.0020752 | 0.00051666 | 1.5188e-06 | -2.4878e-06 | 0.0031548 | 0.0031537 | 0.0031548 | 0.978 | -0.15504 | 0.97873 | -0.14971 | 1.1685
2 | -0.0020752 | -0.00051666 | 0.0020753 | 0.00051644 | 1.346e-07 | -2.2081e-07 | 0.0031537 | 0.0031536 | 0.0031537 | 0.97873 | -0.14971 | 0.9788 | -0.14924 | 1.1681
3 | -0.0031954 | -0.00079717 | 0.0031956 | 0.00079708 | 1.9154e-07 | -8.9925e-08 | 0.0048565 | 0.0048564 | 0.0048565 | 0.9788 | -0.14924 | 0.97886 | -0.1488 | 1.7987
4 | 0.040071 | 0.010076 | -0.039961 | -0.010036 | 0.00011064 | 4.0064e-05 | 0.06033 | 0.060331 | 0.060331 | 0.98854 | -0.080114 | 0.98572 | -0.099978 | 11.1724
5 | -0.056409 | -0.014171 | 0.056452 | 0.014187 | 4.3327e-05 | 1.617e-05 | 0.084923 | 0.084923 | 0.084923 | 0.98854 | -0.080114 | 0.98932 | -0.074596 | 15.7264
6 | 0.035159 | 0.0088329 | -0.035154 | -0.0088313 | 4.2419e-06 | 1.6008e-06 | 0.053082 | 0.053082 | 0.053082 | 0.98572 | -0.099978 | 0.9856 | -0.10085 | 19.66
7 | -0.060539 | -0.015211 | 0.060572 | 0.015224 | 3.3643e-05 | 1.2606e-05 | 0.091069 | 0.091069 | 0.091069 | 0.98932 | -0.074596 | 0.98989 | -0.070605 | 16.8646
8 | -0.0041771 | -0.0010431 | 0.004178 | 0.001043 | 8.8485e-07 | -1.0207e-07 | 0.0063484 | 0.0063483 | 0.0063484 | 0.97886 | -0.1488 | 0.97907 | -0.14726 | 2.3513
9 | -0.0048186 | -0.0012035 | 0.0048191 | 0.0012035 | 4.8562e-07 | 4.1942e-09 | 0.0073219 | 0.0073218 | 0.0073219 | 0.97907 | -0.14726 | 0.97918 | -0.14652 | 2.7118
10 | 0.003504 | 0.00087818 | -0.003504 | -0.00087819 | 2.6805e-08 | -9.6436e-09 | 0.005264 | 0.005264 | 0.005264 | 0.99051 | -0.066319 | 0.9905 | -0.066375 | 1.9496
11 | -0.0092741 | -0.0023243 | 0.0092797 | 0.0023258 | 5.5281e-06 | 1.5384e-06 | 0.013932 | 0.013932 | 0.013932 | 0.99051 | -0.066319 | 0.99112 | -0.062015 | 5.1601
12 | -0.012414 | -0.0031114 | 0.012417 | 0.0031125 | 3.3946e-06 | 1.1037e-06 | 0.018638 | 0.018638 | 0.018638 | 0.99112 | -0.062015 | 0.9914 | -0.06004 | 6.9029
13 | -0.01313 | -0.0032912 | 0.013136 | 0.0032931 | 5.7187e-06 | 1.8951e-06 | 0.019708 | 0.019708 | 0.019708 | 0.9914 | -0.06004 | 0.99184 | -0.056896 | 7.2993
14 | -0.00332 | -0.00083172 | 0.0033204 | 0.00083155 | 4.2605e-07 | -1.645e-07 | 0.0050797 | 0.0050796 | 0.0050797 | 0.9725 | -0.19447 | 0.97263 | -0.19354 | 1.8814
15 | 0.0017614 | 0.0004411 | -0.0017614 | -0.00044122 | 4.7971e-08 | -1.1288e-07 | 0.002695 | 0.002695 | 0.002695 | 0.9725 | -0.19447 | 0.97248 | -0.19467 | 0.99816
16 | -0.0041078 | -0.0010289 | 0.0041084 | 0.0010288 | 6.8188e-07 | -8.1232e-08 | 0.0062842 | 0.006284 | 0.0062842 | 0.97263 | -0.19354 | 0.9728 | -0.19234 | 2.3275
17 | 0.0014421 | 0.00036119 | -0.001442 | -0.00036134 | 3.9389e-08 | -1.4571e-07 | 0.0022065 | 0.0022065 | 0.0022065 | 0.97248 | -0.19467 | 0.97245 | -0.19486 | 0.81724
18 | -0.0045208 | -0.0011321 | 0.004526 | 0.001132 | 5.1673e-06 | -1.6554e-07 | 0.0069148 | 0.006914 | 0.0069148 | 0.9728 | -0.19234 | 0.97395 | -0.18407 | 2.561
19 | 0.00046069 | 0.00011539 | -0.00046069 | -0.00011546 | 1.7236e-09 | -6.83e-08 | 0.00070491 | 0.00070493 | 0.00070493 | 0.97245 | -0.19486 | 0.97245 | -0.19489 | 0.26109
20 | 0.0017298 | 0.00043303 | -0.0017297 | -0.0004332 | 7.1116e-08 | -1.7573e-07 | 0.0026426 | 0.0026427 | 0.0026427 | 0.97395 | -0.18407 | 0.9739 | -0.18436 | 0.97877
21 | -0.0068894 | -0.0017238 | 0.0068905 | 0.001724 | 1.0467e-06 | 2.1411e-07 | 0.010525 | 0.010525 | 0.010525 | 0.97395 | -0.18407 | 0.9741 | -0.18297 | 3.8981
22 | -0.0089963 | -0.0022488 | 0.0089987 | 0.0022495 | 2.3739e-06 | 6.4178e-07 | 0.013475 | 0.013475 | 0.013475 | 0.99327 | -0.046989 | 0.99354 | -0.045074 | 4.9909
23 | 0.0072858 | 0.0018201 | -0.0072846 | -0.0018198 | 1.1947e-06 | 2.5145e-07 | 0.010913 | 0.010913 | 0.010913 | 0.99327 | -0.046989 | 0.9931 | -0.048182 | 4.0418
24 | -0.010484 | -0.0026218 | 0.010487 | 0.0026225 | 2.3602e-06 | 7.0899e-07 | 0.0157 | 0.0157 | 0.0157 | 0.99354 | -0.045074 | 0.99377 | -0.043441 | 5.8149
25 | 0.0068281 | 0.0017054 | -0.0068275 | -0.0017053 | 5.9709e-07 | 1.1133e-07 | 0.010229 | 0.010229 | 0.010229 | 0.9931 | -0.048182 | 0.99301 | -0.048818 | 3.7885
26 | -0.013136 | -0.0032931 | 0.013138 | 0.0032938 | 2.0381e-06 | 6.7534e-07 | 0.019708 | 0.019708 | 0.019708 | 0.99184 | -0.056896 | 0.992 | -0.055776 | 7.2993
27 | -0.0088313 | -0.0022133 | 0.008842 | 0.0022163 | 1.0703e-05 | 2.9377e-06 | 0.013479 | 0.013478 | 0.013479 | 0.97496 | -0.17674 | 0.97618 | -0.16799 | 4.9921
28 | 0.0083148 | 0.0020809 | -0.0083142 | -0.0020807 | 5.3499e-07 | 1.3904e-07 | 0.012673 | 0.012673 | 0.012673 | 0.97618 | -0.16799 | 0.97611 | -0.16846 | 4.6939
29 | -0.017157 | -0.0042971 | 0.017158 | 0.0042974 | 8.2876e-07 | 2.9448e-07 | 0.026152 | 0.026152 | 0.026152 | 0.97618 | -0.16799 | 0.97623 | -0.16764 | 9.6858
30 | 0.0083142 | 0.0020807 | -0.0083108 | -0.0020798 | 3.4431e-06 | 8.9503e-07 | 0.012673 | 0.012674 | 0.012674 | 0.97611 | -0.16846 | 0.9757 | -0.17146 | 4.6939
31 | -0.017158 | -0.0042974 | 0.017181 | 0.0043056 | 2.3097e-05 | 8.2059e-06 | 0.026152 | 0.026151 | 0.026152 | 0.97623 | -0.16764 | 0.97758 | -0.15792 | 9.6858
32 | 0.0076284 | 0.0019088 | -0.0076265 | -0.0019083 | 1.9594e-06 | 4.6389e-07 | 0.011633 | 0.011633 | 0.011633 | 0.9757 | -0.17146 | 0.97544 | -0.17332 | 4.3085
33 | -0.017653 | -0.004424 | 0.017653 | 0.0044241 | 2.1782e-07 | 7.7714e-08 | 0.02687 | 0.02687 | 0.02687 | 0.97758 | -0.15792 | 0.97759 | -0.15783 | 9.952
34 | 0.0076265 | 0.0019083 | -0.0076247 | -0.0019079 | 1.7472e-06 | 4.1378e-07 | 0.011633 | 0.011633 | 0.011633 | 0.97544 | -0.17332 | 0.97521 | -0.17498 | 4.3086
35 | 0.0076247 | 0.0019079 | -0.0076172 | -0.0019062 | 7.5098e-06 | 1.78e-06 | 0.011633 | 0.011634 | 0.011634 | 0.97521 | -0.17498 | 0.97422 | -0.18212 | 4.3087
36 | 0.0071015 | 0.0017769 | -0.0071007 | -0.0017767 | 8.2786e-07 | 1.7799e-07 | 0.010846 | 0.010846 | 0.010846 | 0.97422 | -0.18212 | 0.9741 | -0.18297 | 4.017
37 | 0.0012291 | 0.00030775 | -0.0012291 | -0.00030788 | 2.4336e-08 | -1.2825e-07 | 0.0018779 | 0.0018779 | 0.0018779 | 0.9739 | -0.18436 | 0.97388 | -0.18451 | 0.69552
38 | 0.00028287 | 7.0728e-05 | -0.00028287 | -7.0893e-05 | 1.5534e-09 | -1.6525e-07 | 0.00043214 | 0.0004322 | 0.0004322 | 0.97388 | -0.18451 | 0.97388 | -0.18455 | 0.16007
39 | -0.028738 | -0.0072028 | 0.028776 | 0.007217 | 3.8095e-05 | 1.4224e-05 | 0.043031 | 0.04303 | 0.043031 | 0.99377 | -0.043441 | 0.99513 | -0.033879 | 15.9373
40 | 0.018251 | 0.0045803 | -0.018216 | -0.0045678 | 3.5005e-05 | 1.2492e-05 | 0.02733 | 0.027331 | 0.027331 | 0.99377 | -0.043441 | 0.99181 | -0.057283 | 10.1225
41 | 0.0055227 | 0.0013783 | -0.0055215 | -0.0013782 | 1.1222e-06 | 9.182e-08 | 0.0082736 | 0.0082737 | 0.0082737 | 0.99301 | -0.048818 | 0.9928 | -0.050298 | 3.0643
42 | -0.083476 | -0.020983 | 0.083612 | 0.021034 | 0.00013635 | 5.172e-05 | 0.12524 | 0.12524 | 0.12524 | 0.992 | -0.055776 | 0.99367 | -0.044066 | 23.192
43 | 0.06808 | 0.017123 | -0.067999 | -0.017093 | 8.1086e-05 | 3.0545e-05 | 0.10214 | 0.10214 | 0.10214 | 0.992 | -0.055776 | 0.99078 | -0.064329 | 18.9155
44 | 0.0022569 | 0.00056536 | -0.0022568 | -0.0005656 | 1.6794e-07 | -2.3856e-07 | 0.0033853 | 0.0033854 | 0.0033854 | 0.992 | -0.055776 | 0.99192 | -0.056314 | 1.2539
45 | -0.078085 | -0.019627 | 0.078126 | 0.019643 | 4.1358e-05 | 1.5844e-05 | 0.11678 | 0.11678 | 0.11678 | 0.99513 | -0.033879 | 0.99567 | -0.030077 | 43.2521
46 | 0.049309 | 0.01241 | -0.049194 | -0.012366 | 0.00011507 | 4.3817e-05 | 0.07375 | 0.07375 | 0.07375 | 0.99513 | -0.033879 | 0.99274 | -0.050633 | 27.3149
47 | 0.018216 | 0.0045678 | -0.018207 | -0.0045645 | 9.2509e-06 | 3.3021e-06 | 0.027331 | 0.027331 | 0.027331 | 0.99181 | -0.057283 | 0.99129 | -0.060949 | 10.1226
48 | 0.0052865 | 0.0013193 | -0.0052849 | -0.0013192 | 1.6026e-06 | 8.7291e-08 | 0.0079214 | 0.0079216 | 0.0079216 | 0.9928 | -0.050298 | 0.99249 | -0.052506 | 2.9339
49 | -0.18297 | -0.046022 | 0.18374 | 0.046317 | 0.00077067 | 0.00029555 | 0.2735 | 0.2735 | 0.2735 | 0.99567 | -0.030077 | 1 | 0 | 50.649
50 | 0.087419 | 0.02201 | -0.087249 | -0.021946 | 0.00017053 | 6.4756e-05 | 0.13068 | 0.13068 | 0.13068 | 0.99567 | -0.030077 | 0.99367 | -0.044066 | 24.2004
51 | 0.017425 | 0.0043685 | -0.017412 | -0.0043639 | 1.2979e-05 | 4.5932e-06 | 0.026042 | 0.026042 | 0.026042 | 0.99567 | -0.030077 | 0.99491 | -0.035458 | 9.6452
52 | 0.048113 | 0.012096 | -0.04802 | -0.01206 | 9.3079e-05 | 3.543e-05 | 0.07213 | 0.07213 | 0.07213 | 0.99274 | -0.050633 | 0.99075 | -0.064549 | 26.715
53 | 0.067999 | 0.017093 | -0.06794 | -0.01707 | 5.9377e-05 | 2.2368e-05 | 0.10214 | 0.10214 | 0.10214 | 0.99078 | -0.064329 | 0.98989 | -0.070605 | 18.9155
54 | 0.05816 | 0.014615 | -0.058093 | -0.014589 | 6.6947e-05 | 2.5561e-05 | 0.086556 | 0.086556 | 0.086556 | 1 | 0 | 0.99881 | -0.0082807 | 32.0579
55 | 0.046972 | 0.011797 | -0.046899 | -0.01177 | 7.245e-05 | 2.7566e-05 | 0.070556 | 0.070556 | 0.070556 | 0.99075 | -0.064549 | 0.98918 | -0.075661 | 26.1319
56 | 0.020208 | 0.0050659 | -0.020195 | -0.005061 | 1.3472e-05 | 4.8948e-06 | 0.030739 | 0.030739 | 0.030739 | 0.97827 | -0.15301 | 0.97759 | -0.15783 | 11.3847
57 | -0.020616 | -0.0051682 | 0.02062 | 0.0051695 | 3.6993e-06 | 1.3471e-06 | 0.031359 | 0.031359 | 0.031359 | 0.97827 | -0.15301 | 0.97845 | -0.15172 | 11.6145
58 | -0.020874 | -0.0052333 | 0.020895 | 0.0052408 | 2.0566e-05 | 7.4988e-06 | 0.031746 | 0.031746 | 0.031746 | 0.97845 | -0.15172 | 0.97944 | -0.14461 | 11.7577
59 | 0.00094934 | 0.0002372 | -0.00094932 | -0.00023739 | 2.1026e-08 | -1.9584e-07 | 0.001442 | 0.0014421 | 0.0014421 | 0.97944 | -0.14461 | 0.97942 | -0.14477 | 0.53411
60 | 0.0065059 | 0.0016261 | -0.0065041 | -0.0016258 | 1.7126e-06 | 3.0511e-07 | 0.0098824 | 0.0098826 | 0.0098826 | 0.97944 | -0.14461 | 0.97918 | -0.14652 | 3.6602
61 | -0.02835 | -0.0071041 | 0.028414 | 0.007128 | 6.3826e-05 | 2.3853e-05 | 0.04307 | 0.04307 | 0.04307 | 0.97944 | -0.14461 | 0.98172 | -0.12838 | 15.9519
62 | 0.030353 | 0.0076278 | -0.03032 | -0.0076157 | 3.2267e-05 | 1.2097e-05 | 0.045832 | 0.045832 | 0.045832 | 0.9856 | -0.10085 | 0.98452 | -0.10849 | 16.975
63 | 0.029754 | 0.0074738 | -0.029746 | -0.007471 | 7.4865e-06 | 2.804e-06 | 0.044977 | 0.044977 | 0.044977 | 0.98452 | -0.10849 | 0.98426 | -0.1103 | 16.658
64 | 0.02918 | 0.0073291 | -0.029107 | -0.0073017 | 7.3174e-05 | 2.738e-05 | 0.04412 | 0.044121 | 0.044121 | 0.98426 | -0.1103 | 0.98172 | -0.12838 | 16.341
65 | 0.00056222 | 0.00014038 | -0.0005622 | -0.0001409 | 1.9229e-08 | -5.2422e-07 | 0.00085398 | 0.00085417 | 0.00085417 | 0.97942 | -0.14477 | 0.97939 | -0.14502 | 0.31636
66 | -0.016885 | -0.0042323 | 0.016895 | 0.0042358 | 9.8329e-06 | 3.4635e-06 | 0.025306 | 0.025306 | 0.025306 | 0.99289 | -0.04987 | 0.99348 | -0.045667 | 9.3726
67 | 0.015151 | 0.0037975 | -0.015146 | -0.003796 | 4.4706e-06 | 1.5398e-06 | 0.022706 | 0.022706 | 0.022706 | 0.99289 | -0.04987 | 0.99259 | -0.052002 | 8.4097
68 | 0.029875 | 0.0074823 | -0.029844 | -0.0074705 | 3.1549e-05 | 1.1807e-05 | 0.044745 | 0.044745 | 0.044745 | 0.99348 | -0.045667 | 0.9924 | -0.053313 | 16.5721
69 | -0.046771 | -0.011718 | 0.046882 | 0.011761 | 0.00011169 | 4.2483e-05 | 0.07005 | 0.07005 | 0.07005 | 0.99348 | -0.045667 | 0.99593 | -0.028448 | 25.9446
70 | 0.015942 | 0.0039859 | -0.015928 | -0.0039809 | 1.4388e-05 | 5.0128e-06 | 0.023901 | 0.023901 | 0.023901 | 0.9924 | -0.053313 | 0.99148 | -0.059869 | 8.8522
71 | 0.013901 | 0.0034846 | -0.013894 | -0.0034823 | 6.9826e-06 | 2.353e-06 | 0.020844 | 0.020844 | 0.020844 | 0.9924 | -0.053313 | 0.99189 | -0.056942 | 7.7201
72 | 0.0058362 | 0.0014625 | -0.005835 | -0.0014624 | 1.2423e-06 | 1.3717e-07 | 0.0087198 | 0.0087199 | 0.0087199 | 0.99593 | -0.028448 | 0.99571 | -0.029986 | 3.2296
73 | -0.052718 | -0.013223 | 0.052866 | 0.013279 | 0.00014784 | 5.6364e-05 | 0.07877 | 0.07877 | 0.07877 | 0.99593 | -0.028448 | 0.99881 | -0.0082807 | 29.1741
74 | 0.010969 | 0.002738 | -0.010963 | -0.0027362 | 5.8591e-06 | 1.8067e-06 | 0.016459 | 0.016459 | 0.016459 | 0.99148 | -0.059869 | 0.99093 | -0.06376 | 6.0958
75 | 0.003467 | 0.00085751 | -0.0034621 | -0.00085935 | 4.8834e-06 | -1.8408e-06 | 0.0052022 | 0.0052035 | 0.0052035 | 0.99093 | -0.06376 | 0.98949 | -0.074172 | 1.9272
76 | 0.0014527 | 0.00035949 | -0.0014525 | -0.00036058 | 2.7646e-07 | -1.0874e-06 | 0.002183 | 0.0021835 | 0.0021835 | 0.98949 | -0.074172 | 0.9893 | -0.075577 | 0.80869
77 | 0.0020094 | 0.00049986 | -0.0020088 | -0.00050098 | 6.0099e-07 | -1.1243e-06 | 0.0030204 | 0.0030209 | 0.0030209 | 0.98949 | -0.074172 | 0.98919 | -0.076359 | 1.1189
78 | -0.00099317 | -0.00024891 | 0.00099321 | 0.00024856 | 4.0294e-08 | -3.5535e-07 | 0.0014946 | 0.0014945 | 0.0014946 | 0.98879 | -0.079147 | 0.98884 | -0.078854 | 0.55355
79 | -0.0012794 | -0.00032027 | 0.0012794 | 0.00032007 | 3.8529e-08 | -1.9893e-07 | 0.0019251 | 0.001925 | 0.0019251 | 0.98884 | -0.078854 | 0.98887 | -0.078636 | 0.71299
80 | -0.0017935 | -0.0004485 | 0.0017936 | 0.00044824 | 1.0924e-07 | -2.6644e-07 | 0.0026985 | 0.0026984 | 0.0026985 | 0.98887 | -0.078636 | 0.98893 | -0.078194 | 0.99944
81 | 0.00051414 | 0.00012843 | -0.00051413 | -0.00012885 | 1.2378e-08 | -4.2047e-07 | 0.00077352 | 0.00077367 | 0.00077367 | 0.98887 | -0.078636 | 0.98884 | -0.07881 | 0.28654
82 | -0.0017936 | -0.00044824 | 0.001794 | 0.00044747 | 3.145e-07 | -7.6742e-07 | 0.0026984 | 0.0026981 | 0.0026984 | 0.98893 | -0.078194 | 0.98911 | -0.076918 | 0.9994
83 | -0.0020086 | -0.00050127 | 0.0020088 | 0.00050098 | 1.5391e-07 | -2.8772e-07 | 0.003021 | 0.0030209 | 0.003021 | 0.98911 | -0.076918 | 0.98919 | -0.076359 | 1.1189
84 | 0.001208 | 0.00029932 | -0.0012079 | -0.00030024 | 1.5682e-07 | -9.1802e-07 | 0.0018158 | 0.0018162 | 0.0018162 | 0.9893 | -0.075577 | 0.98916 | -0.076533 | 0.67266
85 | 0.00051525 | 0.00012665 | -0.00051524 | -0.00012693 | 8.1749e-09 | -2.7736e-07 | 0.00077423 | 0.00077433 | 0.00077433 | 0.98916 | -0.076533 | 0.98915 | -0.076652 | 0.28679
86 | 0.00027302 | 6.6219e-05 | -0.00027302 | -6.6441e-05 | 1.8198e-09 | -2.2201e-07 | 0.00040995 | 0.00041002 | 0.00041002 | 0.98915 | -0.076652 | 0.98914 | -0.076703 | 0.15186
87 | 0.00010565 | 2.4495e-05 | -0.00010565 | -2.4602e-05 | 1.3038e-10 | -1.0702e-07 | 0.00015826 | 0.00015829 | 0.00015829 | 0.98914 | -0.076703 | 0.98914 | -0.076713 | 0.058626
88 | 0.00010565 | 2.4602e-05 | -0.00010565 | -2.5647e-05 | 1.276e-09 | -1.0448e-06 | 0.00015829 | 0.00015864 | 0.00015864 | 0.98914 | -0.076713 | 0.98913 | -0.076809 | 0.058757
89 | 0.00010565 | 2.5647e-05 | -0.00010565 | -2.6478e-05 | 1.0193e-09 | -8.3117e-07 | 0.00015864 | 0.00015893 | 0.00015893 | 0.98913 | -0.076809 | 0.98912 | -0.076881 | 0.058865
90 | -0.0015284 | -0.00038305 | 0.0015285 | 0.00038251 | 1.5341e-07 | -5.4369e-07 | 0.0022938 | 0.0022936 | 0.0022938 | 0.99147 | -0.059755 | 0.99158 | -0.059029 | 0.84957
91 | -0.0021293 | -0.00053165 | 0.0021297 | 0.00053093 | 4.3492e-07 | -7.1396e-07 | 0.0031946 | 0.0031943 | 0.0031946 | 0.99158 | -0.059029 | 0.99179 | -0.05754 | 1.1832
92 | 0.00060071 | 0.00014914 | -0.00060068 | -0.00014976 | 2.4881e-08 | -6.2389e-07 | 0.00090096 | 0.00090118 | 0.00090118 | 0.99158 | -0.059029 | 0.99153 | -0.059333 | 0.33377
93 | 0.0020658 | 0.00051702 | -0.0020657 | -0.00051727 | 1.3946e-07 | -2.4661e-07 | 0.0030992 | 0.0030993 | 0.0030993 | 0.99179 | -0.05754 | 0.99172 | -0.058029 | 1.1479
94 | -0.0041955 | -0.001048 | 0.0041984 | 0.0010476 | 2.9028e-06 | -4.0041e-07 | 0.0062935 | 0.0062929 | 0.0062935 | 0.99179 | -0.05754 | 0.99249 | -0.052506 | 2.3309
95 | 0.00041926 | 0.00010429 | -0.00041926 | -0.00010431 | 2.8802e-10 | -1.4936e-08 | 0.00062892 | 0.00062893 | 0.00062893 | 0.99153 | -0.059333 | 0.99153 | -0.059338 | 0.23294
96 | 0.0010864 | 0.00027166 | -0.0010864 | -0.0002719 | 3.2328e-08 | -2.3995e-07 | 0.0016286 | 0.0016287 | 0.0016287 | 0.99249 | -0.052506 | 0.99246 | -0.052721 | 0.60323
97 | 0.00070608 | 0.00017658 | -0.00070606 | -0.00017696 | 2.0649e-08 | -3.7365e-07 | 0.0010585 | 0.0010586 | 0.0010586 | 0.99246 | -0.052721 | 0.99243 | -0.052933 | 0.39209
98 | 0.0018937 | 0.00047417 | -0.0018936 | -0.00047438 | 9.4888e-08 | -2.0653e-07 | 0.0028413 | 0.0028413 | 0.0028413 | 0.99172 | -0.058029 | 0.99167 | -0.058392 | 1.0523
99 | 0.0001813 | 4.4669e-05 | -0.0001813 | -4.5437e-05 | 2.7516e-09 | -7.68e-07 | 0.00027181 | 0.00027208 | 0.00027208 | 0.99153 | -0.059338 | 0.99152 | -0.059449 | 0.10077
100 | 0.0017072 | 0.00042764 | -0.0017071 | -0.00042778 | 4.9299e-08 | -1.3637e-07 | 0.0025615 | 0.0025616 | 0.0025616 | 0.99167 | -0.058392 | 0.99164 | -0.0586 | 0.94874
101 | 0.00035647 | 8.928e-05 | -0.00035647 | -8.934e-05 | 8.3048e-10 | -5.969e-08 | 0.00053489 | 0.00053491 | 0.00053491 | 0.99164 | -0.0586 | 0.99163 | -0.058617 | 0.19811
102 | -0.0062055 | -0.0015552 | 0.0062055 | 0.0015553 | 3.7457e-08 | 5.5365e-09 | 0.0093277 | 0.0093277 | 0.0093277 | 0.98994 | -0.070454 | 0.98995 | -0.070411 | 3.4547
103 | -0.014156 | -0.0035478 | 0.014167 | 0.0035517 | 1.1621e-05 | 3.9404e-06 | 0.021278 | 0.021278 | 0.021278 | 0.98995 | -0.070411 | 0.99078 | -0.064485 | 7.8807
104 | -0.014167 | -0.0035517 | 0.01417 | 0.0035527 | 3.0202e-06 | 1.0239e-06 | 0.021278 | 0.021278 | 0.021278 | 0.99078 | -0.064485 | 0.991 | -0.062946 | 7.8806
105 | 0.0023596 | 0.00059105 | -0.0023594 | -0.00059123 | 1.4351e-07 | -1.8113e-07 | 0.0035418 | 0.0035419 | 0.0035419 | 0.99129 | -0.060949 | 0.99122 | -0.061389 | 1.3118
106 | 0.015847 | 0.0039734 | -0.015843 | -0.0039719 | 4.384e-06 | 1.5261e-06 | 0.023789 | 0.023789 | 0.023789 | 0.99129 | -0.060949 | 0.991 | -0.062946 | 8.8108
107 | 0.00068681 | 0.00017203 | -0.0006868 | -0.00017213 | 4.9426e-09 | -9.4148e-08 | 0.001031 | 0.001031 | 0.001031 | 0.99122 | -0.061389 | 0.99122 | -0.061441 | 0.38186
108 | -0.0060448 | -0.001515 | 0.0060457 | 0.0015151 | 9.0783e-07 | 1.2627e-07 | 0.0091236 | 0.0091236 | 0.0091236 | 0.98587 | -0.099071 | 0.98602 | -0.097986 | 3.3791
109 | -0.0060457 | -0.0015151 | 0.0060459 | 0.0015151 | 2.3285e-07 | 3.2375e-08 | 0.0091236 | 0.0091235 | 0.0091236 | 0.98602 | -0.097986 | 0.98606 | -0.097708 | 3.3791
110 | 0.017686 | 0.0044355 | -0.017671 | -0.0044301 | 1.5014e-05 | 5.3441e-06 | 0.02669 | 0.02669 | 0.02669 | 0.98606 | -0.097708 | 0.9852 | -0.10384 | 9.8853
111 | -0.023732 | -0.0059506 | 0.023737 | 0.0059526 | 5.4913e-06 | 2.0245e-06 | 0.035814 | 0.035814 | 0.035814 | 0.98606 | -0.097708 | 0.9863 | -0.096038 | 13.2643
112 | 0.037104 | 0.0093063 | -0.037091 | -0.0093015 | 1.2455e-05 | 4.7087e-06 | 0.055915 | 0.055915 | 0.055915 | 0.98745 | -0.087859 | 0.98711 | -0.09028 | 20.7094
113 | -0.037104 | -0.0093063 | 0.037124 | 0.0093137 | 1.9575e-05 | 7.4005e-06 | 0.055915 | 0.055915 | 0.055915 | 0.98745 | -0.087859 | 0.98799 | -0.084056 | 20.7094
114 | 0.0063431 | 0.0015892 | -0.006341 | -0.0015888 | 2.0827e-06 | 3.3453e-07 | 0.0095617 | 0.0095619 | 0.0095619 | 0.98711 | -0.09028 | 0.98678 | -0.092654 | 3.5414
115 | 0.030748 | 0.0077124 | -0.030741 | -0.0077098 | 6.8913e-06 | 2.5848e-06 | 0.046354 | 0.046354 | 0.046354 | 0.98711 | -0.09028 | 0.98688 | -0.091897 | 17.168
116 | -0.040531 | -0.010168 | 0.040578 | 0.010186 | 4.7246e-05 | 1.7911e-05 | 0.061047 | 0.061047 | 0.061047 | 0.98799 | -0.084056 | 0.98918 | -0.075661 | 22.6101
117 | 0.017671 | 0.0044301 | -0.017659 | -0.0044258 | 1.2164e-05 | 4.3304e-06 | 0.02669 | 0.02669 | 0.02669 | 0.9852 | -0.10384 | 0.9845 | -0.10881 | 9.8853
118 | -0.026095 | -0.0065435 | 0.026109 | 0.0065488 | 1.4417e-05 | 5.3546e-06 | 0.03937 | 0.03937 | 0.03937 | 0.9863 | -0.096038 | 0.98686 | -0.092054 | 14.5817
119 | 0.011637 | 0.0029166 | -0.011632 | -0.0029149 | 5.4184e-06 | 1.7273e-06 | 0.017589 | 0.017589 | 0.017589 | 0.9845 | -0.10881 | 0.98403 | -0.11217 | 6.5144
120 | 0.006341 | 0.0015888 | -0.00634 | -0.0015887 | 1.028e-06 | 1.6524e-07 | 0.0095619 | 0.0095619 | 0.0095619 | 0.98678 | -0.092654 | 0.98661 | -0.093826 | 3.5415
121 | 0.027534 | 0.0069059 | -0.027533 | -0.0069056 | 5.9786e-07 | 2.2284e-07 | 0.041517 | 0.041517 | 0.041517 | 0.98688 | -0.091897 | 0.98686 | -0.092054 | 15.3767
122 | 0.0099872 | 0.0025027 | -0.009986 | -0.0025024 | 1.1645e-06 | 3.4397e-07 | 0.015102 | 0.015102 | 0.015102 | 0.98403 | -0.11217 | 0.98391 | -0.11302 | 5.5934
123 | 0.0039473 | 0.00098899 | -0.0039473 | -0.000989 | 1.199e-08 | -2.3119e-09 | 0.0059533 | 0.0059533 | 0.0059533 | 0.98661 | -0.093826 | 0.98661 | -0.093848 | 2.2049
124 | -0.0031539 | -0.00079045 | 0.0031541 | 0.00079036 | 1.7203e-07 | -8.7108e-08 | 0.0047748 | 0.0047747 | 0.0047748 | 0.98289 | -0.12025 | 0.98295 | -0.11985 | 1.7684
125 | -0.0055249 | -0.0013845 | 0.0055261 | 0.0013847 | 1.2532e-06 | 1.1798e-07 | 0.0083637 | 0.0083636 | 0.0083637 | 0.98295 | -0.11985 | 0.98318 | -0.11821 | 3.0977
126 | -0.0067085 | -0.001681 | 0.0067102 | 0.0016813 | 1.7157e-06 | 3.2153e-07 | 0.010153 | 0.010153 | 0.010153 | 0.98318 | -0.11821 | 0.98344 | -0.11637 | 3.7604
127 | -0.0083504 | -0.0020924 | 0.0083523 | 0.0020929 | 1.9347e-06 | 4.9761e-07 | 0.012635 | 0.012635 | 0.012635 | 0.98344 | -0.11637 | 0.98367 | -0.11469 | 4.6795
128 | -0.0093966 | -0.0023546 | 0.0093987 | 0.0023552 | 2.1803e-06 | 6.1898e-07 | 0.014214 | 0.014214 | 0.014214 | 0.98367 | -0.11469 | 0.98391 | -0.11302 | 5.2645
129 | 0.0017116 | 0.00042867 | -0.0017115 | -0.00042894 | 1.0062e-07 | -2.703e-07 | 0.0025813 | 0.0025814 | 0.0025814 | 0.98661 | -0.093848 | 0.98655 | -0.094273 | 0.95609

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24547 | 0.061626

## res_load
| p_mw | q_mvar
0 | 0.001634 | 0.00040953
1 | 0.00043942 | 0.00011013
2 | 0.0011201 | 0.00028072
3 | 0.016338 | 0.0040946
4 | 0.0048018 | 0.0012034
5 | 0.0040863 | 0.0010241
6 | 0.00098151 | 0.00024599
7 | 0.00064059 | 0.00016055
8 | 0.0057701 | 0.0014461
9 | 0.003504 | 0.00087819
10 | 0.0031343 | 0.00078553
11 | 0.00071314 | 0.00017873
12 | 0.0015586 | 0.00039061
13 | 0.00078735 | 0.00019733
14 | 0.00031929 | 8.0023e-05
15 | 0.00041237 | 0.00010335
16 | 0.00098135 | 0.00024595
17 | 0.00063371 | 0.00015882
18 | 0.00046069 | 0.00011546
19 | 0.0017106 | 0.00042871
20 | 0.0014856 | 0.00037233
21 | 0.00045648 | 0.00011441
22 | 0.0088313 | 0.0022133
23 | 0.00068236 | 0.00017101
24 | 0.00047241 | 0.0001184
25 | 0.00051573 | 0.00012925
26 | 0.00021018 | 5.2676e-05
27 | 0.00050057 | 0.00012545
28 | 0.00094623 | 0.00023715
29 | 0.00028287 | 7.0893e-05
30 | 0.0013048 | 0.00032702
31 | 0.00023507 | 5.8913e-05
32 | 0.0010808 | 0.00027086
33 | 0.0036366 | 0.00091142
34 | 0.0022568 | 0.0005656
35 | 0.0073677 | 0.0018465
36 | 0.0027675 | 0.00069361
37 | 0.017412 | 0.0043639
38 | 0.0010484 | 0.00026275
39 | 0.00040803 | 0.00010226
40 | 0.0025413 | 0.00063692
41 | 0.00025431 | 6.3736e-05
42 | 0.0048019 | 0.0012035
43 | 0.00056628 | 0.00014192
44 | 0.00056639 | 0.00014195
45 | 0.00069316 | 0.00017372
46 | 0.00038709 | 9.7015e-05
47 | 0.0016851 | 0.00042232
48 | 0.0005622 | 0.0001409
49 | 0.0017348 | 0.00043477
50 | 0.015146 | 0.003796
51 | 0.0049589 | 0.0012428
52 | 0.013894 | 0.0034823
53 | 0.005835 | 0.0014624
54 | 0.0052266 | 0.0013099
55 | 0.0074962 | 0.0018787
56 | 0.00099317 | 0.00024891
57 | 0.00028614 | 7.1714e-05
58 | 0.00051413 | 0.00012885
59 | 0.00021467 | 5.3802e-05
60 | 0.00024442 | 6.1257e-05
61 | 0.00069264 | 0.00017359
62 | 0.00024222 | 6.0707e-05
63 | 0.00016737 | 4.1947e-05
64 | 0.00010565 | 2.6478e-05
65 | 0.0015284 | 0.00038305
66 | 0.00018142 | 4.5468e-05
67 | 0.00038032 | 9.5318e-05
68 | 0.00017197 | 4.3101e-05
69 | 0.00023796 | 5.964e-05
70 | 0.00018646 | 4.6732e-05
71 | 0.0001813 | 4.5437e-05
72 | 0.0013506 | 0.0003385
73 | 0.00035647 | 8.934e-05
74 | 0.0062055 | 0.0015552
75 | 0.0079502 | 0.0019925
76 | 0.0016726 | 0.0004192
77 | 0.0016726 | 0.0004192
78 | 0.0006868 | 0.00017213
79 | 0.0060448 | 0.001515
80 | 0.0034075 | 0.000854
81 | 0.0023576 | 0.00059087
82 | 0.0060218 | 0.0015092
83 | 0.0032078 | 0.00080394
84 | 0.0063211 | 0.0015842
85 | 0.0014237 | 0.00035681
86 | 0.0016444 | 0.00041213
87 | 0.0023927 | 0.00059966
88 | 0.00070606 | 0.00017696
89 | 0.0031539 | 0.00079045
90 | 0.0023708 | 0.00059418
91 | 0.0011823 | 0.00029632
92 | 0.0016402 | 0.00041107
93 | 0.0010442 | 0.00026171
94 | 0.00058731 | 0.00014719
95 | 0.0022357 | 0.00056033
96 | 0.0017115 | 0.00042894

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1