## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1081-36_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1081-36_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1081-36_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1081-36_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1081-36_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1081-36_0_4_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_1081-36_0_4_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_1081-36_0_4_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_1081-36_0_4_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_1081-36_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1081-36_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1081-36_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1081-36_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1081-36_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1081-36_0_4_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_1081-36_0_4_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_1081-36_0_4_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_1081-36_0_4_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1081-36_0_4_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_1081-36_0_4_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_1081-36_0_4_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1081-36_0_4_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_1081-36_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1081-36_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_1081-36_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_1081-36_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_MV_470_2_node_345 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1081-36_0_4_load_0 | 0 | 0.013337 | 0.0033425 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1081-36_0_4_load_1 | 1 | 0.00079763 | 0.0001999 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1081-36_0_4_load_4 | 4 | 0.0095966 | 0.0024051 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1081-36_0_4_load_19 | 5 | 0.00070849 | 0.00017757 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1081-36_0_4_load_5 | 9 | 0.014774 | 0.0037028 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1081-36_0_4_load_9 | 13 | 0.099114 | 0.02484 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1081-36_0_4_load_25 | 14 | 0.00082623 | 0.00020707 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1081-36_0_4_load_23 | 15 | 0.0008016 | 0.0002009 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1081-36_0_4_load_24 | 18 | 0.00079352 | 0.00019887 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1081-36_0_4_load_20 | 19 | 0.0032155 | 0.00080587 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1081-36_0_4_load_18 | 20 | 0.01794 | 0.0044961 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1081-36_0_4_load_26 | 21 | 0.036225 | 0.009079 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1081-36_0_4_load_16 | 22 | 0.0075619 | 0.0018952 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1081-36_0_4_load_13 | 23 | 0.002161 | 0.0005416 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1081-36_0_4_load_14 | 24 | 0.0090276 | 0.0022625 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1081-36_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1081-36_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.023389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1081-36_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.039623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1081-36_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0070927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1081-36_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.017417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1081-36_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.045169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1081-36_0_4_line_6 | NAYY 4x150 SE | 6 | 7 | 0.035074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1081-36_0_4_line_7 | NAYY 4x150 SE | 6 | 8 | 0.045279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1081-36_0_4_line_8 | NAYY 4x150 SE | 7 | 20 | 0.010447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1081-36_0_4_line_9 | NAYY 4x150 SE | 8 | 21 | 0.013998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1081-36_0_4_line_10 | NAYY 4x150 SE | 9 | 10 | 0.053365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_1081-36_0_4_line_11 | NAYY 4x150 SE | 9 | 11 | 0.019376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_1081-36_0_4_line_12 | NAYY 4x150 SE | 10 | 12 | 0.018921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_1081-36_0_4_line_13 | NAYY 4x150 SE | 11 | 13 | 0.0052259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_1081-36_0_4_line_14 | NAYY 4x150 SE | 12 | 14 | 0.022145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_1081-36_0_4_line_15 | NAYY 4x150 SE | 12 | 15 | 0.019268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1081-36_0_4_line_16 | NAYY 4x150 SE | 13 | 16 | 0.014206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_1081-36_0_4_line_17 | NAYY 4x150 SE | 14 | 17 | 0.024236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_1081-36_0_4_line_18 | NAYY 4x150 SE | 15 | 18 | 0.0012761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1081-36_0_4_line_19 | NAYY 4x150 SE | 16 | 19 | 0.018427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1081-36_0_4_line_20 | NAYY 4x150 SE | 17 | 25 | 0.038949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_1081-36_0_4_line_21 | NAYY 4x150 SE | 20 | 22 | 0.02995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1081-36_0_4_line_22 | NAYY 4x150 SE | 22 | 24 | 0.020187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1081-36_0_4_line_23 | NAYY 4x150 SE | 23 | 24 | 0.022489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1081-36_0_4_line_24 | NAYY 4x150 SE | 23 | 25 | 0.0080522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1081-36_0_4_trafo_22 | 0.25 MVA 20/0.4 kV | 26 | 16 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2657178.369 | 1228898.1092 | 2657209.5521 | 1228906.5301
1 | 2657155.6588 | 1228892.5587 | 2657164.8535 | 1228894.4594 | 2657178.369 | 1228898.1092
2 | 2657247.8045 | 1228916.86 | 2657209.5521 | 1228906.5301
3 | 2657155.6588 | 1228892.5587 | 2657148.7139 | 1228891.1182
4 | 2657247.8045 | 1228916.86 | 2657243.4869 | 1228933.7337
5 | 2657104.8236 | 1228889.113 | 2657108.1741 | 1228887.3551 | 2657111.8078 | 1228886.0892 | 2657115.9664 | 1228885.3953 | 2657119.702 | 1228885.3533 | 2657124.0144 | 1228885.9951 | 2657148.7139 | 1228891.1182
6 | 2657104.8236 | 1228889.113 | 2657100.3259 | 1228894.3509 | 2657084.0579 | 1228917.3873
7 | 2657129.1548 | 1228851.7115 | 2657107.9708 | 1228878.5475 | 2657106.4196 | 1228881.5012 | 2657105.4208 | 1228885.3051 | 2657104.8236 | 1228889.113
8 | 2657084.0579 | 1228917.3873 | 2657085.4908 | 1228922.8156 | 2657086.1284 | 1228926.6353 | 2657086.1765 | 1228927.594
9 | 2657129.1548 | 1228851.7115 | 2657136.3867 | 1228850.5135 | 2657142.653 | 1228848.2343
10 | 2657148.6874 | 1229049.5586 | 2657149.6614 | 1229034.147 | 2657154.8727 | 1229027.9598 | 2657156.7964 | 1229025.6657 | 2657164.2304 | 1229016.8203 | 2657179.4877 | 1229017.7453
11 | 2657181.7259 | 1228998.499 | 2657179.4877 | 1229017.7453
12 | 2657148.6874 | 1229049.5586 | 2657139.124 | 1229048.2104 | 2657129.835 | 1229047.4763
13 | 2657181.7259 | 1228998.499 | 2657182.3301 | 1228993.3081
14 | 2657129.835 | 1229047.4763 | 2657107.7001 | 1229046.7974
15 | 2657129.835 | 1229047.4763 | 2657130.5389 | 1229028.2209
16 | 2657183.9723 | 1228979.1971 | 2657182.3301 | 1228993.3081
17 | 2657083.466 | 1229046.9309 | 2657105.0301 | 1229046.7155 | 2657107.7001 | 1229046.7974
18 | 2657130.5389 | 1229028.2209 | 2657130.5856 | 1229026.9457
19 | 2657183.9723 | 1228979.1971 | 2657202.3796 | 1228980.0473
20 | 2657081.3158 | 1229008.1078 | 2657081.3474 | 1229028.4989 | 2657082.2119 | 1229037.8798 | 2657083.466 | 1229046.9309
21 | 2657084.577 | 1228957.4841 | 2657086.3192 | 1228930.4396 | 2657086.1765 | 1228927.594
22 | 2657083.2792 | 1228977.6295 | 2657084.577 | 1228957.4841
23 | 2657081.8334 | 1229000.0722 | 2657083.2792 | 1228977.6295
24 | 2657081.3158 | 1229008.1078 | 2657081.8334 | 1229000.0722

## bus_geodata
| x | y | coords
0 | 2657178.369 | 1228898.1092
1 | 2657209.5521 | 1228906.5301
2 | 2657155.6588 | 1228892.5587
3 | 2657247.8045 | 1228916.86
4 | 2657148.7139 | 1228891.1182
5 | 2657243.4869 | 1228933.7337
6 | 2657104.8236 | 1228889.113
7 | 2657084.0579 | 1228917.3873
8 | 2657129.1548 | 1228851.7115
9 | 2657179.4877 | 1229017.7453
10 | 2657148.6874 | 1229049.5586
11 | 2657181.7259 | 1228998.499
12 | 2657129.835 | 1229047.4763
13 | 2657182.3301 | 1228993.3081
14 | 2657107.7001 | 1229046.7974
15 | 2657130.5389 | 1229028.2209
16 | 2657183.9723 | 1228979.1971
17 | 2657083.466 | 1229046.9309
18 | 2657130.5856 | 1229026.9457
19 | 2657202.3796 | 1228980.0473
20 | 2657086.1765 | 1228927.594
21 | 2657142.653 | 1228848.2343
22 | 2657084.577 | 1228957.4841
23 | 2657081.8334 | 1229000.0722
24 | 2657083.2792 | 1228977.6295
25 | 2657081.3158 | 1229008.1078
26 | 2657181.7259 | 1228998.499

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97207 | -0.19616 | 0.013337 | 0.0033425
1 | 0.972 | -0.19668 | 0.00079763 | 0.0001999
2 | 0.97258 | -0.1925 | 0 | 0
3 | 0.97196 | -0.19698 | 0 | 0
4 | 0.97274 | -0.19139 | 0.0095966 | 0.0024051
5 | 0.97194 | -0.19711 | 0.00070849 | 0.00017757
6 | 0.97436 | -0.17976 | 0 | 0
7 | 0.97748 | -0.15745 | 0 | 0
8 | 0.97195 | -0.19704 | 0 | 0
9 | 0.99717 | -0.019539 | 0.014774 | 0.0037028
10 | 0.99458 | -0.037412 | 0 | 0
11 | 0.99825 | -0.012116 | 0 | 0
12 | 0.99366 | -0.043771 | 0 | 0
13 | 0.99854 | -0.010117 | 0.099114 | 0.02484
14 | 0.9926 | -0.051109 | 0.00082623 | 0.00020707
15 | 0.99361 | -0.044082 | 0.0008016 | 0.0002009
16 | 1 | 0 | -0.22028 | -0.055342
17 | 0.99145 | -0.059088 | 0 | 0
18 | 0.99361 | -0.044092 | 0.00079352 | 0.00019887
19 | 0.99992 | -0.00059156 | 0.0032155 | 0.00080587
20 | 0.97841 | -0.15084 | 0.01794 | 0.0044961
21 | 0.9712 | -0.20241 | 0.036225 | 0.009079
22 | 0.98185 | -0.12637 | 0.0075619 | 0.0018952
23 | 0.98753 | -0.086416 | 0.002161 | 0.0005416
24 | 0.9844 | -0.1084 | 0.0090276 | 0.0022625
25 | 0.98868 | -0.0784 | 0 | 0
26 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0015063 | 0.00037642 | -0.0015062 | -0.00037678 | 1.0712e-07 | -3.5919e-07 | 0.0023054 | 0.0023055 | 0.0023055 | 0.97207 | -0.19616 | 0.972 | -0.19668 | 0.85389
1 | -0.014843 | -0.0037189 | 0.01485 | 0.0037215 | 7.534e-06 | 2.6076e-06 | 0.022721 | 0.02272 | 0.022721 | 0.97207 | -0.19616 | 0.97258 | -0.1925 | 8.415
2 | 0.00070854 | 0.00017687 | -0.00070851 | -0.00017735 | 2.908e-08 | -4.7991e-07 | 0.0010844 | 0.0010846 | 0.0010846 | 0.972 | -0.19668 | 0.97196 | -0.19698 | 0.40171
3 | -0.01485 | -0.0037215 | 0.014853 | 0.0037223 | 2.2847e-06 | 7.9069e-07 | 0.02272 | 0.02272 | 0.02272 | 0.97258 | -0.1925 | 0.97274 | -0.19139 | 8.415
4 | 0.00070851 | 0.00017735 | -0.00070849 | -0.00017757 | 1.2786e-08 | -2.1095e-07 | 0.0010846 | 0.0010847 | 0.0010847 | 0.97196 | -0.19698 | 0.97194 | -0.19711 | 0.40173
5 | -0.024449 | -0.0061274 | 0.024489 | 0.006142 | 3.9425e-05 | 1.4602e-05 | 0.037401 | 0.0374 | 0.037401 | 0.97274 | -0.19139 | 0.97436 | -0.17976 | 13.8521
6 | -0.060828 | -0.015264 | 0.061017 | 0.015336 | 0.0001889 | 7.2214e-05 | 0.092902 | 0.092902 | 0.092902 | 0.97436 | -0.17976 | 0.97748 | -0.15745 | 34.4083
7 | 0.036339 | 0.009122 | -0.036252 | -0.0090891 | 8.7036e-05 | 3.2913e-05 | 0.055502 | 0.055502 | 0.055502 | 0.97436 | -0.17976 | 0.97195 | -0.19704 | 20.5564
8 | -0.061017 | -0.015336 | 0.061073 | 0.015358 | 5.6262e-05 | 2.1508e-05 | 0.092902 | 0.092902 | 0.092902 | 0.97748 | -0.15745 | 0.97841 | -0.15084 | 34.4082
9 | 0.036252 | 0.0090891 | -0.036225 | -0.009079 | 2.6908e-05 | 1.0176e-05 | 0.055502 | 0.055502 | 0.055502 | 0.97195 | -0.19704 | 0.9712 | -0.20241 | 20.5564
10 | 0.10191 | 0.025817 | -0.10165 | -0.02572 | 0.00025704 | 9.6779e-05 | 0.15217 | 0.15217 | 0.15217 | 0.99717 | -0.019539 | 0.99458 | -0.037412 | 18.7869
11 | -0.11669 | -0.02952 | 0.11681 | 0.029566 | 0.00012233 | 4.629e-05 | 0.17422 | 0.17422 | 0.17422 | 0.99717 | -0.019539 | 0.99825 | -0.012116 | 21.5086
12 | 0.10165 | 0.02572 | -0.10156 | -0.025686 | 9.1136e-05 | 3.4316e-05 | 0.15217 | 0.15217 | 0.15217 | 0.99458 | -0.037412 | 0.99366 | -0.043771 | 18.7869
13 | -0.11681 | -0.029566 | 0.11684 | 0.029579 | 3.2993e-05 | 1.2484e-05 | 0.17422 | 0.17422 | 0.17422 | 0.99825 | -0.012116 | 0.99854 | -0.010117 | 21.5086
14 | 0.099968 | 0.025287 | -0.099864 | -0.025248 | 0.00010334 | 3.8888e-05 | 0.14979 | 0.14979 | 0.14979 | 0.99366 | -0.043771 | 0.9926 | -0.051109 | 18.4921
15 | 0.0015952 | 0.00039954 | -0.0015951 | -0.00039976 | 6.8608e-08 | -2.2319e-07 | 0.0023887 | 0.0023888 | 0.0023888 | 0.99366 | -0.043771 | 0.99361 | -0.044082 | 0.88475
16 | -0.21595 | -0.054419 | 0.21626 | 0.054536 | 0.00030622 | 0.00011722 | 0.32192 | 0.32192 | 0.32192 | 0.99854 | -0.010117 | 1 | 0 | 39.743
17 | 0.099038 | 0.025041 | -0.098927 | -0.024999 | 0.00011124 | 4.1846e-05 | 0.14855 | 0.14855 | 0.14855 | 0.9926 | -0.051109 | 0.99145 | -0.059088 | 18.3392
18 | 0.00079352 | 0.00019886 | -0.00079352 | -0.00019887 | 1.1245e-09 | -1.6095e-08 | 0.0011884 | 0.0011884 | 0.0011884 | 0.99361 | -0.044082 | 0.99361 | -0.044092 | 0.44013
19 | 0.0032157 | 0.00080573 | -0.0032155 | -0.00080587 | 2.6327e-07 | -1.4047e-07 | 0.004785 | 0.0047851 | 0.0047851 | 1 | 0 | 0.99992 | -0.00059156 | 1.7723
20 | 0.098927 | 0.024999 | -0.098659 | -0.024897 | 0.00026816 | 0.00010214 | 0.14855 | 0.14855 | 0.14855 | 0.99145 | -0.059088 | 0.98868 | -0.0784 | 27.5089
21 | -0.079013 | -0.019854 | 0.079283 | 0.019957 | 0.00026995 | 0.00010345 | 0.12019 | 0.12019 | 0.12019 | 0.97841 | -0.15084 | 0.98185 | -0.12637 | 44.5133
22 | -0.086845 | -0.021853 | 0.087063 | 0.021936 | 0.00021831 | 8.3709e-05 | 0.13165 | 0.13165 | 0.13165 | 0.98185 | -0.12637 | 0.9844 | -0.1084 | 48.7577
23 | 0.096387 | 0.024312 | -0.096091 | -0.024199 | 0.00029624 | 0.00011365 | 0.14529 | 0.14529 | 0.14529 | 0.98753 | -0.086416 | 0.9844 | -0.1084 | 53.8118
24 | -0.098548 | -0.024854 | 0.098659 | 0.024897 | 0.00011087 | 4.2541e-05 | 0.14855 | 0.14855 | 0.14855 | 0.98753 | -0.086416 | 0.98868 | -0.0784 | 55.0178

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22028 | 0.055342

## res_load
| p_mw | q_mvar
0 | 0.013337 | 0.0033425
1 | 0.00079763 | 0.0001999
2 | 0.0095966 | 0.0024051
3 | 0.00070849 | 0.00017757
4 | 0.014774 | 0.0037028
5 | 0.099114 | 0.02484
6 | 0.00082623 | 0.00020707
7 | 0.0008016 | 0.0002009
8 | 0.00079352 | 0.00019887
9 | 0.0032155 | 0.00080587
10 | 0.01794 | 0.0044961
11 | 0.036225 | 0.009079
12 | 0.0075619 | 0.0018952
13 | 0.002161 | 0.0005416
14 | 0.0090276 | 0.0022625

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1