## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1081-8_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1081-8_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1081-8_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1081-8_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1081-8_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1081-8_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1081-8_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1081-8_0_4_node_37 | 0.4 | n |  | TRUE
8 | bus_LV_1081-8_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1081-8_0_4_node_35 | 0.4 | n |  | TRUE
10 | bus_LV_1081-8_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1081-8_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1081-8_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1081-8_0_4_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_1081-8_0_4_node_51 | 0.4 | n |  | TRUE
15 | bus_LV_1081-8_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1081-8_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1081-8_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1081-8_0_4_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1081-8_0_4_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_1081-8_0_4_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1081-8_0_4_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_1081-8_0_4_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_1081-8_0_4_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1081-8_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1081-8_0_4_node_87 | 0.4 | n |  | TRUE
26 | bus_LV_1081-8_0_4_node_86 | 0.4 | n |  | TRUE
27 | bus_LV_1081-8_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_1081-8_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_1081-8_0_4_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_1081-8_0_4_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_1081-8_0_4_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_1081-8_0_4_node_141 | 0.4 | n |  | TRUE
33 | bus_LV_1081-8_0_4_node_142 | 0.4 | n |  | TRUE
34 | bus_LV_1081-8_0_4_node_44 | 0.4 | n |  | TRUE
35 | bus_LV_1081-8_0_4_node_64 | 0.4 | n |  | TRUE
36 | bus_LV_1081-8_0_4_node_57 | 0.4 | n |  | TRUE
37 | bus_LV_1081-8_0_4_node_40 | 0.4 | n |  | TRUE
38 | bus_LV_1081-8_0_4_node_49 | 0.4 | n |  | TRUE
39 | bus_LV_1081-8_0_4_node_56 | 0.4 | n |  | TRUE
40 | bus_LV_1081-8_0_4_node_39 | 0.4 | n |  | TRUE
41 | bus_LV_1081-8_0_4_node_50 | 0.4 | n |  | TRUE
42 | bus_LV_1081-8_0_4_node_47 | 0.4 | n |  | TRUE
43 | bus_LV_1081-8_0_4_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_1081-8_0_4_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_1081-8_0_4_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_1081-8_0_4_node_32 | 0.4 | n |  | TRUE
47 | bus_LV_1081-8_0_4_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_1081-8_0_4_node_53 | 0.4 | n |  | TRUE
49 | bus_LV_1081-8_0_4_node_52 | 0.4 | n |  | TRUE
50 | bus_LV_1081-8_0_4_node_143 | 0.4 | n |  | TRUE
51 | bus_LV_1081-8_0_4_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_1081-8_0_4_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_1081-8_0_4_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_1081-8_0_4_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_1081-8_0_4_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_1081-8_0_4_node_42 | 0.4 | n |  | TRUE
57 | bus_LV_1081-8_0_4_node_43 | 0.4 | n |  | TRUE
58 | bus_LV_1081-8_0_4_node_45 | 0.4 | n |  | TRUE
59 | bus_LV_1081-8_0_4_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_1081-8_0_4_node_54 | 0.4 | n |  | TRUE
61 | bus_LV_1081-8_0_4_node_55 | 0.4 | n |  | TRUE
62 | bus_LV_1081-8_0_4_node_58 | 0.4 | n |  | TRUE
63 | bus_LV_1081-8_0_4_node_59 | 0.4 | n |  | TRUE
64 | bus_LV_1081-8_0_4_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_1081-8_0_4_node_61 | 0.4 | n |  | TRUE
66 | bus_LV_1081-8_0_4_node_62 | 0.4 | n |  | TRUE
67 | bus_LV_1081-8_0_4_node_79 | 0.4 | n |  | TRUE
68 | bus_LV_1081-8_0_4_node_80 | 0.4 | n |  | TRUE
69 | bus_LV_1081-8_0_4_node_75 | 0.4 | n |  | TRUE
70 | bus_LV_1081-8_0_4_node_84 | 0.4 | n |  | TRUE
71 | bus_LV_1081-8_0_4_node_63 | 0.4 | n |  | TRUE
72 | bus_LV_1081-8_0_4_node_65 | 0.4 | n |  | TRUE
73 | bus_LV_1081-8_0_4_node_66 | 0.4 | n |  | TRUE
74 | bus_LV_1081-8_0_4_node_67 | 0.4 | n |  | TRUE
75 | bus_LV_1081-8_0_4_node_78 | 0.4 | n |  | TRUE
76 | bus_LV_1081-8_0_4_node_73 | 0.4 | n |  | TRUE
77 | bus_LV_1081-8_0_4_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_1081-8_0_4_node_69 | 0.4 | n |  | TRUE
79 | bus_LV_1081-8_0_4_node_70 | 0.4 | n |  | TRUE
80 | bus_LV_1081-8_0_4_node_71 | 0.4 | n |  | TRUE
81 | bus_LV_1081-8_0_4_node_72 | 0.4 | n |  | TRUE
82 | bus_LV_1081-8_0_4_node_82 | 0.4 | n |  | TRUE
83 | bus_LV_1081-8_0_4_node_81 | 0.4 | n |  | TRUE
84 | bus_LV_1081-8_0_4_node_74 | 0.4 | n |  | TRUE
85 | bus_LV_1081-8_0_4_node_76 | 0.4 | n |  | TRUE
86 | bus_LV_1081-8_0_4_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_1081-8_0_4_node_83 | 0.4 | n |  | TRUE
88 | bus_LV_1081-8_0_4_node_88 | 0.4 | n |  | TRUE
89 | bus_LV_1081-8_0_4_node_89 | 0.4 | n |  | TRUE
90 | bus_LV_1081-8_0_4_node_90 | 0.4 | n |  | TRUE
91 | bus_LV_1081-8_0_4_node_91 | 0.4 | n |  | TRUE
92 | bus_LV_1081-8_0_4_node_92 | 0.4 | n |  | TRUE
93 | bus_LV_1081-8_0_4_node_93 | 0.4 | n |  | TRUE
94 | bus_LV_1081-8_0_4_node_116 | 0.4 | n |  | TRUE
95 | bus_LV_1081-8_0_4_node_117 | 0.4 | n |  | TRUE
96 | bus_LV_1081-8_0_4_node_140 | 0.4 | n |  | TRUE
97 | bus_LV_1081-8_0_4_node_108 | 0.4 | n |  | TRUE
98 | bus_LV_1081-8_0_4_node_136 | 0.4 | n |  | TRUE
99 | bus_LV_1081-8_0_4_node_138 | 0.4 | n |  | TRUE
100 | bus_LV_1081-8_0_4_node_144 | 0.4 | n |  | TRUE
101 | bus_LV_1081-8_0_4_node_103 | 0.4 | n |  | TRUE
102 | bus_LV_1081-8_0_4_node_94 | 0.4 | n |  | TRUE
103 | bus_LV_1081-8_0_4_node_95 | 0.4 | n |  | TRUE
104 | bus_LV_1081-8_0_4_node_96 | 0.4 | n |  | TRUE
105 | bus_LV_1081-8_0_4_node_97 | 0.4 | n |  | TRUE
106 | bus_LV_1081-8_0_4_node_98 | 0.4 | n |  | TRUE
107 | bus_LV_1081-8_0_4_node_99 | 0.4 | n |  | TRUE
108 | bus_LV_1081-8_0_4_node_132 | 0.4 | n |  | TRUE
109 | bus_LV_1081-8_0_4_node_134 | 0.4 | n |  | TRUE
110 | bus_LV_1081-8_0_4_node_102 | 0.4 | n |  | TRUE
111 | bus_LV_1081-8_0_4_node_133 | 0.4 | n |  | TRUE
112 | bus_LV_1081-8_0_4_node_135 | 0.4 | n |  | TRUE
113 | bus_LV_1081-8_0_4_node_104 | 0.4 | n |  | TRUE
114 | bus_LV_1081-8_0_4_node_100 | 0.4 | n |  | TRUE
115 | bus_LV_1081-8_0_4_node_101 | 0.4 | n |  | TRUE
116 | bus_LV_1081-8_0_4_node_105 | 0.4 | n |  | TRUE
117 | bus_LV_1081-8_0_4_node_106 | 0.4 | n |  | TRUE
118 | bus_LV_1081-8_0_4_node_107 | 0.4 | n |  | TRUE
119 | bus_LV_1081-8_0_4_node_109 | 0.4 | n |  | TRUE
120 | bus_LV_1081-8_0_4_node_110 | 0.4 | n |  | TRUE
121 | bus_LV_1081-8_0_4_node_111 | 0.4 | n |  | TRUE
122 | bus_LV_1081-8_0_4_node_112 | 0.4 | n |  | TRUE
123 | bus_LV_1081-8_0_4_node_113 | 0.4 | n |  | TRUE
124 | bus_LV_1081-8_0_4_node_118 | 0.4 | n |  | TRUE
125 | bus_LV_1081-8_0_4_node_131 | 0.4 | n |  | TRUE
126 | bus_LV_1081-8_0_4_node_123 | 0.4 | n |  | TRUE
127 | bus_LV_1081-8_0_4_node_128 | 0.4 | n |  | TRUE
128 | bus_LV_1081-8_0_4_node_129 | 0.4 | n |  | TRUE
129 | bus_LV_1081-8_0_4_node_137 | 0.4 | n |  | TRUE
130 | bus_LV_1081-8_0_4_node_119 | 0.4 | n |  | TRUE
131 | bus_LV_1081-8_0_4_node_120 | 0.4 | n |  | TRUE
132 | bus_LV_1081-8_0_4_node_121 | 0.4 | n |  | TRUE
133 | bus_LV_1081-8_0_4_node_124 | 0.4 | n |  | TRUE
134 | bus_LV_1081-8_0_4_node_125 | 0.4 | n |  | TRUE
135 | bus_LV_1081-8_0_4_node_126 | 0.4 | n |  | TRUE
136 | bus_LV_1081-8_0_4_node_127 | 0.4 | n |  | TRUE
137 | bus_MV_470_2_node_169 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1081-8_0_4_load_0 | 0 | 0.0010893 | 0.000273 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1081-8_0_4_load_1 | 1 | 0.00039862 | 9.9904e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1081-8_0_4_load_2 | 2 | 0.00062333 | 0.00015622 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1081-8_0_4_load_3 | 3 | 0.00080557 | 0.00020189 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1081-8_0_4_load_4 | 4 | 0.00038853 | 9.7375e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1081-8_0_4_load_6 | 5 | 0.0001674 | 4.1954e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1081-8_0_4_load_5 | 6 | 0.00058696 | 0.0001471 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1081-8_0_4_load_37 | 7 | 4.2054e-05 | 1.054e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1081-8_0_4_load_35 | 9 | 9.7892e-05 | 2.4534e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1081-8_0_4_load_15 | 13 | 0.00015651 | 3.9225e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1081-8_0_4_load_51 | 14 | 9.0589e-05 | 2.2704e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1081-8_0_4_load_10 | 16 | 0.000349 | 8.7468e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1081-8_0_4_load_12 | 17 | 0.00054418 | 0.00013638 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1081-8_0_4_load_16 | 18 | 0.00038785 | 9.7205e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1081-8_0_4_load_18 | 20 | 0.00014318 | 3.5883e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1081-8_0_4_load_23 | 22 | 0.00066883 | 0.00016762 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1081-8_0_4_load_21 | 23 | 0.00018031 | 4.5191e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1081-8_0_4_load_20 | 24 | 0.00014263 | 3.5748e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1081-8_0_4_load_87 | 25 | 0.00045045 | 0.00011289 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1081-8_0_4_load_24 | 27 | 0.00035282 | 8.8426e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1081-8_0_4_load_25 | 28 | 0.00016485 | 4.1315e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1081-8_0_4_load_26 | 29 | 0.00017545 | 4.3972e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1081-8_0_4_load_27 | 30 | 6.6159e-05 | 1.6581e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1081-8_0_4_load_141 | 32 | 0.0011114 | 0.00027855 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1081-8_0_4_load_44 | 34 | 0.00034464 | 8.6375e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1081-8_0_4_load_64 | 35 | 0.00032516 | 8.1494e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1081-8_0_4_load_57 | 36 | 0.00010665 | 2.6728e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1081-8_0_4_load_40 | 37 | 7.9274e-05 | 1.9868e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1081-8_0_4_load_56 | 39 | 0.00018681 | 4.6818e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1081-8_0_4_load_39 | 40 | 4.6022e-05 | 1.1534e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1081-8_0_4_load_50 | 41 | 7.5351e-05 | 1.8885e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1081-8_0_4_load_47 | 42 | 0.00013435 | 3.3672e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1081-8_0_4_load_29 | 43 | 0.00038147 | 9.5606e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1081-8_0_4_load_30 | 44 | 8.3783e-05 | 2.0998e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1081-8_0_4_load_31 | 45 | 0.00018491 | 4.6343e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1081-8_0_4_load_32 | 46 | 0.0006273 | 0.00015722 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1081-8_0_4_load_33 | 47 | 0.00011062 | 2.7724e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1081-8_0_4_load_53 | 48 | 8.7566e-05 | 2.1946e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1081-8_0_4_load_52 | 49 | 0.00015506 | 3.8861e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1081-8_0_4_load_143 | 50 | 0.0029174 | 0.00073118 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1081-8_0_4_load_34 | 51 | 6.6139e-05 | 1.6576e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1081-8_0_4_load_38 | 53 | 0.000478 | 0.0001198 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1081-8_0_4_load_48 | 54 | 0.00037417 | 9.3775e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1081-8_0_4_load_41 | 55 | 0.00036921 | 9.2533e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1081-8_0_4_load_42 | 56 | 6.0244e-05 | 1.5098e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1081-8_0_4_load_43 | 57 | 0.00040472 | 0.00010143 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1081-8_0_4_load_45 | 58 | 0.00034236 | 8.5803e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1081-8_0_4_load_46 | 59 | 0.0011171 | 0.00027996 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1081-8_0_4_load_54 | 60 | 0.00064271 | 0.00016108 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1081-8_0_4_load_55 | 61 | 0.0013326 | 0.00033398 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1081-8_0_4_load_58 | 62 | 0.00011205 | 2.8083e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1081-8_0_4_load_59 | 63 | 7.0474e-05 | 1.7662e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1081-8_0_4_load_60 | 64 | 0.00017464 | 4.3769e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1081-8_0_4_load_79 | 67 | 0.00030712 | 7.6971e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1081-8_0_4_load_80 | 68 | 0.00024807 | 6.2173e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1081-8_0_4_load_75 | 69 | 0.00060443 | 0.00015148 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1081-8_0_4_load_84 | 70 | 0.00014996 | 3.7583e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1081-8_0_4_load_63 | 71 | 0.00068124 | 0.00017074 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1081-8_0_4_load_65 | 72 | 0.00012973 | 3.2513e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1081-8_0_4_load_66 | 73 | 9.8665e-05 | 2.4728e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1081-8_0_4_load_67 | 74 | 0.00064641 | 0.00016201 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1081-8_0_4_load_78 | 75 | 0.00038887 | 9.7459e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1081-8_0_4_load_68 | 77 | 0.00041112 | 0.00010304 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1081-8_0_4_load_69 | 78 | 0.00028587 | 7.1646e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1081-8_0_4_load_70 | 79 | 0.00029147 | 7.305e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1081-8_0_4_load_71 | 80 | 4.6759e-05 | 1.1719e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1081-8_0_4_load_72 | 81 | 6.5729e-05 | 1.6473e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1081-8_0_4_load_82 | 82 | 0.00022103 | 5.5396e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1081-8_0_4_load_81 | 83 | 0.00012191 | 3.0552e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1081-8_0_4_load_74 | 84 | 0.00041667 | 0.00010443 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1081-8_0_4_load_76 | 85 | 0.0020819 | 0.00052177 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1081-8_0_4_load_77 | 86 | 0.001403 | 0.00035162 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1081-8_0_4_load_83 | 87 | 0.00038902 | 9.7499e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1081-8_0_4_load_88 | 88 | 0.00017884 | 4.4821e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1081-8_0_4_load_89 | 89 | 0.00019697 | 4.9364e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1081-8_0_4_load_93 | 93 | 0.00038173 | 9.5671e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1081-8_0_4_load_117 | 95 | 0.0084665 | 0.0021219 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1081-8_0_4_load_108 | 97 | 0.00036293 | 9.0959e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1081-8_0_4_load_136 | 98 | 0.0032613 | 0.00081737 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1081-8_0_4_load_144 | 100 | 0.0047814 | 0.0011983 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1081-8_0_4_load_103 | 101 | 0.0062453 | 0.0015652 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1081-8_0_4_load_94 | 102 | 0.0023387 | 0.00058612 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1081-8_0_4_load_95 | 103 | 0.0023348 | 0.00058515 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1081-8_0_4_load_97 | 105 | 0.013448 | 0.0033704 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1081-8_0_4_load_98 | 106 | 0.001805 | 0.00045238 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1081-8_0_4_load_99 | 107 | 0.0135 | 0.0033835 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1081-8_0_4_load_132 | 108 | 0.002399 | 0.00060125 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1081-8_0_4_load_134 | 109 | 0.0017808 | 0.00044631 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1081-8_0_4_load_133 | 111 | 0.0024016 | 0.0006019 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1081-8_0_4_load_135 | 112 | 0.0024087 | 0.00060367 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1081-8_0_4_load_104 | 113 | 0.0084327 | 0.0021134 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1081-8_0_4_load_100 | 114 | 0.0048282 | 0.0012101 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1081-8_0_4_load_101 | 115 | 0.0057253 | 0.0014349 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1081-8_0_4_load_105 | 116 | 0.0115 | 0.0028822 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1081-8_0_4_load_106 | 117 | 0.00098501 | 0.00024687 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1081-8_0_4_load_107 | 118 | 0.0014175 | 0.00035525 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1081-8_0_4_load_109 | 119 | 0.0025463 | 0.00063817 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1081-8_0_4_load_110 | 120 | 0.0011694 | 0.00029307 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1081-8_0_4_load_111 | 121 | 0.0024056 | 0.00060291 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1081-8_0_4_load_112 | 122 | 0.0011693 | 0.00029305 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1081-8_0_4_load_113 | 123 | 0.0024058 | 0.00060295 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1081-8_0_4_load_118 | 124 | 0.0020115 | 0.00050412 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1081-8_0_4_load_123 | 126 | 0.0041193 | 0.0010324 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1081-8_0_4_load_128 | 127 | 0.0044371 | 0.001112 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1081-8_0_4_load_129 | 128 | 0.0044672 | 0.0011196 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1081-8_0_4_load_137 | 129 | 0.011499 | 0.002882 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1081-8_0_4_load_119 | 130 | 0.0056424 | 0.0014141 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1081-8_0_4_load_120 | 131 | 0.00099725 | 0.00024994 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1081-8_0_4_load_124 | 133 | 0.004288 | 0.0010747 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1081-8_0_4_load_125 | 134 | 0.0050039 | 0.0012541 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1081-8_0_4_load_126 | 135 | 0.0041136 | 0.001031 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1081-8_0_4_load_127 | 136 | 0.0037529 | 0.00094055 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 101 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1081-8_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.017526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1081-8_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.017935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1081-8_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.013994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1081-8_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.03371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1081-8_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.17211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1081-8_0_4_line_5 | NAYY 4x150 SE | 5 | 6 | 0.025358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1081-8_0_4_line_6 | NAYY 4x150 SE | 6 | 10 | 0.051005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1081-8_0_4_line_7 | NAYY 4x150 SE | 7 | 8 | 0.55357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1081-8_0_4_line_8 | NAYY 4x150 SE | 7 | 9 | 0.0045592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1081-8_0_4_line_9 | NAYY 4x150 SE | 8 | 15 | 0.00772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1081-8_0_4_line_10 | NAYY 4x150 SE | 8 | 16 | 0.027442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1081-8_0_4_line_11 | NAYY 4x150 SE | 9 | 51 | 0.015067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1081-8_0_4_line_12 | NAYY 4x150 SE | 10 | 11 | 0.01518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1081-8_0_4_line_13 | NAYY 4x150 SE | 10 | 12 | 0.042743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1081-8_0_4_line_14 | NAYY 4x150 SE | 11 | 13 | 0.019776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1081-8_0_4_line_15 | NAYY 4x150 SE | 12 | 14 | 0.016085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1081-8_0_4_line_16 | NAYY 4x150 SE | 13 | 15 | 0.012258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1081-8_0_4_line_17 | NAYY 4x150 SE | 16 | 17 | 0.0072771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1081-8_0_4_line_18 | NAYY 4x150 SE | 18 | 19 | 0.010005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1081-8_0_4_line_19 | NAYY 4x150 SE | 19 | 20 | 0.020118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1081-8_0_4_line_20 | NAYY 4x150 SE | 19 | 21 | 0.058808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1081-8_0_4_line_21 | NAYY 4x150 SE | 20 | 22 | 0.0071191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1081-8_0_4_line_22 | NAYY 4x150 SE | 21 | 23 | 0.04953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1081-8_0_4_line_23 | NAYY 4x150 SE | 21 | 24 | 0.068971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1081-8_0_4_line_24 | NAYY 4x150 SE | 23 | 25 | 0.027571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1081-8_0_4_line_25 | NAYY 4x150 SE | 25 | 26 | 0.033705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1081-8_0_4_line_26 | NAYY 4x150 SE | 26 | 70 | 0.071794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1081-8_0_4_line_27 | NAYY 4x150 SE | 26 | 66 | 0.02048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1081-8_0_4_line_28 | NAYY 4x150 SE | 27 | 28 | 0.0010407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1081-8_0_4_line_29 | NAYY 4x150 SE | 27 | 29 | 0.031212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1081-8_0_4_line_30 | NAYY 4x150 SE | 28 | 30 | 0.007751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1081-8_0_4_line_31 | NAYY 4x150 SE | 29 | 31 | 0.019656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1081-8_0_4_line_32 | NAYY 4x150 SE | 30 | 36 | 0.0070392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1081-8_0_4_line_33 | NAYY 4x150 SE | 31 | 37 | 0.0527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1081-8_0_4_line_34 | NAYY 4x150 SE | 31 | 38 | 0.013793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1081-8_0_4_line_35 | NAYY 4x150 SE | 32 | 33 | 0.091981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_1081-8_0_4_line_36 | NAYY 4x150 SE | 32 | 34 | 0.43345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
37 | LV_1081-8_0_4_line_37 | NAYY 4x150 SE | 32 | 35 | 0.32427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1081-8_0_4_line_38 | NAYY 4x150 SE | 33 | 50 | 0.027532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_1081-8_0_4_line_39 | NAYY 4x150 SE | 34 | 58 | 0.014199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1081-8_0_4_line_40 | NAYY 4x150 SE | 35 | 73 | 0.017897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1081-8_0_4_line_41 | NAYY 4x150 SE | 35 | 71 | 0.044159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1081-8_0_4_line_42 | NAYY 4x150 SE | 36 | 39 | 0.018685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1081-8_0_4_line_43 | NAYY 4x150 SE | 37 | 40 | 0.032997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1081-8_0_4_line_44 | NAYY 4x150 SE | 38 | 41 | 0.028287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1081-8_0_4_line_45 | NAYY 4x150 SE | 38 | 42 | 0.027291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1081-8_0_4_line_46 | NAYY 4x150 SE | 39 | 47 | 0.026361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1081-8_0_4_line_47 | NAYY 4x150 SE | 40 | 55 | 0.011566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1081-8_0_4_line_48 | NAYY 4x150 SE | 41 | 61 | 0.034438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1081-8_0_4_line_49 | NAYY 4x150 SE | 42 | 54 | 0.00035632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1081-8_0_4_line_50 | NAYY 4x150 SE | 43 | 44 | 0.086642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1081-8_0_4_line_51 | NAYY 4x150 SE | 43 | 45 | 0.014803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1081-8_0_4_line_52 | NAYY 4x150 SE | 44 | 46 | 0.053546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1081-8_0_4_line_53 | NAYY 4x150 SE | 45 | 47 | 0.010148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1081-8_0_4_line_54 | NAYY 4x150 SE | 46 | 48 | 0.075927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1081-8_0_4_line_55 | NAYY 4x150 SE | 48 | 49 | 0.055334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1081-8_0_4_line_56 | NAYY 4x150 SE | 50 | 100 | 0.25786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
57 | LV_1081-8_0_4_line_57 | NAYY 4x150 SE | 51 | 52 | 0.049759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1081-8_0_4_line_58 | NAYY 4x150 SE | 52 | 53 | 0.040311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1081-8_0_4_line_59 | NAYY 4x150 SE | 53 | 54 | 0.017166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1081-8_0_4_line_60 | NAYY 4x150 SE | 55 | 56 | 0.020851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1081-8_0_4_line_61 | NAYY 4x150 SE | 56 | 57 | 0.018423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1081-8_0_4_line_62 | NAYY 4x150 SE | 58 | 59 | 0.015325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1081-8_0_4_line_63 | NAYY 4x150 SE | 59 | 60 | 0.0069662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1081-8_0_4_line_64 | NAYY 4x150 SE | 60 | 61 | 0.022104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1081-8_0_4_line_65 | NAYY 4x150 SE | 62 | 63 | 0.089937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1081-8_0_4_line_66 | NAYY 4x150 SE | 62 | 64 | 0.0072515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1081-8_0_4_line_67 | NAYY 4x150 SE | 63 | 65 | 0.017217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1081-8_0_4_line_68 | NAYY 4x150 SE | 64 | 66 | 0.1237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1081-8_0_4_line_69 | NAYY 4x150 SE | 65 | 67 | 0.013175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1081-8_0_4_line_70 | NAYY 4x150 SE | 65 | 68 | 0.039446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1081-8_0_4_line_71 | NAYY 4x150 SE | 68 | 69 | 0.13843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1081-8_0_4_line_72 | NAYY 4x150 SE | 69 | 84 | 0.029853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1081-8_0_4_line_73 | NAYY 4x150 SE | 70 | 87 | 0.038156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1081-8_0_4_line_74 | NAYY 4x150 SE | 71 | 72 | 0.0059314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1081-8_0_4_line_75 | NAYY 4x150 SE | 72 | 74 | 0.042823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1081-8_0_4_line_76 | NAYY 4x150 SE | 73 | 75 | 0.0032608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1081-8_0_4_line_77 | NAYY 4x150 SE | 75 | 76 | 0.025089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1081-8_0_4_line_78 | NAYY 4x150 SE | 76 | 82 | 0.0078959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1081-8_0_4_line_79 | NAYY 4x150 SE | 76 | 81 | 0.01354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1081-8_0_4_line_80 | NAYY 4x150 SE | 77 | 78 | 0.00026768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1081-8_0_4_line_81 | NAYY 4x150 SE | 77 | 79 | 0.0082138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1081-8_0_4_line_82 | NAYY 4x150 SE | 79 | 80 | 0.0056107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1081-8_0_4_line_83 | NAYY 4x150 SE | 80 | 81 | 0.023387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1081-8_0_4_line_84 | NAYY 4x150 SE | 82 | 83 | 0.017084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1081-8_0_4_line_85 | NAYY 4x150 SE | 83 | 87 | 0.037803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1081-8_0_4_line_86 | NAYY 4x150 SE | 84 | 85 | 0.007789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1081-8_0_4_line_87 | NAYY 4x150 SE | 85 | 86 | 0.044156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1081-8_0_4_line_88 | NAYY 4x150 SE | 88 | 89 | 0.013794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1081-8_0_4_line_89 | NAYY 4x150 SE | 88 | 90 | 0.058222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1081-8_0_4_line_90 | NAYY 4x150 SE | 89 | 91 | 0.022984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1081-8_0_4_line_91 | NAYY 4x150 SE | 90 | 92 | 0.026913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
92 | LV_1081-8_0_4_line_92 | NAYY 4x150 SE | 90 | 93 | 0.057459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
93 | LV_1081-8_0_4_line_93 | NAYY 4x150 SE | 91 | 94 | 0.008719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1081-8_0_4_line_94 | NAYY 4x150 SE | 91 | 95 | 0.019671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1081-8_0_4_line_95 | NAYY 4x150 SE | 92 | 96 | 0.021822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_1081-8_0_4_line_96 | NAYY 4x150 SE | 93 | 97 | 0.025333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_1081-8_0_4_line_97 | NAYY 4x150 SE | 94 | 98 | 0.021503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1081-8_0_4_line_98 | NAYY 4x150 SE | 95 | 99 | 0.012912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1081-8_0_4_line_99 | NAYY 4x150 SE | 96 | 100 | 0.24865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_1081-8_0_4_line_100 | NAYY 4x150 SE | 97 | 101 | 0.027053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
101 | LV_1081-8_0_4_line_101 | NAYY 4x150 SE | 98 | 128 | 0.0072893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1081-8_0_4_line_102 | NAYY 4x150 SE | 99 | 129 | 0.045442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1081-8_0_4_line_103 | NAYY 4x150 SE | 101 | 115 | 0.039404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1081-8_0_4_line_104 | NAYY 4x150 SE | 102 | 103 | 7.5429e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1081-8_0_4_line_105 | NAYY 4x150 SE | 102 | 104 | 0.024154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1081-8_0_4_line_106 | NAYY 4x150 SE | 103 | 105 | 0.027544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1081-8_0_4_line_107 | NAYY 4x150 SE | 104 | 106 | 0.027485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1081-8_0_4_line_108 | NAYY 4x150 SE | 104 | 107 | 0.023719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1081-8_0_4_line_109 | NAYY 4x150 SE | 105 | 108 | 0.0037427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1081-8_0_4_line_110 | NAYY 4x150 SE | 106 | 109 | 0.021873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1081-8_0_4_line_111 | NAYY 4x150 SE | 107 | 110 | 0.015816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1081-8_0_4_line_112 | NAYY 4x150 SE | 108 | 111 | 0.0001135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1081-8_0_4_line_113 | NAYY 4x150 SE | 109 | 112 | 0.0020505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1081-8_0_4_line_114 | NAYY 4x150 SE | 110 | 113 | 0.0074332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1081-8_0_4_line_115 | NAYY 4x150 SE | 110 | 114 | 0.022022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1081-8_0_4_line_116 | NAYY 4x150 SE | 112 | 124 | 0.012465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1081-8_0_4_line_117 | NAYY 4x150 SE | 113 | 116 | 0.032429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1081-8_0_4_line_118 | NAYY 4x150 SE | 114 | 115 | 0.02433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1081-8_0_4_line_119 | NAYY 4x150 SE | 116 | 117 | 0.020239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1081-8_0_4_line_120 | NAYY 4x150 SE | 117 | 118 | 0.015153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1081-8_0_4_line_121 | NAYY 4x150 SE | 119 | 120 | 0.01579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_1081-8_0_4_line_122 | NAYY 4x150 SE | 119 | 121 | 0.015803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_1081-8_0_4_line_123 | NAYY 4x150 SE | 120 | 122 | 5.6654e-06 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_1081-8_0_4_line_124 | NAYY 4x150 SE | 121 | 123 | 1.5406e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_1081-8_0_4_line_125 | NAYY 4x150 SE | 122 | 124 | 0.010967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_1081-8_0_4_line_126 | NAYY 4x150 SE | 125 | 126 | 0.016439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_1081-8_0_4_line_127 | NAYY 4x150 SE | 125 | 127 | 0.037908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_1081-8_0_4_line_128 | NAYY 4x150 SE | 126 | 132 | 0.0077711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_1081-8_0_4_line_129 | NAYY 4x150 SE | 127 | 135 | 0.0027118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_1081-8_0_4_line_130 | NAYY 4x150 SE | 128 | 136 | 0.0064967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_1081-8_0_4_line_131 | NAYY 4x150 SE | 130 | 131 | 0.028492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_1081-8_0_4_line_132 | NAYY 4x150 SE | 130 | 132 | 0.012091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_1081-8_0_4_line_133 | NAYY 4x150 SE | 132 | 133 | 0.037486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_1081-8_0_4_line_134 | NAYY 4x150 SE | 134 | 135 | 0.017512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_1081-8_0_4_line_135 | NAYY 4x150 SE | 134 | 136 | 0.0066064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1081-8_0_4_trafo_103 | 0.25 MVA 20/0.4 kV | 137 | 101 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2658618.9432 | 1230047.7737 | 2658620.9635 | 1230051.2783 | 2658626.9164 | 1230063.3741
1 | 2658609.9857 | 1230032.2357 | 2658609.9857 | 1230032.2357 | 2658618.9432 | 1230047.7737
2 | 2658626.9164 | 1230063.3741 | 2658627.2758 | 1230064.1043 | 2658630.9374 | 1230076.766
3 | 2658609.9857 | 1230032.2357 | 2658607.9946 | 1230022.1318 | 2658609.6315 | 1230000.5451 | 2658609.7591 | 1229998.7864
4 | 2658501.9176 | 1230190.6742 | 2658630.9374 | 1230076.766
5 | 2658480.248 | 1230202.7059 | 2658487.2485 | 1230201.5478 | 2658499.7258 | 1230192.1533 | 2658501.9176 | 1230190.6742
6 | 2658429.4145 | 1230201.5796 | 2658447.3017 | 1230202.8116 | 2658472.6584 | 1230203.9615 | 2658480.248 | 1230202.7059
7 | 2658036.8523 | 1229767.5476 | 2658374.8787 | 1230205.9248
8 | 2658036.8523 | 1229767.5476 | 2658032.712 | 1229765.6386
9 | 2658382.3521 | 1230203.908 | 2658374.8787 | 1230205.9248
10 | 2658374.8787 | 1230205.9248 | 2658377.6482 | 1230222.4181 | 2658380.3299 | 1230232.7946
11 | 2658019.0297 | 1229759.3301 | 2658032.712 | 1229765.6386
12 | 2658429.4145 | 1230201.5796 | 2658414.1906 | 1230201.43
13 | 2658424.1727 | 1230243.9887 | 2658426.1795 | 1230224.7627 | 2658429.4145 | 1230201.5796
14 | 2658414.1906 | 1230201.43 | 2658394.434 | 1230202.3056
15 | 2658424.1727 | 1230243.9887 | 2658417.5239 | 1230244.5682 | 2658408.3971 | 1230246.8636
16 | 2658382.3521 | 1230203.908 | 2658387.0838 | 1230202.6313 | 2658394.434 | 1230202.3056
17 | 2658382.1508 | 1230239.8402 | 2658380.3299 | 1230232.7946
18 | 2658608.6105 | 1228931.9718 | 2658609.5799 | 1228936.6288 | 2658612.5404 | 1228940.9625
19 | 2658608.6105 | 1228931.9718 | 2658605.7954 | 1228918.5689 | 2658603.8967 | 1228912.4336
20 | 2658561.5208 | 1228945.2723 | 2658560.4258 | 1228934.9105 | 2658572.0042 | 1228934.7465 | 2658579.5229 | 1228935.2208 | 2658587.5526 | 1228934.5884 | 2658600.4719 | 1228932.8923 | 2658608.6105 | 1228931.9718
21 | 2658601.7921 | 1228905.6327 | 2658603.8967 | 1228912.4336
22 | 2658561.5208 | 1228945.2723 | 2658562.8169 | 1228957.5262 | 2658570.1448 | 1228994.0053
23 | 2658561.5208 | 1228945.2723 | 2658549.065 | 1228942.2145 | 2658545.0364 | 1228938.9283 | 2658524.3694 | 1228892.3616
24 | 2658577.4444 | 1229020.5918 | 2658570.1548 | 1228994.0552 | 2658570.1448 | 1228994.0053
25 | 2658572.4805 | 1229052.5377 | 2658576.4083 | 1229046.05 | 2658578.6984 | 1229039.6907 | 2658579.2901 | 1229027.3108 | 2658577.4444 | 1229020.5918
26 | 2658572.4805 | 1229052.5377 | 2658560.6093 | 1229057.0683 | 2658550.7573 | 1229058.8947 | 2658538.123 | 1229055.5238 | 2658514.1698 | 1229039.0554 | 2658507.7335 | 1229036.5053
27 | 2658583.5182 | 1229069.5573 | 2658581.972 | 1229065.0058 | 2658577.3859 | 1229058.3342 | 2658572.4805 | 1229052.5377
28 | 2657909.6582 | 1229645.0094 | 2657908.6191 | 1229644.9516
29 | 2657909.6582 | 1229645.0094 | 2657940.8218 | 1229646.7445
30 | 2657900.8801 | 1229644.5207 | 2657908.6191 | 1229644.9516
31 | 2657960.4476 | 1229647.8372 | 2657940.8218 | 1229646.7445
32 | 2657900.8801 | 1229644.5207 | 2657893.8517 | 1229644.1294
33 | 2657960.4476 | 1229647.8372 | 2657955.3157 | 1229636.5133 | 2657944.8164 | 1229604.6017 | 2657941.7571 | 1229598.6712
34 | 2657968.8786 | 1229658.7708 | 2657960.4476 | 1229647.8372
35 | 2657999.6829 | 1229083.7361 | 2658013.2311 | 1229092.0846 | 2658043.9239 | 1229107.4493 | 2658082.8704 | 1229122.4729
36 | 2658082.8704 | 1229122.4729 | 2658026.6344 | 1229552.2544
37 | 2658374.9407 | 1228981.5961 | 2658082.8704 | 1229122.4729
38 | 2657999.6829 | 1229083.7361 | 2657998.1338 | 1229077.884 | 2658000.2951 | 1229069.911 | 2658007.9388 | 1229059.112
39 | 2658026.6344 | 1229552.2544 | 2658019.113 | 1229564.2979
40 | 2658387.3613 | 1228994.4815 | 2658374.9407 | 1228981.5961
41 | 2658353.9347 | 1228943.1652 | 2658357.33 | 1228952.1152 | 2658365.2704 | 1228967.514 | 2658369.7686 | 1228976.2304 | 2658374.9407 | 1228981.5961
42 | 2657875.196 | 1229643.0907 | 2657893.8517 | 1229644.1294
43 | 2657926.3778 | 1229569.4791 | 2657932.9127 | 1229581.5266 | 2657941.7571 | 1229598.6712
44 | 2657968.8786 | 1229658.7708 | 2657981.3393 | 1229633.3764
45 | 2657968.8786 | 1229658.7708 | 2657969.0943 | 1229670.0579 | 2657969.6854 | 1229686.0488
46 | 2657875.196 | 1229643.0907 | 2657848.8754 | 1229641.6252 | 2657848.8754 | 1229641.6252
47 | 2657926.3778 | 1229569.4791 | 2657920.8631 | 1229559.3125
48 | 2657981.3393 | 1229633.3764 | 2657996.5095 | 1229602.4601
49 | 2657969.6985 | 1229686.4048 | 2657969.6854 | 1229686.0488
50 | 2657836.1529 | 1229662.0075 | 2657818.0407 | 1229714.3277 | 2657808.6307 | 1229724.5984 | 2657798.1075 | 1229726.2527 | 2657791.8153 | 1229723.969
51 | 2657836.1529 | 1229662.0075 | 2657840.9953 | 1229648.0194 | 2657840.9953 | 1229648.0194
52 | 2657791.8153 | 1229723.969 | 2657789.3887 | 1229723.0883 | 2657742.5178 | 1229703.0762
53 | 2657848.8754 | 1229641.6252 | 2657840.9953 | 1229648.0194
54 | 2657672.6892 | 1229673.2622 | 2657742.5178 | 1229703.0762
55 | 2657626.042 | 1229686.2634 | 2657639.5313 | 1229671.5906 | 2657647.2974 | 1229667.5521 | 2657658.3691 | 1229667.148 | 2657672.6892 | 1229673.2622
56 | 2658025.359 | 1228801.8395 | 2658007.9388 | 1229059.112
57 | 2657971.8218 | 1229743.8429 | 2658010.6157 | 1229755.4506 | 2658019.0297 | 1229759.3301
58 | 2657971.8218 | 1229743.8429 | 2657970.3327 | 1229703.5594
59 | 2657969.6985 | 1229686.4048 | 2657970.3327 | 1229703.5594
60 | 2657911.0658 | 1229540.9193 | 2657914.3777 | 1229547.8245 | 2657919.6288 | 1229557.0371 | 2657920.8631 | 1229559.3125
61 | 2657911.0658 | 1229540.9193 | 2657903.0988 | 1229524.3085
62 | 2658010.9956 | 1229577.296 | 2658019.113 | 1229564.2979
63 | 2658007.3056 | 1229583.2046 | 2658010.9956 | 1229577.296
64 | 2658007.3056 | 1229583.2046 | 2658001.0163 | 1229593.2753 | 2657996.5095 | 1229602.4601
65 | 2658688.544 | 1229070.8746 | 2658695.7049 | 1229109.7219 | 2658697.4389 | 1229135.9225 | 2658690.4384 | 1229152.0526 | 2658687.851 | 1229158.1178
66 | 2658687.2294 | 1229063.7432 | 2658688.544 | 1229070.8746
67 | 2658683.0946 | 1229174.5724 | 2658685.087 | 1229164.5968 | 2658687.851 | 1229158.1178
68 | 2658583.5182 | 1229069.5573 | 2658597.4596 | 1229066.3703 | 2658666.9607 | 1229039.8492 | 2658677.4871 | 1229041.8543 | 2658682.8534 | 1229049.3009 | 2658686.759 | 1229061.1915 | 2658687.2294 | 1229063.7432
69 | 2658683.0946 | 1229174.5724 | 2658688.2201 | 1229174.9232 | 2658696.0346 | 1229176.8026
70 | 2658683.0946 | 1229174.5724 | 2658678.4132 | 1229192.9269 | 2658686.3949 | 1229204.8021 | 2658687.7433 | 1229210.8488
71 | 2658687.7433 | 1229210.8488 | 2658549.3817 | 1229215.2126
72 | 2658535.0936 | 1229241.3925 | 2658535.1426 | 1229241.3135 | 2658540.361 | 1229233.004 | 2658549.3817 | 1229215.2126
73 | 2658507.7335 | 1229036.5053 | 2658496.012 | 1229031.8612 | 2658484.2615 | 1229027.1983 | 2658471.6821 | 1229024.3128
74 | 2658353.9347 | 1228943.1652 | 2658351.8309 | 1228937.6194
75 | 2658333.8549 | 1228898.8531 | 2658344.9299 | 1228919.4282 | 2658351.8309 | 1228937.6194
76 | 2658387.3613 | 1228994.4815 | 2658389.6243 | 1228996.8292
77 | 2658410.4727 | 1229010.5518 | 2658392.6735 | 1228999.9925 | 2658389.6243 | 1228996.8292
78 | 2658410.4727 | 1229010.5518 | 2658417.6358 | 1229012.5122 | 2658418.0884 | 1229012.6366
79 | 2658410.4727 | 1229010.5518 | 2658407.8342 | 1229023.8327
80 | 2658401.4741 | 1229060.458 | 2658401.451 | 1229060.7247
81 | 2658401.4741 | 1229060.458 | 2658402.1836 | 1229052.2749
82 | 2658403.2769 | 1229046.7718 | 2658402.1836 | 1229052.2749 | 2658402.1836 | 1229052.2749
83 | 2658403.2769 | 1229046.7718 | 2658407.8342 | 1229023.8327
84 | 2658434.6596 | 1229016.729 | 2658429.9746 | 1229015.9022 | 2658418.0884 | 1229012.6366
85 | 2658434.6596 | 1229016.729 | 2658437.0462 | 1229017.1502 | 2658452.1044 | 1229019.822 | 2658471.6821 | 1229024.3128
86 | 2658535.0936 | 1229241.3925 | 2658531.4475 | 1229247.2699 | 2658530.9644 | 1229247.9964
87 | 2658499.3199 | 1229278.2786 | 2658505.5564 | 1229273.8434 | 2658525.2341 | 1229256.6147 | 2658530.9644 | 1229247.9964
88 | 2657929.551 | 1228498.4662 | 2657917.0302 | 1228492.6779
89 | 2657981.5646 | 1228524.569 | 2657954 | 1228509.7688 | 2657929.551 | 1228498.4662
90 | 2657896.1677 | 1228483.0333 | 2657917.0302 | 1228492.6779
91 | 2657981.5646 | 1228524.569 | 2658003.7366 | 1228539.917
92 | 2657981.5646 | 1228524.569 | 2657974.9799 | 1228534.7113 | 2657968.5467 | 1228542.5203 | 2657959.8986 | 1228548.2619 | 2657935.8885 | 1228554.7389
93 | 2657896.1677 | 1228483.0333 | 2657888.1937 | 1228479.4534
94 | 2657896.1677 | 1228483.0333 | 2657904.4959 | 1228465.2118
95 | 2658003.7366 | 1228539.917 | 2658011.8212 | 1228546.122 | 2658021.0791 | 1228553.2279
96 | 2657935.8885 | 1228554.7389 | 2657922.5068 | 1228558.3488 | 2657911.5741 | 1228561.8271
97 | 2657888.1937 | 1228479.4534 | 2657879.0116 | 1228498.8972
98 | 2657912.8453 | 1228455.7337 | 2657909.0864 | 1228458.1431 | 2657905.1673 | 1228463.7752 | 2657904.4959 | 1228465.2118
99 | 2658021.0791 | 1228553.2279 | 2658025.359 | 1228801.8395
100 | 2657911.5741 | 1228561.8271 | 2657890.091 | 1228568.6621 | 2657885.658 | 1228569.4851
101 | 2657879.0116 | 1228498.8972 | 2657878.5928 | 1228499.7841 | 2657876.7413 | 1228502.4011 | 2657874.0814 | 1228503.9985 | 2657874.0814 | 1228503.9985
102 | 2657912.8453 | 1228455.7337 | 2657907.1085 | 1228447.2725 | 2657877.315 | 1228438.7772 | 2657873.265 | 1228437.5283
103 | 2657846.7592 | 1228569.4777 | 2657851.2323 | 1228570.6745 | 2657869.9455 | 1228572.4019 | 2657885.658 | 1228569.4851
104 | 2657769.8851 | 1228573.7988 | 2657769.9543 | 1228573.8288
105 | 2657792.1225 | 1228583.4194 | 2657769.9543 | 1228573.8288
106 | 2657769.8851 | 1228573.7988 | 2657744.6054 | 1228562.8621
107 | 2657792.1225 | 1228583.4194 | 2657781.4678 | 1228608.7552
108 | 2657792.1225 | 1228583.4194 | 2657801.3536 | 1228561.5704
109 | 2657744.6054 | 1228562.8621 | 2657741.1704 | 1228561.376
110 | 2657781.4678 | 1228608.7552 | 2657772.9884 | 1228628.9182
111 | 2657807.509 | 1228547.0011 | 2657801.3536 | 1228561.5704
112 | 2657741.0663 | 1228561.3309 | 2657741.1704 | 1228561.376
113 | 2657771.1604 | 1228629.847 | 2657772.9884 | 1228628.9182 | 2657772.9884 | 1228628.9182
114 | 2657807.509 | 1228547.0011 | 2657803.0327 | 1228541.0669
115 | 2657807.509 | 1228547.0011 | 2657818.1854 | 1228557.8562 | 2657824.0482 | 1228561.2936
116 | 2657759.4714 | 1228626.6943 | 2657767.9972 | 1228630.2817 | 2657770.8412 | 1228630.0092 | 2657771.1604 | 1228629.847
117 | 2657783.5042 | 1228515.1773 | 2657803.0327 | 1228541.0669
118 | 2657846.7592 | 1228569.4777 | 2657830.6616 | 1228565.171 | 2657824.0482 | 1228561.2936
119 | 2657783.5042 | 1228515.1773 | 2657783.4141 | 1228515.0579 | 2657774.8116 | 1228507.5362 | 2657767.6091 | 1228502.7238
120 | 2657754.6205 | 1228494.9472 | 2657762.2321 | 1228499.131 | 2657767.6091 | 1228502.7238
121 | 2657734.8041 | 1228616.3149 | 2657749.358 | 1228622.4388
122 | 2657720.2377 | 1228610.1857 | 2657734.8041 | 1228616.3149
123 | 2657749.358 | 1228622.4388 | 2657749.3632 | 1228622.441
124 | 2657720.2235 | 1228610.1797 | 2657720.2377 | 1228610.1857
125 | 2657759.4714 | 1228626.6943 | 2657749.3632 | 1228622.441
126 | 2657844.9964 | 1228460.0655 | 2657829.9975 | 1228453.3365
127 | 2657844.9964 | 1228460.0655 | 2657835.8863 | 1228482.1466 | 2657835.8468 | 1228486.2043 | 2657837.7334 | 1228489.3247 | 2657840.4761 | 1228490.9079 | 2657843.3612 | 1228492.1733
128 | 2657822.9072 | 1228450.1556 | 2657829.9975 | 1228453.3365
129 | 2657845.8446 | 1228493.2625 | 2657843.3612 | 1228492.1733
130 | 2657867.9318 | 1228502.9497 | 2657871.3267 | 1228504.4387 | 2657874.0814 | 1228503.9985
131 | 2657812.1421 | 1228444.6513 | 2657790.4343 | 1228433.5518 | 2657787.3076 | 1228430.8826
132 | 2657822.9072 | 1228450.1556 | 2657812.1421 | 1228444.6513
133 | 2657822.9072 | 1228450.1556 | 2657829.6555 | 1228437.2018 | 2657834.435 | 1228428.0202 | 2657842.0717 | 1228418.0878
134 | 2657861.8817 | 1228500.2962 | 2657845.8446 | 1228493.2625
135 | 2657861.8817 | 1228500.2962 | 2657867.9318 | 1228502.9497

## bus_geodata
| x | y | coords
0 | 2658618.9432 | 1230047.7737
1 | 2658626.9164 | 1230063.3741
2 | 2658609.9857 | 1230032.2357
3 | 2658630.9374 | 1230076.766
4 | 2658609.7591 | 1229998.7864
5 | 2658501.9176 | 1230190.6742
6 | 2658480.248 | 1230202.7059
7 | 2658036.8523 | 1229767.5476
8 | 2658374.8787 | 1230205.9248
9 | 2658032.712 | 1229765.6386
10 | 2658429.4145 | 1230201.5796
11 | 2658414.1906 | 1230201.43
12 | 2658424.1727 | 1230243.9887
13 | 2658394.434 | 1230202.3056
14 | 2658408.3971 | 1230246.8636
15 | 2658382.3521 | 1230203.908
16 | 2658380.3299 | 1230232.7946
17 | 2658382.1508 | 1230239.8402
18 | 2658612.5404 | 1228940.9625
19 | 2658608.6105 | 1228931.9718
20 | 2658603.8967 | 1228912.4336
21 | 2658561.5208 | 1228945.2723
22 | 2658601.7921 | 1228905.6327
23 | 2658570.1448 | 1228994.0053
24 | 2658524.3694 | 1228892.3616
25 | 2658577.4444 | 1229020.5918
26 | 2658572.4805 | 1229052.5377
27 | 2657909.6582 | 1229645.0094
28 | 2657908.6191 | 1229644.9516
29 | 2657940.8218 | 1229646.7445
30 | 2657900.8801 | 1229644.5207
31 | 2657960.4476 | 1229647.8372
32 | 2658082.8704 | 1229122.4729
33 | 2657999.6829 | 1229083.7361
34 | 2658026.6344 | 1229552.2544
35 | 2658374.9407 | 1228981.5961
36 | 2657893.8517 | 1229644.1294
37 | 2657941.7571 | 1229598.6712
38 | 2657968.8786 | 1229658.7708
39 | 2657875.196 | 1229643.0907
40 | 2657926.3778 | 1229569.4791
41 | 2657981.3393 | 1229633.3764
42 | 2657969.6854 | 1229686.0488
43 | 2657836.1529 | 1229662.0075
44 | 2657791.8153 | 1229723.969
45 | 2657840.9953 | 1229648.0194
46 | 2657742.5178 | 1229703.0762
47 | 2657848.8754 | 1229641.6252
48 | 2657672.6892 | 1229673.2622
49 | 2657626.042 | 1229686.2634
50 | 2658007.9388 | 1229059.112
51 | 2658019.0297 | 1229759.3301
52 | 2657971.8218 | 1229743.8429
53 | 2657970.3327 | 1229703.5594
54 | 2657969.6985 | 1229686.4048
55 | 2657920.8631 | 1229559.3125
56 | 2657911.0658 | 1229540.9193
57 | 2657903.0988 | 1229524.3085
58 | 2658019.113 | 1229564.2979
59 | 2658010.9956 | 1229577.296
60 | 2658007.3056 | 1229583.2046
61 | 2657996.5095 | 1229602.4601
62 | 2658688.544 | 1229070.8746
63 | 2658687.851 | 1229158.1178
64 | 2658687.2294 | 1229063.7432
65 | 2658683.0946 | 1229174.5724
66 | 2658583.5182 | 1229069.5573
67 | 2658696.0346 | 1229176.8026
68 | 2658687.7433 | 1229210.8488
69 | 2658549.3817 | 1229215.2126
70 | 2658507.7335 | 1229036.5053
71 | 2658353.9347 | 1228943.1652
72 | 2658351.8309 | 1228937.6194
73 | 2658387.3613 | 1228994.4815
74 | 2658333.8549 | 1228898.8531
75 | 2658389.6243 | 1228996.8292
76 | 2658410.4727 | 1229010.5518
77 | 2658401.4741 | 1229060.458
78 | 2658401.451 | 1229060.7247
79 | 2658402.1836 | 1229052.2749
80 | 2658403.2769 | 1229046.7718
81 | 2658407.8342 | 1229023.8327
82 | 2658418.0884 | 1229012.6366
83 | 2658434.6596 | 1229016.729
84 | 2658535.0936 | 1229241.3925
85 | 2658530.9644 | 1229247.9964
86 | 2658499.3199 | 1229278.2786
87 | 2658471.6821 | 1229024.3128
88 | 2657929.551 | 1228498.4662
89 | 2657917.0302 | 1228492.6779
90 | 2657981.5646 | 1228524.569
91 | 2657896.1677 | 1228483.0333
92 | 2658003.7366 | 1228539.917
93 | 2657935.8885 | 1228554.7389
94 | 2657888.1937 | 1228479.4534
95 | 2657904.4959 | 1228465.2118
96 | 2658021.0791 | 1228553.2279
97 | 2657911.5741 | 1228561.8271
98 | 2657879.0116 | 1228498.8972
99 | 2657912.8453 | 1228455.7337
100 | 2658025.359 | 1228801.8395
101 | 2657885.658 | 1228569.4851
102 | 2657769.9543 | 1228573.8288
103 | 2657769.8851 | 1228573.7988
104 | 2657792.1225 | 1228583.4194
105 | 2657744.6054 | 1228562.8621
106 | 2657781.4678 | 1228608.7552
107 | 2657801.3536 | 1228561.5704
108 | 2657741.1704 | 1228561.376
109 | 2657772.9884 | 1228628.9182
110 | 2657807.509 | 1228547.0011
111 | 2657741.0663 | 1228561.3309
112 | 2657771.1604 | 1228629.847
113 | 2657803.0327 | 1228541.0669
114 | 2657824.0482 | 1228561.2936
115 | 2657846.7592 | 1228569.4777
116 | 2657783.5042 | 1228515.1773
117 | 2657767.6091 | 1228502.7238
118 | 2657754.6205 | 1228494.9472
119 | 2657734.8041 | 1228616.3149
120 | 2657749.358 | 1228622.4388
121 | 2657720.2377 | 1228610.1857
122 | 2657749.3632 | 1228622.441
123 | 2657720.2235 | 1228610.1797
124 | 2657759.4714 | 1228626.6943
125 | 2657844.9964 | 1228460.0655
126 | 2657829.9975 | 1228453.3365
127 | 2657843.3612 | 1228492.1733
128 | 2657874.0814 | 1228503.9985
129 | 2657873.265 | 1228437.5283
130 | 2657812.1421 | 1228444.6513
131 | 2657787.3076 | 1228430.8826
132 | 2657822.9072 | 1228450.1556
133 | 2657842.0717 | 1228418.0878
134 | 2657861.8817 | 1228500.2962
135 | 2657845.8446 | 1228493.2625
136 | 2657867.9318 | 1228502.9497
137 | 2657807.509 | 1228547.0011

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97115 | -0.20592 | 0.0010893 | 0.000273
1 | 0.97121 | -0.20553 | 0.00039862 | 9.9904e-05
2 | 0.97113 | -0.20612 | 0.00062333 | 0.00015622
3 | 0.97126 | -0.20516 | 0.00080557 | 0.00020189
4 | 0.97111 | -0.20626 | 0.00038853 | 9.7375e-05
5 | 0.97209 | -0.19912 | 0.0001674 | 4.1954e-05
6 | 0.97222 | -0.19818 | 0.00058696 | 0.0001471
7 | 0.97709 | -0.16289 | 4.2054e-05 | 1.054e-05
8 | 0.97287 | -0.19352 | 0 | 0
9 | 0.97712 | -0.16264 | 9.7892e-05 | 2.4534e-05
10 | 0.97253 | -0.19598 | 0 | 0
11 | 0.97262 | -0.19531 | 0 | 0
12 | 0.97252 | -0.19603 | 0 | 0
13 | 0.97274 | -0.19444 | 0.00015651 | 3.9225e-05
14 | 0.97252 | -0.19604 | 9.0589e-05 | 2.2704e-05
15 | 0.97282 | -0.19388 | 0 | 0
16 | 0.97283 | -0.19378 | 0.000349 | 8.7468e-05
17 | 0.97282 | -0.19382 | 0.00054418 | 0.00013638
18 | 0.97629 | -0.1684 | 0.00038785 | 9.7205e-05
19 | 0.97629 | -0.16836 | 0 | 0
20 | 0.97627 | -0.16853 | 0.00014318 | 3.5883e-05
21 | 0.9764 | -0.16761 | 0 | 0
22 | 0.97626 | -0.16858 | 0.00066883 | 0.00016762
23 | 0.97649 | -0.16691 | 0.00018031 | 4.5191e-05
24 | 0.97638 | -0.16772 | 0.00014263 | 3.5748e-05
25 | 0.97656 | -0.16646 | 0.00045045 | 0.00011289
26 | 0.97665 | -0.16576 | 0 | 0
27 | 0.9781 | -0.15557 | 0.00035282 | 8.8426e-05
28 | 0.97809 | -0.1556 | 0.00016485 | 4.1315e-05
29 | 0.97821 | -0.15474 | 0.00017545 | 4.3972e-05
30 | 0.97807 | -0.15576 | 6.6159e-05 | 1.6581e-05
31 | 0.97829 | -0.15419 | 0 | 0
32 | 0.98474 | -0.10765 | 0.0011114 | 0.00027855
33 | 0.98594 | -0.099121 | 0 | 0
34 | 0.98035 | -0.13925 | 0.00034464 | 8.6375e-05
35 | 0.97923 | -0.14715 | 0.00032516 | 8.1494e-05
36 | 0.97805 | -0.1559 | 0.00010665 | 2.6728e-05
37 | 0.97821 | -0.15472 | 7.9274e-05 | 1.9868e-05
38 | 0.97836 | -0.15365 | 0 | 0
39 | 0.978 | -0.15626 | 0.00018681 | 4.6818e-05
40 | 0.97817 | -0.15502 | 4.6022e-05 | 1.1534e-05
41 | 0.97877 | -0.15065 | 7.5351e-05 | 1.8885e-05
42 | 0.9781 | -0.15551 | 0.00013435 | 3.3672e-05
43 | 0.97789 | -0.15709 | 0.00038147 | 9.5606e-05
44 | 0.97777 | -0.15798 | 8.3783e-05 | 2.0998e-05
45 | 0.97792 | -0.15688 | 0.00018491 | 4.6343e-05
46 | 0.9777 | -0.15847 | 0.0006273 | 0.00015722
47 | 0.97794 | -0.15672 | 0.00011062 | 2.7724e-05
48 | 0.97767 | -0.15867 | 8.7566e-05 | 2.1946e-05
49 | 0.97766 | -0.15876 | 0.00015506 | 3.8861e-05
50 | 0.98629 | -0.096571 | 0.0029174 | 0.00073118
51 | 0.97724 | -0.16178 | 6.6139e-05 | 1.6576e-05
52 | 0.97763 | -0.15892 | 0 | 0
53 | 0.97795 | -0.1566 | 0.000478 | 0.0001198
54 | 0.9781 | -0.15553 | 0.00037417 | 9.3775e-05
55 | 0.97816 | -0.15513 | 0.00036921 | 9.2533e-05
56 | 0.97814 | -0.15523 | 6.0244e-05 | 1.5098e-05
57 | 0.97813 | -0.15531 | 0.00040472 | 0.00010143
58 | 0.98007 | -0.14127 | 0.00034236 | 8.5803e-05
59 | 0.97978 | -0.1434 | 0.0011171 | 0.00027996
60 | 0.97965 | -0.14429 | 0.00064271 | 0.00016108
61 | 0.97928 | -0.14696 | 0.0013326 | 0.00033398
62 | 0.97545 | -0.17441 | 0.00011205 | 2.8083e-05
63 | 0.97478 | -0.17928 | 7.0474e-05 | 1.7662e-05
64 | 0.97551 | -0.17401 | 0.00017464 | 4.3769e-05
65 | 0.97465 | -0.1802 | 0 | 0
66 | 0.97649 | -0.16693 | 0 | 0
67 | 0.97464 | -0.18025 | 0.00030712 | 7.6971e-05
68 | 0.97438 | -0.18218 | 0.00024807 | 6.2173e-05
69 | 0.97346 | -0.18877 | 0.00060443 | 0.00015148
70 | 0.97743 | -0.16015 | 0.00014996 | 3.7583e-05
71 | 0.97914 | -0.14782 | 0.00068124 | 0.00017074
72 | 0.97913 | -0.14787 | 0.00012973 | 3.2513e-05
73 | 0.97897 | -0.149 | 9.8665e-05 | 2.4728e-05
74 | 0.97909 | -0.14816 | 0.00064641 | 0.00016201
75 | 0.97893 | -0.14934 | 0.00038887 | 9.7459e-05
76 | 0.97858 | -0.15181 | 0 | 0
77 | 0.97851 | -0.15234 | 0.00041112 | 0.00010304
78 | 0.97851 | -0.15234 | 0.00028587 | 7.1646e-05
79 | 0.97852 | -0.15228 | 0.00029147 | 7.305e-05
80 | 0.97853 | -0.15222 | 4.6759e-05 | 1.1719e-05
81 | 0.97856 | -0.15197 | 6.5729e-05 | 1.6473e-05
82 | 0.97849 | -0.1525 | 0.00022103 | 5.5396e-05
83 | 0.97829 | -0.15395 | 0.00012191 | 3.0552e-05
84 | 0.97329 | -0.18999 | 0.00041667 | 0.00010443
85 | 0.97325 | -0.19028 | 0.0020819 | 0.00052177
86 | 0.97316 | -0.19094 | 0.001403 | 0.00035162
87 | 0.97785 | -0.15711 | 0.00038902 | 9.7499e-05
88 | 0.98985 | -0.070814 | 0.00017884 | 4.4821e-05
89 | 0.98865 | -0.079293 | 0.00019697 | 4.9364e-05
90 | 0.99495 | -0.035143 | 0 | 0
91 | 0.98665 | -0.093421 | 0 | 0
92 | 0.9945 | -0.038304 | 0 | 0
93 | 0.99758 | -0.016769 | 0.00038173 | 9.5671e-05
94 | 0.98614 | -0.097007 | 0 | 0
95 | 0.98608 | -0.097451 | 0.0084665 | 0.0021219
96 | 0.99414 | -0.040868 | 0 | 0
97 | 0.99875 | -0.0086659 | 0.00036293 | 9.0959e-05
98 | 0.9849 | -0.10587 | 0.0032613 | 0.00081737
99 | 0.98587 | -0.098976 | 0 | 0
100 | 0.99 | -0.070188 | 0.0047814 | 0.0011983
101 | 1 | 0 | -0.18602 | -0.046688
102 | 0.98634 | -0.095791 | 0.0023387 | 0.00058612
103 | 0.98633 | -0.095807 | 0.0023348 | 0.00058515
104 | 0.98714 | -0.090115 | 0 | 0
105 | 0.98561 | -0.10097 | 0.013448 | 0.0033704
106 | 0.98643 | -0.095104 | 0.001805 | 0.00045238
107 | 0.98853 | -0.080256 | 0.0135 | 0.0033835
108 | 0.98558 | -0.10115 | 0.002399 | 0.00060125
109 | 0.98593 | -0.098674 | 0.0017808 | 0.00044631
110 | 0.98977 | -0.071521 | 0 | 0
111 | 0.98558 | -0.10116 | 0.0024016 | 0.0006019
112 | 0.98589 | -0.098971 | 0.0024087 | 0.00060367
113 | 0.98953 | -0.073213 | 0.0084327 | 0.0021134
114 | 0.9922 | -0.054402 | 0.0048282 | 0.0012101
115 | 0.99505 | -0.034403 | 0.0057253 | 0.0014349
116 | 0.98888 | -0.077813 | 0.0115 | 0.0028822
117 | 0.98881 | -0.07831 | 0.00098501 | 0.00024687
118 | 0.98878 | -0.078529 | 0.0014175 | 0.00035525
119 | 0.98536 | -0.10276 | 0.0025463 | 0.00063817
120 | 0.98552 | -0.10156 | 0.0011694 | 0.00029307
121 | 0.98525 | -0.10354 | 0.0024056 | 0.00060291
122 | 0.98552 | -0.10156 | 0.0011693 | 0.00029305
123 | 0.98525 | -0.10354 | 0.0024058 | 0.00060295
124 | 0.98568 | -0.10047 | 0.0020115 | 0.00050412
125 | 0.98242 | -0.12346 | 0 | 0
126 | 0.98206 | -0.12602 | 0.0041193 | 0.0010324
127 | 0.98325 | -0.11756 | 0.0044371 | 0.001112
128 | 0.98451 | -0.10863 | 0.0044672 | 0.0011196
129 | 0.98511 | -0.10435 | 0.011499 | 0.002882
130 | 0.98182 | -0.12773 | 0.0056424 | 0.0014141
131 | 0.98178 | -0.12802 | 0.00099725 | 0.00024994
132 | 0.98194 | -0.12689 | 0 | 0
133 | 0.98171 | -0.12856 | 0.004288 | 0.0010747
134 | 0.98393 | -0.11275 | 0.0050039 | 0.0012541
135 | 0.98333 | -0.11701 | 0.0041136 | 0.001031
136 | 0.9842 | -0.1108 | 0.0037529 | 0.00094055
137 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0021012 | -0.00052597 | 0.0021013 | 0.0005258 | 1.1334e-07 | -1.7328e-07 | 0.0032192 | 0.0032191 | 0.0032192 | 0.97115 | -0.20592 | 0.97121 | -0.20553 | 1.1923
1 | 0.0010119 | 0.00025297 | -0.0010119 | -0.00025318 | 2.6896e-08 | -2.1157e-07 | 0.0015502 | 0.0015503 | 0.0015503 | 0.97115 | -0.20592 | 0.97113 | -0.20612 | 0.57418
2 | -0.0024999 | -0.0006257 | 0.0025 | 0.00062558 | 1.2809e-07 | -1.2392e-07 | 0.0038299 | 0.0038298 | 0.0038299 | 0.97121 | -0.20553 | 0.97126 | -0.20516 | 1.4185
3 | 0.00038854 | 9.6961e-05 | -0.00038853 | -9.7375e-05 | 7.4536e-09 | -4.1421e-07 | 0.00059519 | 0.00059534 | 0.00059534 | 0.97113 | -0.20612 | 0.97111 | -0.20626 | 0.2205
4 | -0.0033056 | -0.00082747 | 0.0033084 | 0.0008264 | 2.7536e-06 | -1.0728e-06 | 0.005064 | 0.0050632 | 0.005064 | 0.97126 | -0.20516 | 0.97209 | -0.19912 | 1.8755
5 | -0.0034758 | -0.00086835 | 0.0034762 | 0.00086821 | 4.4774e-07 | -1.4221e-07 | 0.0053195 | 0.0053193 | 0.0053195 | 0.97209 | -0.19912 | 0.97222 | -0.19818 | 1.9702
6 | -0.0040632 | -0.0010153 | 0.0040644 | 0.0010152 | 1.2304e-06 | -1.5947e-07 | 0.0062177 | 0.0062175 | 0.0062177 | 0.97222 | -0.19818 | 0.97253 | -0.19598 | 2.3028
7 | 0.005228 | 0.0013012 | -0.0052061 | -0.0012997 | 2.1886e-05 | 1.514e-06 | 0.0079585 | 0.007961 | 0.007961 | 0.97709 | -0.16289 | 0.97287 | -0.19352 | 2.9485
8 | -0.0052701 | -0.0013117 | 0.0052702 | 0.0013117 | 1.831e-07 | 1.3319e-08 | 0.0080226 | 0.0080226 | 0.0080226 | 0.97709 | -0.16289 | 0.97712 | -0.16264 | 2.9713
9 | 0.0043129 | 0.0010762 | -0.0043127 | -0.0010762 | 2.0952e-07 | -1.5269e-08 | 0.006595 | 0.006595 | 0.006595 | 0.97287 | -0.19352 | 0.97282 | -0.19388 | 2.4426
10 | 0.00089322 | 0.00022343 | -0.00089318 | -0.00022376 | 3.1956e-08 | -3.2844e-07 | 0.001366 | 0.0013662 | 0.0013662 | 0.97287 | -0.19352 | 0.97283 | -0.19378 | 0.50598
11 | -0.0053681 | -0.0013363 | 0.0053688 | 0.0013363 | 6.2779e-07 | 5.2713e-08 | 0.0081716 | 0.0081716 | 0.0081716 | 0.97712 | -0.16264 | 0.97724 | -0.16178 | 3.0265
12 | -0.004155 | -0.0010371 | 0.0041554 | 0.0010371 | 3.8264e-07 | -4.1207e-08 | 0.0063558 | 0.0063557 | 0.0063558 | 0.97253 | -0.19598 | 0.97262 | -0.19531 | 2.354
13 | 9.059e-05 | 2.1974e-05 | -9.059e-05 | -2.2504e-05 | 5.1119e-10 | -5.3017e-07 | 0.00013835 | 0.00013854 | 0.00013854 | 0.97253 | -0.19598 | 0.97252 | -0.19603 | 0.05131
14 | -0.0041554 | -0.0010371 | 0.0041559 | 0.001037 | 4.9848e-07 | -5.3741e-08 | 0.0063557 | 0.0063557 | 0.0063557 | 0.97262 | -0.19531 | 0.97274 | -0.19444 | 2.354
15 | 9.059e-05 | 2.2504e-05 | -9.0589e-05 | -2.2704e-05 | 1.9273e-10 | -1.9951e-07 | 0.00013854 | 0.00013861 | 0.00013861 | 0.97252 | -0.19603 | 0.97252 | -0.19604 | 0.051336
16 | -0.0043124 | -0.0010763 | 0.0043127 | 0.0010762 | 3.327e-07 | -2.4223e-08 | 0.0065951 | 0.006595 | 0.0065951 | 0.97274 | -0.19444 | 0.97282 | -0.19388 | 2.4426
17 | 0.00054418 | 0.00013629 | -0.00054418 | -0.00013638 | 3.146e-09 | -8.9142e-08 | 0.00083233 | 0.00083237 | 0.00083237 | 0.97283 | -0.19378 | 0.97282 | -0.19382 | 0.30828
18 | -0.00038785 | -9.7205e-05 | 0.00038785 | 9.708e-05 | 2.1816e-09 | -1.2427e-07 | 0.00059115 | 0.0005911 | 0.00059115 | 0.97629 | -0.1684 | 0.97629 | -0.16836 | 0.21894
19 | 0.00081203 | 0.00020318 | -0.00081201 | -0.00020342 | 1.9227e-08 | -2.4416e-07 | 0.0012375 | 0.0012376 | 0.0012376 | 0.97629 | -0.16836 | 0.97627 | -0.16853 | 0.45838
20 | -0.0011999 | -0.00030026 | 0.0012 | 0.00029957 | 1.2269e-07 | -6.8826e-07 | 0.0018286 | 0.0018284 | 0.0018286 | 0.97629 | -0.16836 | 0.9764 | -0.16761 | 0.67727
21 | 0.00066883 | 0.00016754 | -0.00066883 | -0.00016762 | 4.6165e-09 | -8.7242e-08 | 0.0010194 | 0.0010194 | 0.0010194 | 0.97627 | -0.16853 | 0.97626 | -0.16858 | 0.37757
22 | -0.0013426 | -0.00033445 | 0.0013428 | 0.00033388 | 1.2929e-07 | -5.6982e-07 | 0.0020454 | 0.0020452 | 0.0020454 | 0.9764 | -0.16761 | 0.97649 | -0.16691 | 0.75757
23 | 0.00014264 | 3.4886e-05 | -0.00014263 | -3.5748e-05 | 2.0308e-09 | -8.6185e-07 | 0.00021707 | 0.00021738 | 0.00021738 | 0.9764 | -0.16761 | 0.97638 | -0.16772 | 0.08051
24 | -0.0015231 | -0.00037907 | 0.0015232 | 0.00037877 | 9.2592e-08 | -3.0931e-07 | 0.00232 | 0.0023199 | 0.00232 | 0.97649 | -0.16691 | 0.97656 | -0.16646 | 0.85925
25 | -0.0019736 | -0.00049166 | 0.0019738 | 0.00049131 | 1.9006e-07 | -3.4864e-07 | 0.0030062 | 0.0030061 | 0.0030062 | 0.97656 | -0.16646 | 0.97665 | -0.16576 | 1.1134
26 | -0.007409 | -0.0018491 | 0.0074147 | 0.0018504 | 5.7056e-06 | 1.2953e-06 | 0.011286 | 0.011285 | 0.011286 | 0.97665 | -0.16576 | 0.97743 | -0.16015 | 4.1798
27 | 0.0054352 | 0.0013578 | -0.0054343 | -0.0013578 | 8.7604e-07 | 8.0698e-08 | 0.0082795 | 0.0082796 | 0.0082796 | 0.97665 | -0.16576 | 0.97649 | -0.16693 | 3.0665
28 | 0.0021557 | 0.00053586 | -0.0021557 | -0.00053587 | 6.978e-09 | -1.0378e-08 | 0.003278 | 0.003278 | 0.003278 | 0.9781 | -0.15557 | 0.97809 | -0.1556 | 1.2141
29 | -0.0025085 | -0.00062429 | 0.0025088 | 0.000624 | 2.8341e-07 | -2.8278e-07 | 0.0038147 | 0.0038146 | 0.0038147 | 0.9781 | -0.15557 | 0.97821 | -0.15474 | 1.4129
30 | 0.0019908 | 0.00049455 | -0.0019908 | -0.00049463 | 4.4323e-08 | -8.0232e-08 | 0.0030272 | 0.0030272 | 0.0030272 | 0.97809 | -0.1556 | 0.97807 | -0.15576 | 1.1212
31 | -0.0026843 | -0.00066797 | 0.0026845 | 0.00066781 | 2.0432e-07 | -1.6819e-07 | 0.0040815 | 0.0040814 | 0.0040815 | 0.97821 | -0.15474 | 0.97829 | -0.15419 | 1.5117
32 | 0.0019246 | 0.00047805 | -0.0019246 | -0.00047813 | 3.7621e-08 | -7.3872e-08 | 0.0029266 | 0.0029266 | 0.0029266 | 0.97807 | -0.15576 | 0.97805 | -0.1559 | 1.0839
33 | 0.0009596 | 0.0002388 | -0.00095953 | -0.00023944 | 7.0012e-08 | -6.3471e-07 | 0.001459 | 0.0014592 | 0.0014592 | 0.97829 | -0.15419 | 0.97821 | -0.15472 | 0.54045
34 | -0.0036441 | -0.00090661 | 0.0036443 | 0.00090654 | 2.6419e-07 | -7.1582e-08 | 0.0055404 | 0.0055403 | 0.0055404 | 0.97829 | -0.15419 | 0.97836 | -0.15365 | 2.052
35 | -0.026868 | -0.0067105 | 0.0269 | 0.0067192 | 3.1522e-05 | 8.6092e-06 | 0.040591 | 0.04059 | 0.040591 | 0.98474 | -0.10765 | 0.98594 | -0.099121 | 5.0113
36 | 0.01401 | 0.003493 | -0.013949 | -0.0034807 | 6.0582e-05 | 1.2321e-05 | 0.021164 | 0.021167 | 0.021167 | 0.98474 | -0.10765 | 0.98035 | -0.13925 | 3.9199
37 | 0.011747 | 0.002939 | -0.011683 | -0.0029186 | 6.3746e-05 | 2.0415e-05 | 0.017749 | 0.01775 | 0.01775 | 0.98474 | -0.10765 | 0.97923 | -0.14715 | 6.5741
38 | -0.0269 | -0.0067192 | 0.026909 | 0.0067217 | 9.435e-06 | 2.5751e-06 | 0.04059 | 0.04059 | 0.04059 | 0.98594 | -0.099121 | 0.98629 | -0.096571 | 5.0111
39 | 0.013605 | 0.0033943 | -0.013601 | -0.003393 | 3.7762e-06 | 1.2734e-06 | 0.020644 | 0.020644 | 0.020644 | 0.98035 | -0.13925 | 0.98007 | -0.14127 | 7.6461
40 | 0.0099004 | 0.002473 | -0.0098979 | -0.0024722 | 2.5267e-06 | 7.467e-07 | 0.015041 | 0.015042 | 0.015042 | 0.97923 | -0.14715 | 0.97897 | -0.149 | 5.5709
41 | 0.0014575 | 0.00036415 | -0.0014574 | -0.00036465 | 1.3514e-07 | -5.0349e-07 | 0.0022144 | 0.0022146 | 0.0022146 | 0.97923 | -0.14715 | 0.97914 | -0.14782 | 0.82024
42 | 0.001818 | 0.0004514 | -0.0018179 | -0.0004516 | 8.9098e-08 | -2.0021e-07 | 0.0027644 | 0.0027644 | 0.0027644 | 0.97805 | -0.1559 | 0.978 | -0.15626 | 1.0239
43 | 0.00088026 | 0.00021957 | -0.00088022 | -0.00021997 | 3.6901e-08 | -4.0003e-07 | 0.0013386 | 0.0013388 | 0.0013388 | 0.97821 | -0.15472 | 0.97817 | -0.15502 | 0.49585
44 | -0.010072 | -0.0025074 | 0.010076 | 0.0025087 | 4.1389e-06 | 1.2365e-06 | 0.015313 | 0.015313 | 0.015313 | 0.97836 | -0.15365 | 0.97877 | -0.15065 | 5.6715
45 | 0.0064278 | 0.0016009 | -0.0064262 | -0.0016006 | 1.6264e-06 | 2.8292e-07 | 0.0097726 | 0.0097727 | 0.0097727 | 0.97836 | -0.15365 | 0.9781 | -0.15551 | 3.6195
46 | 0.0016311 | 0.00040478 | -0.001631 | -0.00040507 | 1.0119e-07 | -2.9185e-07 | 0.0024802 | 0.0024803 | 0.0024803 | 0.978 | -0.15626 | 0.97794 | -0.15672 | 0.91864
47 | 0.0008342 | 0.00020843 | -0.00083419 | -0.00020858 | 1.1619e-08 | -1.4071e-07 | 0.0012688 | 0.0012688 | 0.0012688 | 0.97817 | -0.15502 | 0.97816 | -0.15513 | 0.46994
48 | -0.010152 | -0.0025275 | 0.010157 | 0.0025291 | 5.1144e-06 | 1.534e-06 | 0.015427 | 0.015427 | 0.015427 | 0.97877 | -0.15065 | 0.97928 | -0.14696 | 5.7138
49 | 0.0062918 | 0.0015669 | -0.0062918 | -0.0015669 | 2.0356e-08 | 3.3571e-09 | 0.0095683 | 0.0095683 | 0.0095683 | 0.9781 | -0.15551 | 0.9781 | -0.15553 | 3.5438
50 | 0.00095388 | 0.00023569 | -0.00095377 | -0.00023673 | 1.1375e-07 | -1.0431e-06 | 0.0014503 | 0.0014507 | 0.0014507 | 0.97789 | -0.15709 | 0.97777 | -0.15798 | 0.53729
51 | -0.0013354 | -0.00033129 | 0.0013354 | 0.00033112 | 3.8091e-08 | -1.7106e-07 | 0.0020308 | 0.0020307 | 0.0020308 | 0.97789 | -0.15709 | 0.97792 | -0.15688 | 0.75213
52 | 0.00086999 | 0.00021573 | -0.00086993 | -0.00021638 | 5.8509e-08 | -6.4904e-07 | 0.0013232 | 0.0013234 | 0.0013234 | 0.97777 | -0.15798 | 0.9777 | -0.15847 | 0.49015
53 | -0.0015203 | -0.00037746 | 0.0015203 | 0.00037735 | 3.3849e-08 | -1.143e-07 | 0.0023121 | 0.002312 | 0.0023121 | 0.97792 | -0.15688 | 0.97794 | -0.15672 | 0.85632
54 | 0.00024263 | 5.9165e-05 | -0.00024263 | -6.0114e-05 | 6.4463e-09 | -9.4967e-07 | 0.0003687 | 0.00036903 | 0.00036903 | 0.9777 | -0.15847 | 0.97767 | -0.15867 | 0.13668
55 | 0.00015506 | 3.8168e-05 | -0.00015506 | -3.8861e-05 | 1.9211e-09 | -6.9314e-07 | 0.00023576 | 0.000236 | 0.000236 | 0.97767 | -0.15867 | 0.97766 | -0.15876 | 0.087408
56 | -0.029827 | -0.0074529 | 0.029935 | 0.0074848 | 0.00010856 | 3.1845e-05 | 0.044991 | 0.044988 | 0.044991 | 0.98629 | -0.096571 | 0.99 | -0.070188 | 5.5545
57 | -0.0054349 | -0.0013529 | 0.005437 | 0.0013531 | 2.1247e-06 | 1.9351e-07 | 0.0082723 | 0.0082721 | 0.0082723 | 0.97724 | -0.16178 | 0.97763 | -0.15892 | 3.0638
58 | -0.005437 | -0.0013531 | 0.0054387 | 0.0013532 | 1.7212e-06 | 1.5637e-07 | 0.0082721 | 0.0082719 | 0.0082721 | 0.97763 | -0.15892 | 0.97795 | -0.1566 | 3.0637
59 | -0.0059167 | -0.001473 | 0.0059176 | 0.0014731 | 8.6749e-07 | 1.1823e-07 | 0.0089992 | 0.0089991 | 0.0089992 | 0.97795 | -0.1566 | 0.9781 | -0.15553 | 3.333
60 | 0.00046498 | 0.00011604 | -0.00046497 | -0.0001163 | 6.5075e-09 | -2.5922e-07 | 0.00070717 | 0.00070726 | 0.00070726 | 0.97816 | -0.15513 | 0.97814 | -0.15523 | 0.26195
61 | 0.00040473 | 0.0001012 | -0.00040472 | -0.00010143 | 4.3573e-09 | -2.2956e-07 | 0.00061562 | 0.0006157 | 0.0006157 | 0.97814 | -0.15523 | 0.97813 | -0.15531 | 0.22804
62 | 0.013259 | 0.0033072 | -0.013255 | -0.0033059 | 3.8728e-06 | 1.2965e-06 | 0.020125 | 0.020125 | 0.020125 | 0.98007 | -0.14127 | 0.97978 | -0.1434 | 7.4536
63 | 0.012138 | 0.0030259 | -0.012136 | -0.0030255 | 1.4762e-06 | 4.8005e-07 | 0.018428 | 0.018428 | 0.018428 | 0.97978 | -0.1434 | 0.97965 | -0.14429 | 6.8253
64 | 0.011493 | 0.0028644 | -0.011489 | -0.002863 | 4.201e-06 | 1.3376e-06 | 0.017452 | 0.017452 | 0.017452 | 0.97965 | -0.14429 | 0.97928 | -0.14696 | 6.4637
65 | 0.0051421 | 0.0012854 | -0.0051386 | -0.0012852 | 3.4522e-06 | 2.0583e-07 | 0.0078428 | 0.0078432 | 0.0078432 | 0.97545 | -0.17441 | 0.97478 | -0.17928 | 2.9049
66 | -0.0052541 | -0.0013135 | 0.0052544 | 0.0013135 | 2.9059e-07 | 2.1239e-08 | 0.0080138 | 0.0080137 | 0.0080138 | 0.97545 | -0.17441 | 0.97551 | -0.17401 | 2.9681
67 | 0.0050681 | 0.0012675 | -0.0050675 | -0.0012675 | 6.4288e-07 | 3.267e-08 | 0.0077356 | 0.0077357 | 0.0077357 | 0.97478 | -0.17928 | 0.97465 | -0.1802 | 2.8651
68 | -0.0054291 | -0.0013573 | 0.0054343 | 0.0013578 | 5.2915e-06 | 4.8937e-07 | 0.0082801 | 0.0082796 | 0.0082801 | 0.97551 | -0.17401 | 0.97649 | -0.16693 | 3.0667
69 | 0.00030712 | 7.6808e-05 | -0.00030712 | -7.6971e-05 | 1.8072e-09 | -1.635e-07 | 0.00046883 | 0.00046889 | 0.00046889 | 0.97465 | -0.1802 | 0.97464 | -0.18025 | 0.17366
70 | 0.0047604 | 0.0011907 | -0.0047591 | -0.0011907 | 1.2998e-06 | 8.4849e-09 | 0.0072669 | 0.0072671 | 0.0072671 | 0.97465 | -0.1802 | 0.97438 | -0.18218 | 2.6915
71 | 0.004511 | 0.0011285 | -0.0045069 | -0.0011286 | 4.0989e-06 | -1.461e-07 | 0.0068882 | 0.0068889 | 0.0068889 | 0.97438 | -0.18218 | 0.97346 | -0.18877 | 2.5514
72 | 0.0039025 | 0.00097716 | -0.0039018 | -0.00097728 | 6.6281e-07 | -1.1614e-07 | 0.0059649 | 0.0059651 | 0.0059651 | 0.97346 | -0.18877 | 0.97329 | -0.18999 | 2.2093
73 | -0.0075647 | -0.001888 | 0.0075679 | 0.0018888 | 3.1561e-06 | 7.3546e-07 | 0.011514 | 0.011513 | 0.011514 | 0.97743 | -0.16015 | 0.97785 | -0.15711 | 4.2643
74 | 0.00077617 | 0.00019392 | -0.00077616 | -0.00019399 | 5.148e-09 | -7.2623e-08 | 0.0011793 | 0.0011794 | 0.0011794 | 0.97914 | -0.14782 | 0.97913 | -0.14787 | 0.4368
75 | 0.00064644 | 0.00016148 | -0.00064641 | -0.00016201 | 2.5784e-08 | -5.2866e-07 | 0.00098222 | 0.00098241 | 0.00098241 | 0.97913 | -0.14787 | 0.97909 | -0.14816 | 0.36386
76 | 0.0097992 | 0.0024475 | -0.0097988 | -0.0024474 | 4.5122e-07 | 1.3255e-07 | 0.014892 | 0.014892 | 0.014892 | 0.97897 | -0.149 | 0.97893 | -0.14934 | 5.5154
77 | 0.0094099 | 0.0023499 | -0.0094067 | -0.002349 | 3.2017e-06 | 9.161e-07 | 0.0143 | 0.014301 | 0.014301 | 0.97893 | -0.14934 | 0.97858 | -0.15181 | 5.2965
78 | 0.0083057 | 0.0020737 | -0.0083049 | -0.0020735 | 7.8553e-07 | 2.0294e-07 | 0.012627 | 0.012627 | 0.012627 | 0.97858 | -0.15181 | 0.97849 | -0.1525 | 4.6765
79 | 0.001101 | 0.00027531 | -0.001101 | -0.00027547 | 2.3677e-08 | -1.61e-07 | 0.001674 | 0.001674 | 0.001674 | 0.97858 | -0.15181 | 0.97856 | -0.15197 | 0.62001
80 | 0.00028587 | 7.1643e-05 | -0.00028587 | -7.1646e-05 | 3.1526e-11 | -3.3503e-09 | 0.00043472 | 0.00043473 | 0.00043473 | 0.97851 | -0.15234 | 0.97851 | -0.15234 | 0.16101
81 | -0.00069699 | -0.00017468 | 0.00069699 | 0.00017458 | 5.7577e-09 | -1.0096e-07 | 0.0010599 | 0.0010599 | 0.0010599 | 0.97851 | -0.15234 | 0.97852 | -0.15228 | 0.39256
82 | -0.00098847 | -0.00024763 | 0.00098848 | 0.00024756 | 7.9099e-09 | -6.7438e-08 | 0.0015031 | 0.0015031 | 0.0015031 | 0.97852 | -0.15228 | 0.97853 | -0.15222 | 0.55671
83 | -0.0010352 | -0.00025928 | 0.0010353 | 0.000259 | 3.6162e-08 | -2.7989e-07 | 0.0015742 | 0.0015741 | 0.0015742 | 0.97853 | -0.15222 | 0.97856 | -0.15197 | 0.58303
84 | 0.0080839 | 0.0020181 | -0.0080822 | -0.0020177 | 1.6103e-06 | 4.0481e-07 | 0.012291 | 0.012291 | 0.012291 | 0.97849 | -0.1525 | 0.97829 | -0.15395 | 4.5521
85 | 0.0079603 | 0.0019871 | -0.0079569 | -0.0019863 | 3.4567e-06 | 8.5506e-07 | 0.012105 | 0.012105 | 0.012105 | 0.97829 | -0.15395 | 0.97785 | -0.15711 | 4.4835
86 | 0.0034851 | 0.00087285 | -0.003485 | -0.00087289 | 1.3798e-07 | -4.3729e-08 | 0.005328 | 0.0053281 | 0.0053281 | 0.97329 | -0.18999 | 0.97325 | -0.19028 | 1.9734
87 | 0.0014031 | 0.00035112 | -0.001403 | -0.00035162 | 1.2679e-07 | -4.9991e-07 | 0.002145 | 0.0021452 | 0.0021452 | 0.97325 | -0.19028 | 0.97316 | -0.19094 | 0.79453
88 | 0.060595 | 0.015229 | -0.060523 | -0.015202 | 7.1444e-05 | 2.7301e-05 | 0.091105 | 0.091105 | 0.091105 | 0.98985 | -0.070814 | 0.98865 | -0.079293 | 33.7427
89 | -0.060774 | -0.015274 | 0.061077 | 0.01539 | 0.00030333 | 0.00011591 | 0.091374 | 0.091374 | 0.091374 | 0.98985 | -0.070814 | 0.99495 | -0.035143 | 33.8423
90 | 0.060326 | 0.015152 | -0.060208 | -0.015107 | 0.00011827 | 4.5193e-05 | 0.090809 | 0.090809 | 0.090809 | 0.98865 | -0.079293 | 0.98665 | -0.093421 | 33.633
91 | 0.034885 | 0.0087363 | -0.03487 | -0.0087315 | 1.5236e-05 | 4.812e-06 | 0.052171 | 0.052171 | 0.052171 | 0.99495 | -0.035143 | 0.9945 | -0.038304 | 6.4409
92 | -0.095962 | -0.024126 | 0.096208 | 0.024219 | 0.00024626 | 9.247e-05 | 0.14354 | 0.14354 | 0.14354 | 0.99495 | -0.035143 | 0.99758 | -0.016769 | 17.7215
93 | 0.04022 | 0.010096 | -0.0402 | -0.010088 | 2.0022e-05 | 7.5894e-06 | 0.060663 | 0.060663 | 0.060663 | 0.98665 | -0.093421 | 0.98614 | -0.097007 | 22.468
94 | 0.019988 | 0.0050114 | -0.019977 | -0.0050074 | 1.1155e-05 | 4.0393e-06 | 0.030146 | 0.030146 | 0.030146 | 0.98665 | -0.093421 | 0.98608 | -0.097451 | 11.165
95 | 0.03487 | 0.0087315 | -0.034857 | -0.0087276 | 1.2354e-05 | 3.9025e-06 | 0.052171 | 0.052171 | 0.052171 | 0.9945 | -0.038304 | 0.99414 | -0.040868 | 6.4409
96 | -0.09659 | -0.024314 | 0.096699 | 0.024355 | 0.00010943 | 4.1096e-05 | 0.14411 | 0.14411 | 0.14411 | 0.99758 | -0.016769 | 0.99875 | -0.0086659 | 17.7917
97 | 0.0402 | 0.010088 | -0.040151 | -0.01007 | 4.9378e-05 | 1.8718e-05 | 0.060663 | 0.060664 | 0.060664 | 0.98614 | -0.097007 | 0.9849 | -0.10587 | 22.468
98 | 0.01151 | 0.0028855 | -0.011508 | -0.0028847 | 2.4308e-06 | 7.7026e-07 | 0.01737 | 0.01737 | 0.01737 | 0.98608 | -0.097451 | 0.98587 | -0.098976 | 6.4332
99 | 0.034857 | 0.0087276 | -0.034717 | -0.0086831 | 0.00014078 | 4.4514e-05 | 0.052171 | 0.052175 | 0.052175 | 0.99414 | -0.040868 | 0.99 | -0.070188 | 6.4413
100 | -0.097062 | -0.024446 | 0.09718 | 0.024491 | 0.00011774 | 4.4222e-05 | 0.14465 | 0.14465 | 0.14465 | 0.99875 | -0.0086659 | 1 | 0 | 17.8584
101 | 0.036889 | 0.0092521 | -0.036875 | -0.0092468 | 1.413e-05 | 5.3419e-06 | 0.055736 | 0.055736 | 0.055736 | 0.9849 | -0.10587 | 0.98451 | -0.10863 | 20.6431
102 | 0.011508 | 0.0028847 | -0.011499 | -0.002882 | 8.5551e-06 | 2.7114e-06 | 0.01737 | 0.01737 | 0.01737 | 0.98587 | -0.098976 | 0.98511 | -0.10435 | 6.4333
103 | 0.088039 | 0.022198 | -0.087617 | -0.022036 | 0.00042229 | 0.0001619 | 0.13105 | 0.13105 | 0.13105 | 1 | 0 | 0.99505 | -0.034403 | 48.5374
104 | 0.020597 | 0.0051634 | -0.020597 | -0.0051634 | 4.5445e-08 | 1.6517e-08 | 0.031073 | 0.031073 | 0.031073 | 0.98634 | -0.095791 | 0.98633 | -0.095807 | 11.5086
105 | -0.022935 | -0.0057495 | 0.022953 | 0.0057562 | 1.8045e-05 | 6.6319e-06 | 0.034602 | 0.034601 | 0.034602 | 0.98634 | -0.095791 | 0.98714 | -0.090115 | 12.8154
106 | 0.018262 | 0.0045782 | -0.018249 | -0.0045736 | 1.3046e-05 | 4.6665e-06 | 0.027551 | 0.027551 | 0.027551 | 0.98633 | -0.095807 | 0.98561 | -0.10097 | 10.2041
107 | 0.017729 | 0.0044454 | -0.017716 | -0.004441 | 1.225e-05 | 4.3602e-06 | 0.026725 | 0.026725 | 0.026725 | 0.98714 | -0.090115 | 0.98643 | -0.095104 | 9.8982
108 | -0.040682 | -0.010202 | 0.040738 | 0.010223 | 5.5664e-05 | 2.1106e-05 | 0.061326 | 0.061326 | 0.061326 | 0.98714 | -0.090115 | 0.98853 | -0.080256 | 22.7135
109 | 0.0048007 | 0.0012031 | -0.0048006 | -0.0012031 | 1.2268e-07 | -5.1056e-10 | 0.0072479 | 0.0072479 | 0.0072479 | 0.98561 | -0.10097 | 0.98558 | -0.10115 | 2.6844
110 | 0.015911 | 0.0039887 | -0.015904 | -0.0039859 | 7.8634e-06 | 2.7453e-06 | 0.024002 | 0.024002 | 0.024002 | 0.98643 | -0.095104 | 0.98593 | -0.098674 | 8.8898
111 | -0.054238 | -0.013606 | 0.054304 | 0.013631 | 6.5793e-05 | 2.5102e-05 | 0.081648 | 0.081648 | 0.081648 | 0.98853 | -0.080256 | 0.98977 | -0.071521 | 30.2401
112 | 0.0024016 | 0.0006019 | -0.0024016 | -0.0006019 | 9.3127e-10 | -1.0886e-09 | 0.0036259 | 0.0036259 | 0.0036259 | 0.98558 | -0.10115 | 0.98558 | -0.10116 | 1.3429
113 | 0.014123 | 0.0035396 | -0.014122 | -0.0035394 | 5.813e-07 | 1.9743e-07 | 0.021315 | 0.021315 | 0.021315 | 0.98593 | -0.098674 | 0.98589 | -0.098971 | 7.8944
114 | 0.022349 | 0.0056023 | -0.022344 | -0.0056003 | 5.2366e-06 | 1.9186e-06 | 0.033601 | 0.033601 | 0.033601 | 0.98977 | -0.071521 | 0.98953 | -0.073213 | 12.4447
115 | -0.076653 | -0.019234 | 0.076836 | 0.019303 | 0.00018252 | 6.9916e-05 | 0.11525 | 0.11525 | 0.11525 | 0.98977 | -0.071521 | 0.9922 | -0.054402 | 42.6847
116 | 0.011714 | 0.0029357 | -0.011711 | -0.002935 | 2.4311e-06 | 7.7613e-07 | 0.017679 | 0.017679 | 0.017679 | 0.98589 | -0.098971 | 0.98568 | -0.10047 | 6.5479
117 | 0.013912 | 0.0034869 | -0.013903 | -0.0034839 | 8.856e-06 | 2.9898e-06 | 0.02092 | 0.02092 | 0.02092 | 0.98953 | -0.073213 | 0.98888 | -0.077813 | 7.7481
118 | -0.081664 | -0.020513 | 0.081892 | 0.020601 | 0.00022778 | 8.7294e-05 | 0.12249 | 0.12249 | 0.12249 | 0.9922 | -0.054402 | 0.99505 | -0.034403 | 45.3665
119 | 0.0024027 | 0.00060174 | -0.0024025 | -0.00060194 | 1.6507e-07 | -1.9614e-07 | 0.0036153 | 0.0036154 | 0.0036154 | 0.98888 | -0.077813 | 0.98881 | -0.07831 | 1.339
120 | 0.0014175 | 0.00035507 | -0.0014175 | -0.00035525 | 4.3023e-08 | -1.7781e-07 | 0.0021331 | 0.0021332 | 0.0021332 | 0.98881 | -0.07831 | 0.98878 | -0.078529 | 0.79006
121 | -0.0073583 | -0.001844 | 0.0073595 | 0.0018443 | 1.2166e-06 | 2.6675e-07 | 0.011112 | 0.011112 | 0.011112 | 0.98536 | -0.10276 | 0.98552 | -0.10156 | 4.1155
122 | 0.0048119 | 0.0012058 | -0.0048114 | -0.0012059 | 5.2071e-07 | -1.0036e-09 | 0.0072666 | 0.0072667 | 0.0072667 | 0.98536 | -0.10276 | 0.98525 | -0.10354 | 2.6914
123 | -0.0085289 | -0.0021374 | 0.0085289 | 0.0021374 | 5.8611e-10 | 1.5377e-10 | 0.012877 | 0.012877 | 0.012877 | 0.98552 | -0.10156 | 0.98552 | -0.10156 | 4.7694
124 | 0.0024058 | 0.00060295 | -0.0024058 | -0.00060295 | 1.2656e-10 | -1.4474e-10 | 0.0036335 | 0.0036335 | 0.0036335 | 0.98525 | -0.10354 | 0.98525 | -0.10354 | 1.3457
125 | -0.0096982 | -0.0024304 | 0.0096996 | 0.0024308 | 1.4673e-06 | 4.2458e-07 | 0.014643 | 0.014643 | 0.014643 | 0.98552 | -0.10156 | 0.98568 | -0.10047 | 5.4233
126 | 0.015055 | 0.0037731 | -0.01505 | -0.0037712 | 5.3342e-06 | 1.8435e-06 | 0.022803 | 0.022804 | 0.022804 | 0.98242 | -0.12346 | 0.98206 | -0.12602 | 8.4457
127 | -0.015055 | -0.0037731 | 0.015068 | 0.0037773 | 1.23e-05 | 4.2505e-06 | 0.022803 | 0.022803 | 0.022803 | 0.98242 | -0.12346 | 0.98325 | -0.11756 | 8.4457
128 | 0.010931 | 0.0027388 | -0.010929 | -0.0027384 | 1.3301e-06 | 4.1327e-07 | 0.016562 | 0.016562 | 0.016562 | 0.98206 | -0.12602 | 0.98194 | -0.12689 | 6.1341
129 | -0.019505 | -0.0048894 | 0.019506 | 0.0048899 | 1.4744e-06 | 5.3268e-07 | 0.029518 | 0.029518 | 0.029518 | 0.98325 | -0.11756 | 0.98333 | -0.11701 | 10.9327
130 | 0.032408 | 0.0081272 | -0.032398 | -0.0081236 | 9.7273e-06 | 3.6587e-06 | 0.048984 | 0.048984 | 0.048984 | 0.98451 | -0.10863 | 0.9842 | -0.1108 | 18.1424
131 | 0.0009973 | 0.00024959 | -0.00099725 | -0.00024994 | 4.0613e-08 | -3.4469e-07 | 0.0015113 | 0.0015115 | 0.0015115 | 0.98182 | -0.12773 | 0.98178 | -0.12802 | 0.5598
132 | -0.0066397 | -0.0016637 | 0.0066404 | 0.0016638 | 7.6395e-07 | 1.409e-07 | 0.010063 | 0.010063 | 0.010063 | 0.98182 | -0.12773 | 0.98194 | -0.12689 | 3.7269
133 | 0.004289 | 0.0010746 | -0.004288 | -0.0010747 | 9.8812e-07 | -9.4029e-08 | 0.0064994 | 0.0064996 | 0.0064996 | 0.98194 | -0.12689 | 0.98171 | -0.12856 | 2.4072
134 | 0.023634 | 0.005926 | -0.02362 | -0.0059209 | 1.396e-05 | 5.1471e-06 | 0.035743 | 0.035743 | 0.035743 | 0.98393 | -0.11275 | 0.98333 | -0.11701 | 13.2382
135 | -0.028638 | -0.0071801 | 0.028645 | 0.007183 | 7.7328e-06 | 2.8902e-06 | 0.043311 | 0.043311 | 0.043311 | 0.98393 | -0.11275 | 0.9842 | -0.1108 | 16.041

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.19226 | 0.048253

## res_load
| p_mw | q_mvar
0 | 0.0010893 | 0.000273
1 | 0.00039862 | 9.9904e-05
2 | 0.00062333 | 0.00015622
3 | 0.00080557 | 0.00020189
4 | 0.00038853 | 9.7375e-05
5 | 0.0001674 | 4.1954e-05
6 | 0.00058696 | 0.0001471
7 | 4.2054e-05 | 1.054e-05
8 | 9.7892e-05 | 2.4534e-05
9 | 0.00015651 | 3.9225e-05
10 | 9.0589e-05 | 2.2704e-05
11 | 0.000349 | 8.7468e-05
12 | 0.00054418 | 0.00013638
13 | 0.00038785 | 9.7205e-05
14 | 0.00014318 | 3.5883e-05
15 | 0.00066883 | 0.00016762
16 | 0.00018031 | 4.5191e-05
17 | 0.00014263 | 3.5748e-05
18 | 0.00045045 | 0.00011289
19 | 0.00035282 | 8.8426e-05
20 | 0.00016485 | 4.1315e-05
21 | 0.00017545 | 4.3972e-05
22 | 6.6159e-05 | 1.6581e-05
23 | 0.0011114 | 0.00027855
24 | 0.00034464 | 8.6375e-05
25 | 0.00032516 | 8.1494e-05
26 | 0.00010665 | 2.6728e-05
27 | 7.9274e-05 | 1.9868e-05
28 | 0.00018681 | 4.6818e-05
29 | 4.6022e-05 | 1.1534e-05
30 | 7.5351e-05 | 1.8885e-05
31 | 0.00013435 | 3.3672e-05
32 | 0.00038147 | 9.5606e-05
33 | 8.3783e-05 | 2.0998e-05
34 | 0.00018491 | 4.6343e-05
35 | 0.0006273 | 0.00015722
36 | 0.00011062 | 2.7724e-05
37 | 8.7566e-05 | 2.1946e-05
38 | 0.00015506 | 3.8861e-05
39 | 0.0029174 | 0.00073118
40 | 6.6139e-05 | 1.6576e-05
41 | 0.000478 | 0.0001198
42 | 0.00037417 | 9.3775e-05
43 | 0.00036921 | 9.2533e-05
44 | 6.0244e-05 | 1.5098e-05
45 | 0.00040472 | 0.00010143
46 | 0.00034236 | 8.5803e-05
47 | 0.0011171 | 0.00027996
48 | 0.00064271 | 0.00016108
49 | 0.0013326 | 0.00033398
50 | 0.00011205 | 2.8083e-05
51 | 7.0474e-05 | 1.7662e-05
52 | 0.00017464 | 4.3769e-05
53 | 0.00030712 | 7.6971e-05
54 | 0.00024807 | 6.2173e-05
55 | 0.00060443 | 0.00015148
56 | 0.00014996 | 3.7583e-05
57 | 0.00068124 | 0.00017074
58 | 0.00012973 | 3.2513e-05
59 | 9.8665e-05 | 2.4728e-05
60 | 0.00064641 | 0.00016201
61 | 0.00038887 | 9.7459e-05
62 | 0.00041112 | 0.00010304
63 | 0.00028587 | 7.1646e-05
64 | 0.00029147 | 7.305e-05
65 | 4.6759e-05 | 1.1719e-05
66 | 6.5729e-05 | 1.6473e-05
67 | 0.00022103 | 5.5396e-05
68 | 0.00012191 | 3.0552e-05
69 | 0.00041667 | 0.00010443
70 | 0.0020819 | 0.00052177
71 | 0.001403 | 0.00035162
72 | 0.00038902 | 9.7499e-05
73 | 0.00017884 | 4.4821e-05
74 | 0.00019697 | 4.9364e-05
75 | 0.00038173 | 9.5671e-05
76 | 0.0084665 | 0.0021219
77 | 0.00036293 | 9.0959e-05
78 | 0.0032613 | 0.00081737
79 | 0.0047814 | 0.0011983
80 | 0.0062453 | 0.0015652
81 | 0.0023387 | 0.00058612
82 | 0.0023348 | 0.00058515
83 | 0.013448 | 0.0033704
84 | 0.001805 | 0.00045238
85 | 0.0135 | 0.0033835
86 | 0.002399 | 0.00060125
87 | 0.0017808 | 0.00044631
88 | 0.0024016 | 0.0006019
89 | 0.0024087 | 0.00060367
90 | 0.0084327 | 0.0021134
91 | 0.0048282 | 0.0012101
92 | 0.0057253 | 0.0014349
93 | 0.0115 | 0.0028822
94 | 0.00098501 | 0.00024687
95 | 0.0014175 | 0.00035525
96 | 0.0025463 | 0.00063817
97 | 0.0011694 | 0.00029307
98 | 0.0024056 | 0.00060291
99 | 0.0011693 | 0.00029305
100 | 0.0024058 | 0.00060295
101 | 0.0020115 | 0.00050412
102 | 0.0041193 | 0.0010324
103 | 0.0044371 | 0.001112
104 | 0.0044672 | 0.0011196
105 | 0.011499 | 0.002882
106 | 0.0056424 | 0.0014141
107 | 0.00099725 | 0.00024994
108 | 0.004288 | 0.0010747
109 | 0.0050039 | 0.0012541
110 | 0.0041136 | 0.001031
111 | 0.0037529 | 0.00094055

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1