## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1084-3_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1084-3_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1084-3_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1084-3_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1084-3_0_5_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1084-3_0_5_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1084-3_0_5_node_24 | 0.4 | n |  | TRUE
7 | bus_LV_1084-3_0_5_node_45 | 0.4 | n |  | TRUE
8 | bus_LV_1084-3_0_5_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_1084-3_0_5_node_23 | 0.4 | n |  | TRUE
10 | bus_LV_1084-3_0_5_node_32 | 0.4 | n |  | TRUE
11 | bus_LV_1084-3_0_5_node_31 | 0.4 | n |  | TRUE
12 | bus_LV_1084-3_0_5_node_41 | 0.4 | n |  | TRUE
13 | bus_LV_1084-3_0_5_node_34 | 0.4 | n |  | TRUE
14 | bus_LV_1084-3_0_5_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_1084-3_0_5_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_1084-3_0_5_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1084-3_0_5_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1084-3_0_5_node_44 | 0.4 | n |  | TRUE
19 | bus_LV_1084-3_0_5_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1084-3_0_5_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1084-3_0_5_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1084-3_0_5_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1084-3_0_5_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1084-3_0_5_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1084-3_0_5_node_46 | 0.4 | n |  | TRUE
26 | bus_LV_1084-3_0_5_node_66 | 0.4 | n |  | TRUE
27 | bus_LV_1084-3_0_5_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_1084-3_0_5_node_61 | 0.4 | n |  | TRUE
29 | bus_LV_1084-3_0_5_node_63 | 0.4 | n |  | TRUE
30 | bus_LV_1084-3_0_5_node_64 | 0.4 | n |  | TRUE
31 | bus_LV_1084-3_0_5_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_1084-3_0_5_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_1084-3_0_5_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_1084-3_0_5_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_1084-3_0_5_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_1084-3_0_5_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_1084-3_0_5_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_1084-3_0_5_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_1084-3_0_5_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_1084-3_0_5_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_1084-3_0_5_node_28 | 0.4 | n |  | TRUE
42 | bus_LV_1084-3_0_5_node_81 | 0.4 | n |  | TRUE
43 | bus_LV_1084-3_0_5_node_80 | 0.4 | n |  | TRUE
44 | bus_LV_1084-3_0_5_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_1084-3_0_5_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_1084-3_0_5_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_1084-3_0_5_node_60 | 0.4 | n |  | TRUE
48 | bus_LV_1084-3_0_5_node_49 | 0.4 | n |  | TRUE
49 | bus_LV_1084-3_0_5_node_51 | 0.4 | n |  | TRUE
50 | bus_LV_1084-3_0_5_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_1084-3_0_5_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_1084-3_0_5_node_39 | 0.4 | n |  | TRUE
53 | bus_LV_1084-3_0_5_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_1084-3_0_5_node_58 | 0.4 | n |  | TRUE
55 | bus_LV_1084-3_0_5_node_54 | 0.4 | n |  | TRUE
56 | bus_LV_1084-3_0_5_node_55 | 0.4 | n |  | TRUE
57 | bus_LV_1084-3_0_5_node_53 | 0.4 | n |  | TRUE
58 | bus_LV_1084-3_0_5_node_57 | 0.4 | n |  | TRUE
59 | bus_LV_1084-3_0_5_node_62 | 0.4 | n |  | TRUE
60 | bus_LV_1084-3_0_5_node_48 | 0.4 | n |  | TRUE
61 | bus_LV_1084-3_0_5_node_50 | 0.4 | n |  | TRUE
62 | bus_LV_1084-3_0_5_node_59 | 0.4 | n |  | TRUE
63 | bus_LV_1084-3_0_5_node_56 | 0.4 | n |  | TRUE
64 | bus_LV_1084-3_0_5_node_52 | 0.4 | n |  | TRUE
65 | bus_MV_354_0_node_225 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1084-3_0_5_load_0 | 0 | 0.0088764 | 0.0022246 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1084-3_0_5_load_1 | 1 | 0.0056583 | 0.0014181 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1084-3_0_5_load_2 | 2 | 0.0071522 | 0.0017925 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1084-3_0_5_load_4 | 5 | 0.0056938 | 0.001427 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1084-3_0_5_load_45 | 7 | 0.0056612 | 0.0014188 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1084-3_0_5_load_32 | 10 | 0.0021157 | 0.00053026 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1084-3_0_5_load_31 | 11 | 0.014267 | 0.0035756 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1084-3_0_5_load_41 | 12 | 0.014928 | 0.0037412 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1084-3_0_5_load_6 | 14 | 0.004532 | 0.0011358 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1084-3_0_5_load_7 | 15 | 0.001798 | 0.00045062 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1084-3_0_5_load_8 | 16 | 0.0038669 | 0.00096913 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1084-3_0_5_load_9 | 17 | 0.0038486 | 0.00096455 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1084-3_0_5_load_44 | 18 | 0.0035215 | 0.00088258 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1084-3_0_5_load_10 | 19 | 0.0071375 | 0.0017888 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1084-3_0_5_load_11 | 20 | 0.0028772 | 0.0007211 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1084-3_0_5_load_12 | 21 | 0.003499 | 0.00087694 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1084-3_0_5_load_13 | 22 | 0.0029252 | 0.00073313 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1084-3_0_5_load_14 | 23 | 0.0020299 | 0.00050874 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1084-3_0_5_load_46 | 25 | 0.01061 | 0.0026591 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1084-3_0_5_load_66 | 26 | 0.0014991 | 0.0003757 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1084-3_0_5_load_22 | 27 | 0.007142 | 0.00179 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1084-3_0_5_load_61 | 28 | 0.0013188 | 0.00033052 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1084-3_0_5_load_63 | 29 | 0.0006364 | 0.0001595 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1084-3_0_5_load_64 | 30 | 0.00027826 | 6.9739e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1084-3_0_5_load_15 | 31 | 0.0015506 | 0.00038862 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1084-3_0_5_load_18 | 33 | 0.0072228 | 0.0018102 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1084-3_0_5_load_19 | 34 | 0.0051381 | 0.0012877 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1084-3_0_5_load_29 | 35 | 0.0072588 | 0.0018192 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1084-3_0_5_load_20 | 36 | 0.002157 | 0.00054059 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1084-3_0_5_load_27 | 38 | 0.0020099 | 0.00050373 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1084-3_0_5_load_25 | 39 | 0.0026973 | 0.00067601 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1084-3_0_5_load_26 | 40 | 0.0047271 | 0.0011847 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1084-3_0_5_load_28 | 41 | 0.0033844 | 0.00084822 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1084-3_0_5_load_81 | 42 | 0.00090302 | 0.00022632 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1084-3_0_5_load_80 | 43 | 0.0027186 | 0.00068135 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1084-3_0_5_load_37 | 44 | 0.0046565 | 0.001167 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1084-3_0_5_load_35 | 45 | 0.0034513 | 0.00086497 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1084-3_0_5_load_60 | 47 | 0.010894 | 0.0027303 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1084-3_0_5_load_49 | 48 | 0.0030162 | 0.00075593 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1084-3_0_5_load_51 | 49 | 0.00079903 | 0.00020026 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1084-3_0_5_load_47 | 50 | 0.0015221 | 0.00038146 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1084-3_0_5_load_40 | 53 | 0.002149 | 0.00053858 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1084-3_0_5_load_58 | 54 | 0.0071236 | 0.0017853 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1084-3_0_5_load_55 | 56 | 0.0028026 | 0.0007024 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1084-3_0_5_load_53 | 57 | 0.0047578 | 0.0011924 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1084-3_0_5_load_62 | 59 | 0.0074329 | 0.0018629 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1084-3_0_5_load_48 | 60 | 0.001553 | 0.00038921 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1084-3_0_5_load_59 | 62 | 0.0019462 | 0.00048777 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1084-3_0_5_load_56 | 63 | 0.0059101 | 0.0014812 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1084-3_0_5_load_52 | 64 | 0.0017415 | 0.00043645 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1084-3_0_5_line_0 | NAYY 4x150 SE | 0 | 1 | 0.012992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1084-3_0_5_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0047329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1084-3_0_5_line_2 | NAYY 4x150 SE | 1 | 3 | 0.013849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1084-3_0_5_line_3 | NAYY 4x150 SE | 3 | 4 | 0.071237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1084-3_0_5_line_4 | NAYY 4x150 SE | 3 | 5 | 0.010767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1084-3_0_5_line_5 | NAYY 4x150 SE | 4 | 6 | 0.039109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1084-3_0_5_line_6 | NAYY 4x150 SE | 4 | 7 | 0.026825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1084-3_0_5_line_7 | NAYY 4x150 SE | 6 | 12 | 0.12194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1084-3_0_5_line_8 | NAYY 4x150 SE | 6 | 8 | 0.04234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1084-3_0_5_line_9 | NAYY 4x150 SE | 7 | 13 | 0.024031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_1084-3_0_5_line_10 | NAYY 4x150 SE | 8 | 9 | 0.042483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1084-3_0_5_line_11 | NAYY 4x150 SE | 8 | 10 | 0.066707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1084-3_0_5_line_12 | NAYY 4x150 SE | 9 | 11 | 0.066847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1084-3_0_5_line_13 | NAYY 4x150 SE | 10 | 33 | 0.019558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1084-3_0_5_line_14 | NAYY 4x150 SE | 11 | 37 | 0.0022444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1084-3_0_5_line_15 | NAYY 4x150 SE | 13 | 18 | 0.02505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1084-3_0_5_line_16 | NAYY 4x150 SE | 13 | 17 | 0.027602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1084-3_0_5_line_17 | NAYY 4x150 SE | 14 | 15 | 0.0088256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1084-3_0_5_line_18 | NAYY 4x150 SE | 14 | 16 | 0.10537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1084-3_0_5_line_19 | NAYY 4x150 SE | 16 | 17 | 0.020269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1084-3_0_5_line_20 | NAYY 4x150 SE | 18 | 44 | 0.0088943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1084-3_0_5_line_21 | NAYY 4x150 SE | 19 | 20 | 0.013215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1084-3_0_5_line_22 | NAYY 4x150 SE | 19 | 21 | 0.0059864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1084-3_0_5_line_23 | NAYY 4x150 SE | 20 | 22 | 0.017701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1084-3_0_5_line_24 | NAYY 4x150 SE | 21 | 23 | 0.12216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1084-3_0_5_line_25 | NAYY 4x150 SE | 22 | 24 | 0.023533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1084-3_0_5_line_26 | NAYY 4x150 SE | 23 | 25 | 0.029744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1084-3_0_5_line_27 | NAYY 4x150 SE | 23 | 26 | 0.2035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1084-3_0_5_line_28 | NAYY 4x150 SE | 24 | 27 | 0.018761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1084-3_0_5_line_29 | NAYY 4x150 SE | 25 | 28 | 0.0073466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1084-3_0_5_line_30 | NAYY 4x150 SE | 26 | 30 | 0.0073997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1084-3_0_5_line_31 | NAYY 4x150 SE | 27 | 37 | 0.022018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1084-3_0_5_line_32 | NAYY 4x150 SE | 28 | 59 | 0.0010264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1084-3_0_5_line_33 | NAYY 4x150 SE | 29 | 30 | 0.015894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1084-3_0_5_line_34 | NAYY 4x150 SE | 31 | 32 | 0.024937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1084-3_0_5_line_35 | NAYY 4x150 SE | 32 | 33 | 0.012861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1084-3_0_5_line_36 | NAYY 4x150 SE | 32 | 34 | 0.015519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1084-3_0_5_line_37 | NAYY 4x150 SE | 34 | 35 | 0.038242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1084-3_0_5_line_38 | NAYY 4x150 SE | 35 | 38 | 0.038225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1084-3_0_5_line_39 | NAYY 4x150 SE | 36 | 37 | 0.037107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1084-3_0_5_line_40 | NAYY 4x150 SE | 38 | 39 | 0.0026801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1084-3_0_5_line_41 | NAYY 4x150 SE | 39 | 40 | 0.015602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1084-3_0_5_line_42 | NAYY 4x150 SE | 40 | 41 | 0.010051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1084-3_0_5_line_43 | NAYY 4x150 SE | 41 | 42 | 0.054297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1084-3_0_5_line_44 | NAYY 4x150 SE | 42 | 43 | 0.20324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1084-3_0_5_line_45 | NAYY 4x150 SE | 44 | 46 | 0.023129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1084-3_0_5_line_46 | NAYY 4x150 SE | 45 | 46 | 0.027874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1084-3_0_5_line_47 | NAYY 4x150 SE | 46 | 47 | 0.18119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1084-3_0_5_line_48 | NAYY 4x150 SE | 47 | 49 | 0.020078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1084-3_0_5_line_49 | NAYY 4x150 SE | 48 | 49 | 0.011331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1084-3_0_5_line_50 | NAYY 4x150 SE | 48 | 50 | 0.017853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1084-3_0_5_line_51 | NAYY 4x150 SE | 50 | 60 | 0.013498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1084-3_0_5_line_52 | NAYY 4x150 SE | 51 | 52 | 0.004246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1084-3_0_5_line_53 | NAYY 4x150 SE | 51 | 53 | 0.063525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1084-3_0_5_line_54 | NAYY 4x150 SE | 52 | 54 | 0.033975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1084-3_0_5_line_55 | NAYY 4x150 SE | 54 | 58 | 0.042476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1084-3_0_5_line_56 | NAYY 4x150 SE | 55 | 56 | 0.026946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1084-3_0_5_line_57 | NAYY 4x150 SE | 55 | 57 | 0.021963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1084-3_0_5_line_58 | NAYY 4x150 SE | 56 | 63 | 0.0072735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1084-3_0_5_line_59 | NAYY 4x150 SE | 58 | 62 | 0.11796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1084-3_0_5_line_60 | NAYY 4x150 SE | 58 | 63 | 0.027472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1084-3_0_5_line_61 | NAYY 4x150 SE | 60 | 61 | 0.01148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1084-3_0_5_line_62 | NAYY 4x150 SE | 61 | 64 | 0.0041009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1084-3_0_5_line_63 | NAYY 4x150 SE | 62 | 64 | 0.090631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1084-3_0_5_trafo_5 | 0.25 MVA 20/0.4 kV | 65 | 4 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2655184.5892 | 1222910.9593 | 2655171.6623 | 1222909.6646
1 | 2655189.2985 | 1222911.431 | 2655184.5892 | 1222910.9593
2 | 2655158.0385 | 1222907.1944 | 2655170.7046 | 1222909.5687 | 2655171.6623 | 1222909.6646
3 | 2655124.6225 | 1222969.5238 | 2655134.8377 | 1222941.7233 | 2655147.6442 | 1222920.751 | 2655158.0385 | 1222907.1944
4 | 2655158.0385 | 1222907.1944 | 2655164.2954 | 1222898.4324
5 | 2655094.2005 | 1222954.2551 | 2655096.1619 | 1222956.2078 | 2655097.3674 | 1222958.6983 | 2655097.6984 | 1222961.4475 | 2655097.1047 | 1222964.1437 | 2655106.9737 | 1222966.3474 | 2655111.5538 | 1222967.2348 | 2655124.6225 | 1222969.5238
6 | 2655124.6225 | 1222969.5238 | 2655135.9466 | 1222971.0295 | 2655148.4587 | 1222972.0015 | 2655151.304 | 1222972.1838
7 | 2655094.2005 | 1222954.2551 | 2655098.3072 | 1222944.0201 | 2655105.0659 | 1222926.6607 | 2655113.604 | 1222908.7952 | 2655121.7634 | 1222896.6187 | 2655125.6735 | 1222891.2404 | 2655139.8865 | 1222871.5375 | 2655152.1334 | 1222856.1302 | 2655156.886 | 1222850.723
8 | 2655077.5707 | 1222985.2095 | 2655085.5463 | 1222978.1232 | 2655086.9157 | 1222976.0235 | 2655087.7825 | 1222973.3187 | 2655088.017 | 1222969.285 | 2655090.8234 | 1222969.2554 | 2655093.4638 | 1222968.3015 | 2655095.634 | 1222966.5316 | 2655097.1047 | 1222964.1437 | 2655097.6984 | 1222961.4475 | 2655097.3674 | 1222958.6983 | 2655096.1619 | 1222956.2078 | 2655094.2005 | 1222954.2551
9 | 2655175.2732 | 1222973.8954 | 2655163.6782 | 1222972.9764 | 2655151.304 | 1222972.1838
10 | 2655077.5707 | 1222985.2095 | 2655065.5336 | 1222972.2457 | 2655064.2722 | 1222968.4094 | 2655064.032 | 1222962.4035 | 2655057.0462 | 1222949.3864
11 | 2655077.5707 | 1222985.2095 | 2655067.9458 | 1222992.6807 | 2655056.1287 | 1223001.8549 | 2655041.3586 | 1223012.1471 | 2655028.5285 | 1223023.4355 | 2655025.135 | 1223026.3459
12 | 2655057.0462 | 1222949.3864 | 2654998.3722 | 1222981.4158
13 | 2655010.258 | 1223039.0418 | 2655012.0088 | 1223037.6029 | 2655025.135 | 1223026.3459
14 | 2654996.4022 | 1222982.4912 | 2654998.3722 | 1222981.4158
15 | 2655175.2732 | 1222973.8954 | 2655200.2504 | 1222975.7984
16 | 2655175.2732 | 1222973.8954 | 2655174.5889 | 1222979.8039 | 2655172.5917 | 1222984.9997 | 2655169.6615 | 1222990.2092 | 2655163.6541 | 1222997.6804 | 2655163.2495 | 1222998.0137
17 | 2655053.1751 | 1223056.6075 | 2655044.8893 | 1223059.6465
18 | 2655147.042 | 1223010.1555 | 2655130.4117 | 1223021.6542 | 2655111.9555 | 1223033.6242 | 2655097.5295 | 1223040.3394 | 2655053.1751 | 1223056.6075
19 | 2655147.042 | 1223010.1555 | 2655156.18 | 1223003.8372 | 2655163.2495 | 1222998.0137
20 | 2655200.2504 | 1222975.7984 | 2655201.1919 | 1222975.8701 | 2655209.1266 | 1222976.3646
21 | 2654929.285 | 1222972.4162 | 2654940.91 | 1222966.1323
22 | 2654924.0188 | 1222975.2629 | 2654929.285 | 1222972.4162
23 | 2654956.4812 | 1222957.7152 | 2654940.91 | 1222966.1323
24 | 2654924.0188 | 1222975.2629 | 2654914.6751 | 1222980.3137 | 2654863.8484 | 1223008.2071 | 2654852.2004 | 1223013.8812 | 2654846.4181 | 1223015.0731 | 2654834.7307 | 1223014.3095 | 2654826.8206 | 1223011.8574 | 2654820.9829 | 1223008.357 | 2654818.6239 | 1223005.1 | 2654817.4138 | 1223001.4133
25 | 2654977.183 | 1222946.5248 | 2654956.4812 | 1222957.7152
26 | 2654817.4138 | 1223001.4133 | 2654817.1781 | 1223000.695 | 2654817.5694 | 1222995.2619 | 2654826.9307 | 1222973.6622
27 | 2654817.4138 | 1223001.4133 | 2654689.442 | 1223159.638
28 | 2654977.183 | 1222946.5248 | 2654986.0309 | 1222963.0687
29 | 2654826.9307 | 1222973.6622 | 2654828.2624 | 1222970.5895 | 2654828.0457 | 1222966.5976
30 | 2654694.7604 | 1223164.7828 | 2654689.442 | 1223159.638
31 | 2654996.4022 | 1222982.4912 | 2654991.3254 | 1222972.9829 | 2654986.5766 | 1222964.0891 | 2654986.0309 | 1222963.0687
32 | 2654828.0457 | 1222966.5976 | 2654827.9901 | 1222965.5727
33 | 2654701.2097 | 1223179.1865 | 2654700.0149 | 1223177.2722 | 2654698.1997 | 1223170.9627 | 2654694.7604 | 1223164.7828 | 2654694.7604 | 1223164.7828
34 | 2654999.2188 | 1223045.3896 | 2654978.1653 | 1223052.0327 | 2654975.4578 | 1223052.9561
35 | 2654999.2188 | 1223045.3896 | 2655006.1093 | 1223042.4514 | 2655010.258 | 1223039.0418
36 | 2654999.2188 | 1223045.3896 | 2654999.952 | 1223060.891
37 | 2655004.3802 | 1223098.8249 | 2655000.5955 | 1223074.4982 | 2654999.952 | 1223060.891
38 | 2655004.3802 | 1223098.8249 | 2655005.3417 | 1223105.0054 | 2655009.0379 | 1223136.7617
39 | 2654996.4022 | 1222982.4912 | 2654963.8311 | 1223000.2689
40 | 2655009.0379 | 1223136.7617 | 2655009.3477 | 1223139.4238
41 | 2655006.1068 | 1223154.3543 | 2655006.1068 | 1223154.3543 | 2655009.8524 | 1223143.7601 | 2655009.3477 | 1223139.4238
42 | 2655006.1068 | 1223154.3543 | 2655001.2257 | 1223163.1405
43 | 2655001.2257 | 1223163.1405 | 2654999.968 | 1223165.4045 | 2654987.7837 | 1223191.3859 | 2654975.226 | 1223210.6683
44 | 2654975.226 | 1223210.6683 | 2654842.7558 | 1223364.8028
45 | 2655232.1232 | 1222978.7142 | 2655218.7993 | 1222976.9673 | 2655209.1266 | 1222976.3646
46 | 2655232.1232 | 1222978.7142 | 2655234.7687 | 1222969.8665 | 2655235.8935 | 1222967.153 | 2655238.7279 | 1222964.0996 | 2655247.9774 | 1222957.2053
47 | 2655232.1232 | 1222978.7142 | 2655335.6498 | 1223127.4118
48 | 2655335.6498 | 1223127.4118 | 2655354.5337 | 1223120.5913
49 | 2655365.1906 | 1223116.7423 | 2655354.5337 | 1223120.5913
50 | 2655380.9571 | 1223108.6473 | 2655376.5788 | 1223111.9715 | 2655369.321 | 1223115.2505 | 2655365.1906 | 1223116.7423
51 | 2655380.9571 | 1223108.6473 | 2655388.0507 | 1223103.2616 | 2655392.1351 | 1223101.1649
52 | 2655461.2779 | 1222912.1574 | 2655465.5049 | 1222912.6748
53 | 2655461.2779 | 1222912.1574 | 2655455.7364 | 1222905.3793 | 2655441.8812 | 1222894.6993 | 2655422.6455 | 1222872.9735 | 2655418.0452 | 1222866.1153
54 | 2655465.5049 | 1222912.6748 | 2655468.4522 | 1222931.7141 | 2655473.7572 | 1222945.4334
55 | 2655503.2443 | 1222971.9299 | 2655496.4068 | 1222969.9538 | 2655484.0989 | 1222964.1689 | 2655478.7903 | 1222958.4492 | 2655473.7572 | 1222945.4334
56 | 2655515.8764 | 1222920.9825 | 2655523.905 | 1222943.249 | 2655524.2235 | 1222946.5095
57 | 2655515.8764 | 1222920.9825 | 2655528.8349 | 1222917.201 | 2655536.1082 | 1222912.8722
58 | 2655519.0513 | 1222951.4705 | 2655522.6009 | 1222948.907 | 2655524.2235 | 1222946.5095
59 | 2655503.2443 | 1222971.9299 | 2655411.1202 | 1223045.5994
60 | 2655503.2443 | 1222971.9299 | 2655503.9426 | 1222966.1661 | 2655506.5055 | 1222960.5309 | 2655519.0513 | 1222951.4705
61 | 2655403.4383 | 1223101.6148 | 2655397.6328 | 1223100.4045 | 2655392.1351 | 1223101.1649 | 2655392.1351 | 1223101.1649
62 | 2655403.4383 | 1223101.6148 | 2655406.4975 | 1223098.8836
63 | 2655411.1202 | 1223045.5994 | 2655427.0936 | 1223047.7013 | 2655434.2766 | 1223050.0251 | 2655437.7464 | 1223052.8592 | 2655440.7936 | 1223057.9129 | 2655441.3009 | 1223059.6298 | 2655441.5119 | 1223063.8455 | 2655440.1555 | 1223069.4252 | 2655435.9151 | 1223074.4222 | 2655420.3849 | 1223086.4852 | 2655406.4975 | 1223098.8836

## bus_geodata
| x | y | coords
0 | 2655184.5892 | 1222910.9593
1 | 2655171.6623 | 1222909.6646
2 | 2655189.2985 | 1222911.431
3 | 2655158.0385 | 1222907.1944
4 | 2655124.6225 | 1222969.5238
5 | 2655164.2954 | 1222898.4324
6 | 2655094.2005 | 1222954.2551
7 | 2655151.304 | 1222972.1838
8 | 2655077.5707 | 1222985.2095
9 | 2655057.0462 | 1222949.3864
10 | 2655025.135 | 1223026.3459
11 | 2654998.3722 | 1222981.4158
12 | 2655156.886 | 1222850.723
13 | 2655175.2732 | 1222973.8954
14 | 2655053.1751 | 1223056.6075
15 | 2655044.8893 | 1223059.6465
16 | 2655147.042 | 1223010.1555
17 | 2655163.2495 | 1222998.0137
18 | 2655200.2504 | 1222975.7984
19 | 2654929.285 | 1222972.4162
20 | 2654940.91 | 1222966.1323
21 | 2654924.0188 | 1222975.2629
22 | 2654956.4812 | 1222957.7153
23 | 2654817.4138 | 1223001.4133
24 | 2654977.183 | 1222946.5248
25 | 2654826.9307 | 1222973.6622
26 | 2654689.442 | 1223159.638
27 | 2654986.0309 | 1222963.0687
28 | 2654828.0457 | 1222966.5976
29 | 2654701.2097 | 1223179.1865
30 | 2654694.7604 | 1223164.7828
31 | 2654975.4578 | 1223052.9561
32 | 2654999.2188 | 1223045.3896
33 | 2655010.258 | 1223039.0418
34 | 2654999.952 | 1223060.891
35 | 2655004.3802 | 1223098.8249
36 | 2654963.8311 | 1223000.2689
37 | 2654996.4022 | 1222982.4912
38 | 2655009.0379 | 1223136.7617
39 | 2655009.3477 | 1223139.4238
40 | 2655006.1068 | 1223154.3543
41 | 2655001.2257 | 1223163.1405
42 | 2654975.226 | 1223210.6683
43 | 2654842.7558 | 1223364.8028
44 | 2655209.1266 | 1222976.3646
45 | 2655247.9774 | 1222957.2053
46 | 2655232.1232 | 1222978.7142
47 | 2655335.6498 | 1223127.4118
48 | 2655365.1906 | 1223116.7423
49 | 2655354.5338 | 1223120.5913
50 | 2655380.9571 | 1223108.6473
51 | 2655461.2779 | 1222912.1574
52 | 2655465.5049 | 1222912.6748
53 | 2655418.0452 | 1222866.1153
54 | 2655473.7572 | 1222945.4334
55 | 2655515.8764 | 1222920.9825
56 | 2655524.2235 | 1222946.5095
57 | 2655536.1082 | 1222912.8722
58 | 2655503.2443 | 1222971.9299
59 | 2654827.9901 | 1222965.5727
60 | 2655392.1351 | 1223101.1649
61 | 2655403.4383 | 1223101.6148
62 | 2655411.1202 | 1223045.5994
63 | 2655519.0513 | 1222951.4705
64 | 2655406.4975 | 1223098.8836
65 | 2655097.1047 | 1222964.1437

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99648 | -0.024635 | 0.0088764 | 0.0022246
1 | 0.99678 | -0.022543 | 0.0056583 | 0.0014181
2 | 0.99643 | -0.024975 | 0.0071522 | 0.0017925
3 | 0.99721 | -0.019527 | 0 | 0
4 | 1 | 0 | -0.22551 | -0.056728
5 | 0.99712 | -0.020142 | 0.0056938 | 0.001427
6 | 0.99664 | -0.023223 | 0 | 0
7 | 0.99853 | -0.010141 | 0.0056612 | 0.0014188
8 | 0.99345 | -0.045341 | 0 | 0
9 | 0.9895 | -0.072888 | 0 | 0
10 | 0.98962 | -0.072272 | 0.0021157 | 0.00053026
11 | 0.98328 | -0.11668 | 0.014267 | 0.0035756
12 | 0.99403 | -0.041568 | 0.014928 | 0.0037412
13 | 0.99731 | -0.018569 | 0 | 0
14 | 0.99551 | -0.031261 | 0.004532 | 0.0011358
15 | 0.99549 | -0.031421 | 0.001798 | 0.00045062
16 | 0.99646 | -0.024544 | 0.0038669 | 0.00096913
17 | 0.99676 | -0.022465 | 0.0038486 | 0.00096455
18 | 0.9963 | -0.025603 | 0.0035215 | 0.00088258
19 | 0.97747 | -0.15797 | 0.0071375 | 0.0017888
20 | 0.97814 | -0.15321 | 0.0028772 | 0.0007211
21 | 0.97723 | -0.15968 | 0.003499 | 0.00087694
22 | 0.9791 | -0.14632 | 0.0029252 | 0.00073313
23 | 0.97297 | -0.19024 | 0.0020299 | 0.00050874
24 | 0.98049 | -0.13647 | 0 | 0
25 | 0.97212 | -0.19632 | 0.01061 | 0.0026591
26 | 0.97225 | -0.19545 | 0.0014991 | 0.0003757
27 | 0.98159 | -0.12863 | 0.007142 | 0.00179
28 | 0.97203 | -0.197 | 0.0013188 | 0.00033052
29 | 0.97222 | -0.19563 | 0.0006364 | 0.0001595
30 | 0.97224 | -0.19552 | 0.00027826 | 6.9739e-05
31 | 0.98794 | -0.084179 | 0.0015506 | 0.00038862
32 | 0.988 | -0.083784 | 0 | 0
33 | 0.98856 | -0.079785 | 0.0072228 | 0.0018102
34 | 0.98735 | -0.088368 | 0.0051381 | 0.0012877
35 | 0.98604 | -0.097671 | 0.0072588 | 0.0018192
36 | 0.983 | -0.11865 | 0.002157 | 0.00054059
37 | 0.98312 | -0.11783 | 0 | 0
38 | 0.98513 | -0.10414 | 0.0020099 | 0.00050373
39 | 0.98507 | -0.10454 | 0.0026973 | 0.00067601
40 | 0.98481 | -0.10643 | 0.0047271 | 0.0011847
41 | 0.9847 | -0.10715 | 0.0033844 | 0.00084822
42 | 0.98442 | -0.10919 | 0.00090302 | 0.00022632
43 | 0.98362 | -0.1149 | 0.0027186 | 0.00068135
44 | 0.99562 | -0.030292 | 0.0046565 | 0.001167
45 | 0.99387 | -0.042399 | 0.0034513 | 0.00086497
46 | 0.99401 | -0.041426 | 0 | 0
47 | 0.98231 | -0.12342 | 0.010894 | 0.0027303
48 | 0.98079 | -0.13418 | 0.0030162 | 0.00075593
49 | 0.98133 | -0.13035 | 0.00079903 | 0.00020026
50 | 0.98001 | -0.13966 | 0.0015221 | 0.00038146
51 | 0.97094 | -0.20463 | 0 | 0
52 | 0.97095 | -0.20453 | 0 | 0
53 | 0.97074 | -0.20607 | 0.002149 | 0.00053858
54 | 0.97106 | -0.20375 | 0.0071236 | 0.0017853
55 | 0.97082 | -0.20544 | 0 | 0
56 | 0.97101 | -0.20408 | 0.0028026 | 0.0007024
57 | 0.97067 | -0.20655 | 0.0047578 | 0.0011924
58 | 0.97164 | -0.19958 | 0 | 0
59 | 0.97202 | -0.19708 | 0.0074329 | 0.0018629
60 | 0.97946 | -0.14359 | 0.001553 | 0.00038921
61 | 0.97902 | -0.14675 | 0 | 0
62 | 0.97557 | -0.1713 | 0.0019462 | 0.00048777
63 | 0.97109 | -0.2035 | 0.0059101 | 0.0014812
64 | 0.97886 | -0.14788 | 0.0017415 | 0.00043645
65 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.016029 | -0.0040172 | 0.016034 | 0.0040188 | 4.6444e-06 | 1.617e-06 | 0.023936 | 0.023935 | 0.023936 | 0.99648 | -0.024635 | 0.99678 | -0.022543 | 8.865
1 | 0.0071525 | 0.0017926 | -0.0071522 | -0.0017925 | 3.369e-07 | 6.7926e-08 | 0.010681 | 0.010681 | 0.010681 | 0.99648 | -0.024635 | 0.99643 | -0.024975 | 3.9558
2 | -0.021692 | -0.0054369 | 0.021701 | 0.0054402 | 9.062e-06 | 3.3048e-06 | 0.032382 | 0.032382 | 0.032382 | 0.99678 | -0.022543 | 0.99721 | -0.019527 | 11.9934
3 | -0.027395 | -0.0068673 | 0.02747 | 0.0068949 | 7.4283e-05 | 2.7638e-05 | 0.040879 | 0.040879 | 0.040879 | 0.99721 | -0.019527 | 1 | 0 | 15.1404
4 | 0.0056943 | 0.001427 | -0.0056938 | -0.001427 | 4.8504e-07 | 4.6104e-08 | 0.0084968 | 0.0084969 | 0.0084969 | 0.99721 | -0.019527 | 0.99712 | -0.020142 | 3.147
5 | 0.12051 | 0.030457 | -0.12011 | -0.030307 | 0.00039274 | 0.00015003 | 0.17941 | 0.17941 | 0.17941 | 1 | 0 | 0.99664 | -0.023223 | 33.2233
6 | 0.076732 | 0.019376 | -0.076623 | -0.019334 | 0.00010921 | 4.13e-05 | 0.11423 | 0.11423 | 0.11423 | 1 | 0 | 0.99853 | -0.010141 | 21.1538
7 | 0.014966 | 0.0037542 | -0.014928 | -0.0037412 | 3.7994e-05 | 1.3028e-05 | 0.022345 | 0.022346 | 0.022346 | 0.99664 | -0.023223 | 0.99403 | -0.041568 | 8.2762
8 | 0.10515 | 0.026553 | -0.10482 | -0.026429 | 0.00032587 | 0.00012423 | 0.15706 | 0.15706 | 0.15706 | 0.99664 | -0.023223 | 0.99345 | -0.045341 | 29.0854
9 | 0.070962 | 0.017916 | -0.070878 | -0.017884 | 8.3916e-05 | 3.1648e-05 | 0.10579 | 0.10579 | 0.10579 | 0.99853 | -0.010141 | 0.99731 | -0.018569 | 19.5915
10 | 0.064819 | 0.016372 | -0.064569 | -0.016277 | 0.00025011 | 9.5647e-05 | 0.097132 | 0.097132 | 0.097132 | 0.99345 | -0.045341 | 0.9895 | -0.072888 | 35.9749
11 | 0.040004 | 0.010057 | -0.039854 | -0.0099999 | 0.0001495 | 5.6638e-05 | 0.059929 | 0.059929 | 0.059929 | 0.99345 | -0.045341 | 0.98962 | -0.072272 | 22.1961
12 | 0.064569 | 0.016277 | -0.064175 | -0.016126 | 0.00039354 | 0.00015051 | 0.097132 | 0.097132 | 0.097132 | 0.9895 | -0.072888 | 0.98328 | -0.11668 | 35.975
13 | 0.037738 | 0.0094697 | -0.037699 | -0.0094548 | 3.9303e-05 | 1.4865e-05 | 0.056748 | 0.056748 | 0.056748 | 0.98962 | -0.072272 | 0.98856 | -0.079785 | 21.0178
14 | 0.049908 | 0.01255 | -0.0499 | -0.012547 | 7.9921e-06 | 3.0454e-06 | 0.075542 | 0.075542 | 0.075542 | 0.98328 | -0.11668 | 0.98312 | -0.11783 | 27.9786
15 | 0.056816 | 0.01436 | -0.05676 | -0.014339 | 5.622e-05 | 2.097e-05 | 0.084813 | 0.084814 | 0.084814 | 0.99731 | -0.018569 | 0.9963 | -0.025603 | 15.7062
16 | 0.014062 | 0.0035243 | -0.014054 | -0.0035218 | 7.5819e-06 | 2.5561e-06 | 0.020981 | 0.020981 | 0.020981 | 0.99731 | -0.018569 | 0.99676 | -0.022465 | 7.7707
17 | 0.001798 | 0.00045052 | -0.001798 | -0.00045062 | 3.9778e-08 | -9.9447e-08 | 0.0026875 | 0.0026876 | 0.0026876 | 0.99551 | -0.031261 | 0.99549 | -0.031421 | 0.99539
18 | -0.00633 | -0.0015864 | 0.0063359 | 0.0015872 | 5.8861e-06 | 8.9253e-07 | 0.0094617 | 0.0094612 | 0.0094617 | 0.99551 | -0.031261 | 0.99646 | -0.024544 | 3.5043
19 | -0.010203 | -0.0025564 | 0.010206 | 0.0025572 | 2.9358e-06 | 8.6505e-07 | 0.015236 | 0.015235 | 0.015236 | 0.99646 | -0.024544 | 0.99676 | -0.022465 | 5.6428
20 | 0.053238 | 0.013456 | -0.053203 | -0.013443 | 3.5125e-05 | 1.3394e-05 | 0.079554 | 0.079554 | 0.079554 | 0.9963 | -0.025603 | 0.99562 | -0.030292 | 29.4645
21 | -0.034568 | -0.0086757 | 0.034591 | 0.0086843 | 2.2839e-05 | 8.6184e-06 | 0.052628 | 0.052628 | 0.052628 | 0.97747 | -0.15797 | 0.97814 | -0.15321 | 19.4919
22 | 0.027431 | 0.0068869 | -0.027424 | -0.0068845 | 6.5151e-06 | 2.4308e-06 | 0.041763 | 0.041763 | 0.041763 | 0.97747 | -0.15797 | 0.97723 | -0.15968 | 15.4676
23 | -0.037468 | -0.0094054 | 0.037504 | 0.009419 | 3.5892e-05 | 1.3582e-05 | 0.057005 | 0.057005 | 0.057005 | 0.97814 | -0.15321 | 0.9791 | -0.14632 | 21.113
24 | 0.023925 | 0.0060075 | -0.023824 | -0.0059701 | 0.00010119 | 3.7397e-05 | 0.036435 | 0.036435 | 0.036435 | 0.97723 | -0.15968 | 0.97297 | -0.19024 | 13.4945
25 | -0.040429 | -0.010152 | 0.040485 | 0.010173 | 5.5451e-05 | 2.1031e-05 | 0.061451 | 0.061451 | 0.061451 | 0.9791 | -0.14632 | 0.98049 | -0.13647 | 22.7595
26 | 0.019379 | 0.0048586 | -0.019362 | -0.0048527 | 1.6303e-05 | 5.9014e-06 | 0.029638 | 0.029638 | 0.029638 | 0.97297 | -0.19024 | 0.97212 | -0.19632 | 10.9769
27 | 0.0024155 | 0.0006028 | -0.0024137 | -0.00060466 | 1.7324e-06 | -1.8592e-06 | 0.0036932 | 0.0036941 | 0.0036941 | 0.97297 | -0.19024 | 0.97225 | -0.19545 | 1.3682
28 | -0.040485 | -0.010173 | 0.040529 | 0.01019 | 4.4208e-05 | 1.6766e-05 | 0.061451 | 0.061451 | 0.061451 | 0.98049 | -0.13647 | 0.98159 | -0.12863 | 22.7595
29 | 0.0087525 | 0.0021936 | -0.0087517 | -0.0021934 | 8.2284e-07 | 2.254e-07 | 0.013397 | 0.013397 | 0.013397 | 0.97212 | -0.19632 | 0.97203 | -0.197 | 4.962
30 | 0.00091468 | 0.00022895 | -0.00091467 | -0.00022904 | 9.0478e-09 | -8.8284e-08 | 0.0013998 | 0.0013998 | 0.0013998 | 0.97225 | -0.19545 | 0.97224 | -0.19552 | 0.51846
31 | -0.047671 | -0.01198 | 0.047743 | 0.012007 | 7.1774e-05 | 2.7327e-05 | 0.072277 | 0.072277 | 0.072277 | 0.98159 | -0.12863 | 0.98312 | -0.11783 | 26.7694
32 | 0.0074329 | 0.0018629 | -0.0074329 | -0.0018629 | 8.2921e-08 | 1.917e-08 | 0.011379 | 0.011379 | 0.011379 | 0.97203 | -0.197 | 0.97202 | -0.19708 | 4.2143
33 | -0.0006364 | -0.0001595 | 0.00063641 | 0.0001593 | 9.409e-09 | -1.9348e-07 | 0.00097403 | 0.00097396 | 0.00097403 | 0.97222 | -0.19563 | 0.97224 | -0.19552 | 0.36075
34 | -0.0015506 | -0.00038862 | 0.0015507 | 0.00038833 | 8.4874e-08 | -2.8669e-07 | 0.0023355 | 0.0023354 | 0.0023355 | 0.98794 | -0.084179 | 0.988 | -0.083784 | 0.865
35 | -0.030459 | -0.0076383 | 0.030476 | 0.0076446 | 1.689e-05 | 6.3313e-06 | 0.045876 | 0.045876 | 0.045876 | 0.988 | -0.083784 | 0.98856 | -0.079785 | 16.9912
36 | 0.028909 | 0.0072499 | -0.02889 | -0.0072431 | 1.8358e-05 | 6.8623e-06 | 0.043541 | 0.043541 | 0.043541 | 0.988 | -0.083784 | 0.98735 | -0.088368 | 16.1263
37 | 0.023752 | 0.0059554 | -0.023722 | -0.0059441 | 3.0579e-05 | 1.1273e-05 | 0.035797 | 0.035798 | 0.035798 | 0.98735 | -0.088368 | 0.98604 | -0.097671 | 13.2584
38 | 0.016463 | 0.0041249 | -0.016448 | -0.0041197 | 1.4722e-05 | 5.1751e-06 | 0.024843 | 0.024844 | 0.024844 | 0.98604 | -0.097671 | 0.98513 | -0.10414 | 9.2013
39 | -0.002157 | -0.00054059 | 0.0021572 | 0.00054022 | 2.4684e-07 | -3.7552e-07 | 0.0032651 | 0.003265 | 0.0032651 | 0.983 | -0.11865 | 0.98312 | -0.11783 | 1.2093
40 | 0.014438 | 0.0036159 | -0.014437 | -0.0036157 | 7.9534e-07 | 2.7178e-07 | 0.021808 | 0.021808 | 0.021808 | 0.98513 | -0.10414 | 0.98507 | -0.10454 | 8.0769
41 | 0.01174 | 0.0029397 | -0.011737 | -0.0029387 | 3.0616e-06 | 9.7898e-07 | 0.017733 | 0.017733 | 0.017733 | 0.98507 | -0.10454 | 0.98481 | -0.10643 | 6.5679
42 | 0.0070099 | 0.001754 | -0.0070092 | -0.0017538 | 7.0348e-07 | 1.427e-07 | 0.010591 | 0.010591 | 0.010591 | 0.98481 | -0.10643 | 0.9847 | -0.10715 | 3.9225
43 | 0.0036248 | 0.00090561 | -0.0036238 | -0.00090591 | 1.0162e-06 | -2.9966e-07 | 0.0054765 | 0.0054768 | 0.0054768 | 0.9847 | -0.10715 | 0.98442 | -0.10919 | 2.0284
44 | 0.0027208 | 0.00067959 | -0.0027186 | -0.00068135 | 2.1446e-06 | -1.757e-06 | 0.0041118 | 0.0041127 | 0.0041127 | 0.98442 | -0.10919 | 0.98362 | -0.1149 | 1.5232
45 | 0.048547 | 0.012276 | -0.048471 | -0.012247 | 7.6061e-05 | 2.8954e-05 | 0.072595 | 0.072595 | 0.072595 | 0.99562 | -0.030292 | 0.99401 | -0.041426 | 26.887
46 | -0.0034513 | -0.00086497 | 0.0034517 | 0.00086479 | 4.644e-07 | -1.8266e-07 | 0.0051672 | 0.0051671 | 0.0051672 | 0.99387 | -0.042399 | 0.99401 | -0.041426 | 1.9138
47 | 0.045019 | 0.011382 | -0.044505 | -0.011186 | 0.00051404 | 0.00019539 | 0.067428 | 0.067429 | 0.067429 | 0.99401 | -0.041426 | 0.98231 | -0.12342 | 24.9735
48 | 0.033611 | 0.0084561 | -0.033578 | -0.0084439 | 3.2493e-05 | 1.2243e-05 | 0.050926 | 0.050926 | 0.050926 | 0.98231 | -0.12342 | 0.98133 | -0.13035 | 18.8615
49 | -0.032762 | -0.0082371 | 0.032779 | 0.0082436 | 1.7475e-05 | 6.5779e-06 | 0.049715 | 0.049715 | 0.049715 | 0.98079 | -0.13418 | 0.98133 | -0.13035 | 18.4128
50 | 0.029746 | 0.0074811 | -0.029723 | -0.0074726 | 2.2698e-05 | 8.505e-06 | 0.045139 | 0.045139 | 0.045139 | 0.98079 | -0.13418 | 0.98001 | -0.13966 | 16.718
51 | 0.028201 | 0.0070911 | -0.028186 | -0.0070854 | 1.5449e-05 | 5.7718e-06 | 0.042828 | 0.042828 | 0.042828 | 0.98001 | -0.13966 | 0.97946 | -0.14359 | 15.8621
52 | -0.0021494 | -0.00053796 | 0.0021494 | 0.00053792 | 2.8745e-08 | -4.1459e-08 | 0.0032938 | 0.0032938 | 0.0032938 | 0.97094 | -0.20463 | 0.97095 | -0.20453 | 1.2199
53 | 0.0021494 | 0.00053796 | -0.002149 | -0.00053858 | 4.3009e-07 | -6.2008e-07 | 0.0032938 | 0.0032941 | 0.0032941 | 0.97094 | -0.20463 | 0.97074 | -0.20607 | 1.22
54 | -0.0021494 | -0.00053792 | 0.0021497 | 0.00053759 | 2.3e-07 | -3.318e-07 | 0.0032938 | 0.0032936 | 0.0032938 | 0.97095 | -0.20453 | 0.97106 | -0.20375 | 1.2199
55 | -0.0092732 | -0.0023229 | 0.0092786 | 0.0023245 | 5.3515e-06 | 1.5325e-06 | 0.01421 | 0.014209 | 0.01421 | 0.97106 | -0.20375 | 0.97164 | -0.19958 | 5.2628
56 | -0.0047585 | -0.0011924 | 0.0047594 | 0.0011924 | 8.9442e-07 | 1.0762e-08 | 0.0072935 | 0.0072934 | 0.0072935 | 0.97082 | -0.20544 | 0.97101 | -0.20408 | 2.7013
57 | 0.0047585 | 0.0011924 | -0.0047578 | -0.0011924 | 7.2905e-07 | 8.8756e-09 | 0.0072935 | 0.0072936 | 0.0072936 | 0.97082 | -0.20544 | 0.97067 | -0.20655 | 2.7013
58 | -0.007562 | -0.0018948 | 0.0075626 | 0.001895 | 6.0948e-07 | 1.4444e-07 | 0.011588 | 0.011588 | 0.011588 | 0.97101 | -0.20408 | 0.97109 | -0.2035 | 4.2919
59 | -0.022759 | -0.0057031 | 0.022848 | 0.005736 | 8.9413e-05 | 3.2923e-05 | 0.034854 | 0.034853 | 0.034854 | 0.97164 | -0.19958 | 0.97557 | -0.1713 | 12.9087
60 | 0.01348 | 0.0033787 | -0.013473 | -0.0033762 | 7.3059e-06 | 2.4699e-06 | 0.020644 | 0.020644 | 0.020644 | 0.97164 | -0.19958 | 0.97109 | -0.2035 | 7.646
61 | 0.026633 | 0.0066962 | -0.026621 | -0.0066918 | 1.1732e-05 | 4.3679e-06 | 0.040468 | 0.040468 | 0.040468 | 0.97946 | -0.14359 | 0.97902 | -0.14675 | 14.9883
62 | 0.026621 | 0.0066918 | -0.026617 | -0.0066902 | 4.1908e-06 | 1.5603e-06 | 0.040468 | 0.040468 | 0.040468 | 0.97902 | -0.14675 | 0.97886 | -0.14788 | 14.9883
63 | -0.024794 | -0.0062238 | 0.024875 | 0.0062538 | 8.0897e-05 | 2.9979e-05 | 0.037822 | 0.037821 | 0.037822 | 0.97557 | -0.1713 | 0.97886 | -0.14788 | 14.008

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22551 | 0.056728

## res_load
| p_mw | q_mvar
0 | 0.0088764 | 0.0022246
1 | 0.0056583 | 0.0014181
2 | 0.0071522 | 0.0017925
3 | 0.0056938 | 0.001427
4 | 0.0056612 | 0.0014188
5 | 0.0021157 | 0.00053026
6 | 0.014267 | 0.0035756
7 | 0.014928 | 0.0037412
8 | 0.004532 | 0.0011358
9 | 0.001798 | 0.00045062
10 | 0.0038669 | 0.00096913
11 | 0.0038486 | 0.00096455
12 | 0.0035215 | 0.00088258
13 | 0.0071375 | 0.0017888
14 | 0.0028772 | 0.0007211
15 | 0.003499 | 0.00087694
16 | 0.0029252 | 0.00073313
17 | 0.0020299 | 0.00050874
18 | 0.01061 | 0.0026591
19 | 0.0014991 | 0.0003757
20 | 0.007142 | 0.00179
21 | 0.0013188 | 0.00033052
22 | 0.0006364 | 0.0001595
23 | 0.00027826 | 6.9739e-05
24 | 0.0015506 | 0.00038862
25 | 0.0072228 | 0.0018102
26 | 0.0051381 | 0.0012877
27 | 0.0072588 | 0.0018192
28 | 0.002157 | 0.00054059
29 | 0.0020099 | 0.00050373
30 | 0.0026973 | 0.00067601
31 | 0.0047271 | 0.0011847
32 | 0.0033844 | 0.00084822
33 | 0.00090302 | 0.00022632
34 | 0.0027186 | 0.00068135
35 | 0.0046565 | 0.001167
36 | 0.0034513 | 0.00086497
37 | 0.010894 | 0.0027303
38 | 0.0030162 | 0.00075593
39 | 0.00079903 | 0.00020026
40 | 0.0015221 | 0.00038146
41 | 0.002149 | 0.00053858
42 | 0.0071236 | 0.0017853
43 | 0.0028026 | 0.0007024
44 | 0.0047578 | 0.0011924
45 | 0.0074329 | 0.0018629
46 | 0.001553 | 0.00038921
47 | 0.0019462 | 0.00048777
48 | 0.0059101 | 0.0014812
49 | 0.0017415 | 0.00043645

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1