## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1085-11_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1085-11_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1085-11_0_2_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1085-11_0_2_node_9 | 0.4 | n |  | TRUE
4 | bus_LV_1085-11_0_2_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_1085-11_0_2_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1085-11_0_2_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1085-11_0_2_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1085-11_0_2_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1085-11_0_2_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_1085-11_0_2_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_1085-11_0_2_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_1085-11_0_2_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_1085-11_0_2_node_25 | 0.4 | n |  | TRUE
14 | bus_LV_1085-11_0_2_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_1085-11_0_2_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1085-11_0_2_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_1085-11_0_2_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_1085-11_0_2_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_1085-11_0_2_node_28 | 0.4 | n |  | TRUE
20 | bus_LV_1085-11_0_2_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_1085-11_0_2_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_1085-11_0_2_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_1085-11_0_2_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_1085-11_0_2_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1085-11_0_2_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1085-11_0_2_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1085-11_0_2_node_24 | 0.4 | n |  | TRUE
28 | bus_MV_473_0_node_191 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1085-11_0_2_load_0 | 0 | 0.0081262 | 0.0020366 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1085-11_0_2_load_1 | 1 | 0.0075542 | 0.0018933 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1085-11_0_2_load_7 | 4 | 0.0072363 | 0.0018136 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1085-11_0_2_load_4 | 5 | 0.0081358 | 0.002039 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1085-11_0_2_load_5 | 6 | 0.0038891 | 0.00097469 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1085-11_0_2_load_6 | 7 | 0.0033386 | 0.00083672 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1085-11_0_2_load_11 | 10 | 0.0074498 | 0.0018671 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1085-11_0_2_load_12 | 12 | 0.010769 | 0.0026989 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1085-11_0_2_load_30 | 14 | 0.010916 | 0.0027359 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1085-11_0_2_load_26 | 18 | 0.0018032 | 0.00045191 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1085-11_0_2_load_28 | 19 | 0.0063939 | 0.0016025 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1085-11_0_2_load_31 | 20 | 0.010904 | 0.0027328 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1085-11_0_2_load_17 | 22 | 0.01215 | 0.003045 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1085-11_0_2_load_18 | 23 | 0.01091 | 0.0027342 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1085-11_0_2_load_21 | 25 | 0.010959 | 0.0027467 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1085-11_0_2_load_22 | 26 | 0.010813 | 0.0027101 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1085-11_0_2_load_24 | 27 | 0.010804 | 0.0027077 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1085-11_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.012388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1085-11_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.033616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1085-11_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.018277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1085-11_0_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.022077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1085-11_0_2_line_4 | NAYY 4x150 SE | 4 | 6 | 0.044433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1085-11_0_2_line_5 | NAYY 4x150 SE | 5 | 6 | 0.019635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1085-11_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.019176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1085-11_0_2_line_7 | NAYY 4x150 SE | 7 | 8 | 0.025351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1085-11_0_2_line_8 | NAYY 4x150 SE | 8 | 9 | 0.051376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1085-11_0_2_line_9 | NAYY 4x150 SE | 8 | 10 | 0.029896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1085-11_0_2_line_10 | NAYY 4x150 SE | 9 | 11 | 0.021286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1085-11_0_2_line_11 | NAYY 4x150 SE | 9 | 12 | 0.01921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1085-11_0_2_line_12 | NAYY 4x150 SE | 11 | 13 | 0.021166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1085-11_0_2_line_13 | NAYY 4x150 SE | 11 | 14 | 0.007877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1085-11_0_2_line_14 | NAYY 4x150 SE | 12 | 15 | 0.015368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1085-11_0_2_line_15 | NAYY 4x150 SE | 13 | 20 | 0.007847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1085-11_0_2_line_16 | NAYY 4x150 SE | 13 | 21 | 0.008927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1085-11_0_2_line_17 | NAYY 4x150 SE | 15 | 16 | 0.023137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1085-11_0_2_line_18 | NAYY 4x150 SE | 15 | 17 | 0.069363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1085-11_0_2_line_19 | NAYY 4x150 SE | 16 | 18 | 0.014458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1085-11_0_2_line_20 | NAYY 4x150 SE | 17 | 19 | 0.015782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1085-11_0_2_line_21 | NAYY 4x150 SE | 21 | 27 | 0.007799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_1085-11_0_2_line_22 | NAYY 4x150 SE | 21 | 25 | 0.017556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1085-11_0_2_line_23 | NAYY 4x150 SE | 22 | 23 | 0.019424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1085-11_0_2_line_24 | NAYY 4x150 SE | 23 | 24 | 0.01165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1085-11_0_2_line_25 | NAYY 4x150 SE | 24 | 25 | 0.015223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1085-11_0_2_line_26 | NAYY 4x150 SE | 24 | 26 | 0.007481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1085-11_0_2_trafo_24 | 0.25 MVA 20/0.4 kV | 28 | 27 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2650496.3003 | 1228075.3345 | 2650497.1171 | 1228075.5914 | 2650507.6135 | 1228080.3679
1 | 2650538.0318 | 1228094.6617 | 2650530.0799 | 1228090.5916 | 2650507.6135 | 1228080.3679
2 | 2650554.0593 | 1228090.9288 | 2650549.8154 | 1228089.2139 | 2650545.2302 | 1228089.3195 | 2650541.069 | 1228091.252 | 2650538.0318 | 1228094.6617
3 | 2650554.0593 | 1228090.9288 | 2650558.1708 | 1228084.1372 | 2650565.0071 | 1228071.7624
4 | 2650565.0071 | 1228071.7624 | 2650586.4926 | 1228032.8697
5 | 2650595.9873 | 1228015.6826 | 2650586.4926 | 1228032.8697
6 | 2650595.9873 | 1228015.6826 | 2650597.8581 | 1228012.2961 | 2650604.9599 | 1227998.7361
7 | 2650616.7217 | 1227976.2784 | 2650604.9599 | 1227998.7361
8 | 2650616.7217 | 1227976.2784 | 2650659.3402 | 1227999.9669 | 2650661.1413 | 1228002.0168
9 | 2650616.7217 | 1227976.2784 | 2650629.0018 | 1227949.0213
10 | 2650661.1413 | 1228002.0168 | 2650661.9224 | 1228004.614 | 2650661.0876 | 1228007.442 | 2650652.7459 | 1228020.6682
11 | 2650661.1413 | 1228002.0168 | 2650666.7841 | 1228004.0772 | 2650678.1703 | 1228010.7608
12 | 2650652.7459 | 1228020.6682 | 2650641.447 | 1228038.5832
13 | 2650646.4823 | 1228015.8674 | 2650652.7459 | 1228020.6682
14 | 2650691.4239 | 1228018.5405 | 2650678.1703 | 1228010.7608
15 | 2650641.447 | 1228038.5832 | 2650648.1482 | 1228042.6984
16 | 2650641.447 | 1228038.5832 | 2650636.6771 | 1228046.1363
17 | 2650700.0923 | 1227997.2232 | 2650695.0201 | 1228006.4525 | 2650691.4239 | 1228018.5405
18 | 2650691.4239 | 1228018.5405 | 2650690.8467 | 1228020.4813 | 2650690.2895 | 1228037.8541 | 2650694.003 | 1228068.9051 | 2650695.0894 | 1228073.017 | 2650695.8168 | 1228083.6854 | 2650695.641 | 1228087.4196
19 | 2650700.0923 | 1227997.2232 | 2650702.7786 | 1227992.3208 | 2650708.2846 | 1227985.3696
20 | 2650695.641 | 1228087.4196 | 2650686.2167 | 1228088.0953 | 2650680.5036 | 1228090.8294
21 | 2650629.8367 | 1228042.3535 | 2650636.6771 | 1228046.1363
22 | 2650636.6771 | 1228046.1363 | 2650627.31 | 1228060.985
23 | 2650602.6098 | 1228100.1427 | 2650612.9722 | 1228083.7142
24 | 2650619.1876 | 1228073.8604 | 2650612.9722 | 1228083.7142
25 | 2650619.1876 | 1228073.8604 | 2650627.31 | 1228060.985
26 | 2650612.9335 | 1228069.7269 | 2650619.1876 | 1228073.8604

## bus_geodata
| x | y | coords
0 | 2650496.3003 | 1228075.3345
1 | 2650507.6135 | 1228080.3679
2 | 2650538.0318 | 1228094.6617
3 | 2650554.0593 | 1228090.9288
4 | 2650565.0071 | 1228071.7624
5 | 2650595.9873 | 1228015.6826
6 | 2650586.4926 | 1228032.8697
7 | 2650604.9599 | 1227998.7361
8 | 2650616.7217 | 1227976.2784
9 | 2650661.1413 | 1228002.0168
10 | 2650629.0018 | 1227949.0213
11 | 2650652.7459 | 1228020.6682
12 | 2650678.1703 | 1228010.7608
13 | 2650641.447 | 1228038.5832
14 | 2650646.4823 | 1228015.8674
15 | 2650691.4239 | 1228018.5405
16 | 2650700.0923 | 1227997.2232
17 | 2650695.641 | 1228087.4196
18 | 2650708.2846 | 1227985.3696
19 | 2650680.5036 | 1228090.8294
20 | 2650648.1482 | 1228042.6984
21 | 2650636.6771 | 1228046.1363
22 | 2650602.6098 | 1228100.1427
23 | 2650612.9722 | 1228083.7142
24 | 2650619.1876 | 1228073.8604
25 | 2650627.31 | 1228060.985
26 | 2650612.9335 | 1228069.7269
27 | 2650629.8367 | 1228042.3535
28 | 2650636.6771 | 1228046.1363

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98404 | -0.1122 | 0.0081262 | 0.0020366
1 | 0.98418 | -0.11116 | 0.0075542 | 0.0018933
2 | 0.98494 | -0.10573 | 0 | 0
3 | 0.98536 | -0.10278 | 0 | 0
4 | 0.98586 | -0.099226 | 0.0072363 | 0.0018136
5 | 0.9881 | -0.083393 | 0.0081358 | 0.002039
6 | 0.98734 | -0.08878 | 0.0038891 | 0.00097469
7 | 0.98907 | -0.076548 | 0.0033386 | 0.00083672
8 | 0.99047 | -0.066656 | 0 | 0
9 | 0.99386 | -0.042824 | 0 | 0
10 | 0.99015 | -0.068923 | 0.0074498 | 0.0018671
11 | 0.99585 | -0.028929 | 0 | 0
12 | 0.99334 | -0.04651 | 0.010769 | 0.0026989
13 | 0.99815 | -0.01285 | 0 | 0
14 | 0.99572 | -0.029794 | 0.010916 | 0.0027359
15 | 0.99316 | -0.047786 | 0 | 0
16 | 0.9931 | -0.048209 | 0 | 0
17 | 0.99252 | -0.05228 | 0 | 0
18 | 0.99306 | -0.048473 | 0.0018032 | 0.00045191
19 | 0.99238 | -0.053303 | 0.0063939 | 0.0016025
20 | 0.99803 | -0.013707 | 0.010904 | 0.0027328
21 | 0.99926 | -0.0051178 | 0 | 0
22 | 0.99668 | -0.023232 | 0.01215 | 0.003045
23 | 0.99702 | -0.020861 | 0.01091 | 0.0027342
24 | 0.9974 | -0.018165 | 0 | 0
25 | 0.99814 | -0.012995 | 0.010959 | 0.0027467
26 | 0.99729 | -0.018977 | 0.010813 | 0.0027101
27 | 1 | 0 | -0.13306 | -0.033262
28 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0081262 | -0.0020366 | 0.0081274 | 0.0020369 | 1.1673e-06 | 2.9154e-07 | 0.012288 | 0.012288 | 0.012288 | 0.98404 | -0.1122 | 0.98418 | -0.11116 | 4.5512
1 | -0.015682 | -0.0039302 | 0.015693 | 0.0039343 | 1.1792e-05 | 4.1078e-06 | 0.023709 | 0.023709 | 0.023709 | 0.98418 | -0.11116 | 0.98494 | -0.10573 | 8.7813
2 | -0.015693 | -0.0039343 | 0.0157 | 0.0039365 | 6.411e-06 | 2.2331e-06 | 0.023709 | 0.023709 | 0.023709 | 0.98494 | -0.10573 | 0.98536 | -0.10278 | 8.7812
3 | -0.0157 | -0.0039365 | 0.015708 | 0.0039392 | 7.7438e-06 | 2.697e-06 | 0.023709 | 0.023709 | 0.023709 | 0.98536 | -0.10278 | 0.98586 | -0.099226 | 8.7812
4 | -0.022944 | -0.0057528 | 0.022977 | 0.005765 | 3.3252e-05 | 1.2222e-05 | 0.034631 | 0.034631 | 0.034631 | 0.98586 | -0.099226 | 0.98734 | -0.08878 | 12.8264
5 | 0.026886 | 0.0067472 | -0.026866 | -0.0067397 | 2.0089e-05 | 7.4754e-06 | 0.040492 | 0.040492 | 0.040492 | 0.9881 | -0.083393 | 0.98734 | -0.08878 | 14.9972
6 | -0.035022 | -0.0087862 | 0.035055 | 0.0087988 | 3.3289e-05 | 1.2557e-05 | 0.052744 | 0.052744 | 0.052744 | 0.9881 | -0.083393 | 0.98907 | -0.076548 | 19.5349
7 | -0.038394 | -0.0096355 | 0.038447 | 0.0096555 | 5.2789e-05 | 1.9978e-05 | 0.057767 | 0.057767 | 0.057767 | 0.98907 | -0.076548 | 0.99047 | -0.066656 | 21.3952
8 | -0.045899 | -0.011523 | 0.046051 | 0.011581 | 0.00015246 | 5.7977e-05 | 0.068962 | 0.068962 | 0.068962 | 0.99047 | -0.066656 | 0.99386 | -0.042824 | 25.5417
9 | 0.0074522 | 0.0018676 | -0.0074498 | -0.0018671 | 2.3383e-06 | 5.147e-07 | 0.011196 | 0.011196 | 0.011196 | 0.99047 | -0.066656 | 0.99015 | -0.068923 | 4.1466
10 | -0.065033 | -0.016338 | 0.065159 | 0.016387 | 0.00012596 | 4.817e-05 | 0.097382 | 0.097382 | 0.097382 | 0.99386 | -0.042824 | 0.99585 | -0.028929 | 36.0674
11 | 0.018982 | 0.0047574 | -0.018972 | -0.004754 | 9.6818e-06 | 3.4749e-06 | 0.02842 | 0.02842 | 0.02842 | 0.99386 | -0.042824 | 0.99334 | -0.04651 | 10.5259
12 | -0.076077 | -0.019123 | 0.076248 | 0.019188 | 0.00017073 | 6.5389e-05 | 0.1137 | 0.1137 | 0.1137 | 0.99585 | -0.028929 | 0.99815 | -0.01285 | 42.1094
13 | 0.010918 | 0.0027363 | -0.010916 | -0.0027359 | 1.3081e-06 | 4.0064e-07 | 0.016313 | 0.016314 | 0.016314 | 0.99585 | -0.028929 | 0.99572 | -0.029794 | 6.042
14 | 0.0082036 | 0.0020551 | -0.0082021 | -0.0020547 | 1.4482e-06 | 3.5808e-07 | 0.012289 | 0.012289 | 0.012289 | 0.99334 | -0.04651 | 0.99316 | -0.047786 | 4.5514
15 | 0.010905 | 0.0027332 | -0.010904 | -0.0027328 | 1.2942e-06 | 3.952e-07 | 0.016257 | 0.016257 | 0.016257 | 0.99815 | -0.01285 | 0.99803 | -0.013707 | 6.0213
16 | -0.087153 | -0.021922 | 0.087247 | 0.021958 | 9.4072e-05 | 3.6065e-05 | 0.12995 | 0.12995 | 0.12995 | 0.99815 | -0.01285 | 0.99926 | -0.0051178 | 48.1306
17 | 0.0018033 | 0.00045149 | -0.0018032 | -0.00045175 | 1.0539e-07 | -2.5885e-07 | 0.0027017 | 0.0027018 | 0.0027018 | 0.99316 | -0.047786 | 0.9931 | -0.048209 | 1.0007
18 | 0.0063988 | 0.0016032 | -0.0063948 | -0.0016026 | 3.9782e-06 | 6.3308e-07 | 0.009587 | 0.0095873 | 0.0095873 | 0.99316 | -0.047786 | 0.99252 | -0.05228 | 3.5508
19 | 0.0018032 | 0.00045175 | -0.0018032 | -0.00045191 | 6.5857e-08 | -1.6173e-07 | 0.0027018 | 0.0027019 | 0.0027019 | 0.9931 | -0.048209 | 0.99306 | -0.048473 | 1.0007
20 | 0.0063948 | 0.0016026 | -0.0063939 | -0.0016025 | 9.052e-07 | 1.4422e-07 | 0.0095873 | 0.0095873 | 0.0095873 | 0.99252 | -0.05228 | 0.99238 | -0.053303 | 3.5509
21 | -0.13217 | -0.033226 | 0.13226 | 0.033262 | 9.4286e-05 | 3.6059e-05 | 0.19685 | 0.19685 | 0.19685 | 0.99926 | -0.0051178 | 1 | 0 | 36.453
22 | 0.044919 | 0.011269 | -0.04487 | -0.01125 | 4.9022e-05 | 1.8625e-05 | 0.066894 | 0.066894 | 0.066894 | 0.99926 | -0.0051178 | 0.99814 | -0.012995 | 24.7754
23 | -0.01215 | -0.003045 | 0.012154 | 0.0030463 | 3.988e-06 | 1.2806e-06 | 0.018139 | 0.018139 | 0.018139 | 0.99668 | -0.023232 | 0.99702 | -0.020861 | 6.7183
24 | -0.023063 | -0.0057805 | 0.023072 | 0.0057837 | 8.6134e-06 | 3.1609e-06 | 0.034421 | 0.034421 | 0.034421 | 0.99702 | -0.020861 | 0.9974 | -0.018165 | 12.7487
25 | -0.033887 | -0.0084941 | 0.033911 | 0.0085033 | 2.4279e-05 | 9.1393e-06 | 0.050556 | 0.050555 | 0.050556 | 0.9974 | -0.018165 | 0.99814 | -0.012995 | 18.7243
26 | 0.010815 | 0.0027104 | -0.010813 | -0.0027101 | 1.2152e-06 | 3.6975e-07 | 0.016134 | 0.016134 | 0.016134 | 0.9974 | -0.018165 | 0.99729 | -0.018977 | 5.9756

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.14386 | 0.03597

## res_load
| p_mw | q_mvar
0 | 0.0081262 | 0.0020366
1 | 0.0075542 | 0.0018933
2 | 0.0072363 | 0.0018136
3 | 0.0081358 | 0.002039
4 | 0.0038891 | 0.00097469
5 | 0.0033386 | 0.00083672
6 | 0.0074498 | 0.0018671
7 | 0.010769 | 0.0026989
8 | 0.010916 | 0.0027359
9 | 0.0018032 | 0.00045191
10 | 0.0063939 | 0.0016025
11 | 0.010904 | 0.0027328
12 | 0.01215 | 0.003045
13 | 0.01091 | 0.0027342
14 | 0.010959 | 0.0027467
15 | 0.010813 | 0.0027101
16 | 0.010804 | 0.0027077

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1