## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1089-11_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1089-11_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1089-11_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1089-11_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1089-11_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1089-11_0_3_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_1089-11_0_3_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_1089-11_0_3_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_1089-11_0_3_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_1089-11_0_3_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_1089-11_0_3_node_22 | 0.4 | n |  | TRUE
11 | bus_LV_1089-11_0_3_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1089-11_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1089-11_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1089-11_0_3_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_1089-11_0_3_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_1089-11_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1089-11_0_3_node_50 | 0.4 | n |  | TRUE
18 | bus_LV_1089-11_0_3_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1089-11_0_3_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1089-11_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1089-11_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1089-11_0_3_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_1089-11_0_3_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_1089-11_0_3_node_31 | 0.4 | n |  | TRUE
25 | bus_LV_1089-11_0_3_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_1089-11_0_3_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_1089-11_0_3_node_48 | 0.4 | n |  | TRUE
28 | bus_LV_1089-11_0_3_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_1089-11_0_3_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_1089-11_0_3_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_1089-11_0_3_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_1089-11_0_3_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_1089-11_0_3_node_49 | 0.4 | n |  | TRUE
34 | bus_LV_1089-11_0_3_node_44 | 0.4 | n |  | TRUE
35 | bus_LV_1089-11_0_3_node_51 | 0.4 | n |  | TRUE
36 | bus_LV_1089-11_0_3_node_43 | 0.4 | n |  | TRUE
37 | bus_LV_1089-11_0_3_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_1089-11_0_3_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_1089-11_0_3_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_1089-11_0_3_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_1089-11_0_3_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_1089-11_0_3_node_40 | 0.4 | n |  | TRUE
43 | bus_LV_1089-11_0_3_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_1089-11_0_3_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_1089-11_0_3_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_1089-11_0_3_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_1089-11_0_3_node_38 | 0.4 | n |  | TRUE
48 | bus_LV_1089-11_0_3_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_1089-11_0_3_node_46 | 0.4 | n |  | TRUE
50 | bus_MV_473_0_node_39 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1089-11_0_3_load_0 | 0 | 0.0054205 | 0.0013585 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1089-11_0_3_load_1 | 1 | 0.0033055 | 0.00082845 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1089-11_0_3_load_2 | 2 | 0.0064701 | 0.0016216 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1089-11_0_3_load_3 | 3 | 0.0017817 | 0.00044654 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1089-11_0_3_load_4 | 4 | 0.0062763 | 0.001573 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1089-11_0_3_load_9 | 5 | 0.0021536 | 0.00053975 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1089-11_0_3_load_10 | 7 | 0.0008461 | 0.00021205 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1089-11_0_3_load_19 | 9 | 0.02408 | 0.0060351 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1089-11_0_3_load_22 | 10 | 0.0012975 | 0.00032518 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1089-11_0_3_load_5 | 11 | 0.0027393 | 0.00068654 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1089-11_0_3_load_6 | 12 | 0.0040535 | 0.0010159 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1089-11_0_3_load_20 | 14 | 0.0084644 | 0.0021214 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1089-11_0_3_load_18 | 15 | 0.0033414 | 0.00083742 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1089-11_0_3_load_11 | 16 | 0.0070101 | 0.0017569 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1089-11_0_3_load_50 | 17 | 0.0032328 | 0.00081022 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1089-11_0_3_load_12 | 18 | 0.0014116 | 0.00035379 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1089-11_0_3_load_13 | 19 | 0.0037946 | 0.00095102 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1089-11_0_3_load_14 | 20 | 0.0014132 | 0.00035418 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1089-11_0_3_load_15 | 21 | 0.0033457 | 0.00083851 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1089-11_0_3_load_23 | 23 | 0.00092157 | 0.00023097 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1089-11_0_3_load_31 | 24 | 0.010816 | 0.0027107 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1089-11_0_3_load_30 | 25 | 0.0042526 | 0.0010658 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1089-11_0_3_load_17 | 26 | 0.0019677 | 0.00049316 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1089-11_0_3_load_48 | 27 | 0.0068587 | 0.0017189 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1089-11_0_3_load_28 | 28 | 0.0047623 | 0.0011935 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1089-11_0_3_load_25 | 29 | 0.0081346 | 0.0020387 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1089-11_0_3_load_26 | 30 | 0.010001 | 0.0025066 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1089-11_0_3_load_44 | 34 | 0.0066793 | 0.001674 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1089-11_0_3_load_51 | 35 | 0.0018524 | 0.00046424 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1089-11_0_3_load_43 | 36 | 0.0038189 | 0.00095711 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1089-11_0_3_load_32 | 37 | 0.00094377 | 0.00023653 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1089-11_0_3_load_33 | 38 | 0.0021788 | 0.00054605 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1089-11_0_3_load_34 | 39 | 0.0053662 | 0.0013449 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1089-11_0_3_load_35 | 40 | 0.0027061 | 0.00067821 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1089-11_0_3_load_36 | 41 | 0.0034569 | 0.00086638 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1089-11_0_3_load_41 | 43 | 0.0049307 | 0.0012358 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1089-11_0_3_load_42 | 45 | 0.0044861 | 0.0011243 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1089-11_0_3_load_37 | 46 | 0.00077408 | 0.000194 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1089-11_0_3_load_38 | 47 | 0.00090197 | 0.00022606 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1089-11_0_3_load_45 | 48 | 0.0031729 | 0.0007952 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1089-11_0_3_load_46 | 49 | 0.0039688 | 0.00099467 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1089-11_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.025553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1089-11_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.024702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1089-11_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.033162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1089-11_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0071908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1089-11_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0051417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1089-11_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.027443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1089-11_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.032652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1089-11_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.030451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1089-11_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.018691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1089-11_0_3_line_9 | NAYY 4x150 SE | 6 | 10 | 0.012594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1089-11_0_3_line_10 | NAYY 4x150 SE | 7 | 16 | 0.0073854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1089-11_0_3_line_11 | NAYY 4x150 SE | 8 | 24 | 0.04121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_1089-11_0_3_line_12 | NAYY 4x150 SE | 8 | 25 | 0.0054624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1089-11_0_3_line_13 | NAYY 4x150 SE | 9 | 26 | 0.043369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1089-11_0_3_line_14 | NAYY 4x150 SE | 10 | 22 | 0.031862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1089-11_0_3_line_15 | NAYY 4x150 SE | 11 | 12 | 0.017419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1089-11_0_3_line_16 | NAYY 4x150 SE | 12 | 13 | 0.014062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1089-11_0_3_line_17 | NAYY 4x150 SE | 13 | 14 | 0.033833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1089-11_0_3_line_18 | NAYY 4x150 SE | 14 | 15 | 0.0037831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1089-11_0_3_line_19 | NAYY 4x150 SE | 15 | 26 | 0.02368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1089-11_0_3_line_20 | NAYY 4x150 SE | 16 | 17 | 0.12292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1089-11_0_3_line_21 | NAYY 4x150 SE | 18 | 19 | 0.01141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1089-11_0_3_line_22 | NAYY 4x150 SE | 18 | 20 | 0.024904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1089-11_0_3_line_23 | NAYY 4x150 SE | 19 | 21 | 0.02352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1089-11_0_3_line_24 | NAYY 4x150 SE | 21 | 22 | 0.012575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1089-11_0_3_line_25 | NAYY 4x150 SE | 22 | 23 | 0.010237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1089-11_0_3_line_26 | NAYY 4x150 SE | 24 | 27 | 0.012316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1089-11_0_3_line_27 | NAYY 4x150 SE | 25 | 28 | 0.0091637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1089-11_0_3_line_28 | NAYY 4x150 SE | 28 | 30 | 0.011892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1089-11_0_3_line_29 | NAYY 4x150 SE | 29 | 30 | 0.012798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1089-11_0_3_line_30 | NAYY 4x150 SE | 29 | 31 | 0.015309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1089-11_0_3_line_31 | NAYY 4x150 SE | 31 | 32 | 0.029164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1089-11_0_3_line_32 | NAYY 4x150 SE | 32 | 33 | 0.025979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1089-11_0_3_line_33 | NAYY 4x150 SE | 32 | 34 | 0.049104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1089-11_0_3_line_34 | NAYY 4x150 SE | 33 | 35 | 0.03112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1089-11_0_3_line_35 | NAYY 4x150 SE | 34 | 36 | 0.011914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1089-11_0_3_line_36 | NAYY 4x150 SE | 36 | 45 | 0.013967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1089-11_0_3_line_37 | NAYY 4x150 SE | 37 | 38 | 0.043174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1089-11_0_3_line_38 | NAYY 4x150 SE | 37 | 39 | 0.011206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1089-11_0_3_line_39 | NAYY 4x150 SE | 38 | 40 | 0.021168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1089-11_0_3_line_40 | NAYY 4x150 SE | 39 | 41 | 0.012828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1089-11_0_3_line_41 | NAYY 4x150 SE | 40 | 42 | 0.057683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1089-11_0_3_line_42 | NAYY 4x150 SE | 41 | 43 | 0.033868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1089-11_0_3_line_43 | NAYY 4x150 SE | 42 | 44 | 0.057533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1089-11_0_3_line_44 | NAYY 4x150 SE | 43 | 45 | 0.010933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1089-11_0_3_line_45 | NAYY 4x150 SE | 44 | 46 | 0.043468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1089-11_0_3_line_46 | NAYY 4x150 SE | 45 | 48 | 0.066331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1089-11_0_3_line_47 | NAYY 4x150 SE | 46 | 47 | 0.0044224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1089-11_0_3_line_48 | NAYY 4x150 SE | 48 | 49 | 0.014466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1089-11_0_3_trafo_31 | 0.25 MVA 20/0.4 kV | 50 | 24 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2647963.7768 | 1227763.776 | 2647962.4368 | 1227755.4086 | 2647959.1632 | 1227738.6462
1 | 2647963.7768 | 1227763.776 | 2647967.2272 | 1227785.3213 | 2647968.2505 | 1227788.0158
2 | 2647959.1632 | 1227738.6462 | 2647957.9612 | 1227732.4916 | 2647949.2465 | 1227707.0521
3 | 2647970.8034 | 1227794.7382 | 2647968.2505 | 1227788.0158
4 | 2647947.5802 | 1227702.1879 | 2647949.2465 | 1227707.0521
5 | 2647986.089 | 1227817.1376 | 2647979.3242 | 1227810.3121 | 2647972.8516 | 1227800.1314 | 2647970.8034 | 1227794.7382
6 | 2647947.5802 | 1227702.1879 | 2647947.4852 | 1227701.9105 | 2647941.3795 | 1227684.7395 | 2647939.0987 | 1227676.2492 | 2647937.7109 | 1227671.089
7 | 2647986.089 | 1227817.1376 | 2647993.4063 | 1227822.1664 | 2648000.8979 | 1227828.1305 | 2648004.9525 | 1227832.7549 | 2648008.1482 | 1227837.706
8 | 2647986.089 | 1227817.1376 | 2647992.8737 | 1227809.2763 | 2647997.6374 | 1227802.4708
9 | 2647986.089 | 1227817.1376 | 2647981.8289 | 1227822.0174 | 2647979.3254 | 1227827.0781 | 2647979.1171 | 1227827.4997
10 | 2647935.7927 | 1227663.957 | 2647937.7109 | 1227671.089
11 | 2648008.1482 | 1227837.706 | 2648015.8758 | 1227834.1328 | 2648020.2452 | 1227829.7986 | 2648031.7441 | 1227805.8765
12 | 2648008.1482 | 1227837.706 | 2648010.3802 | 1227842.6915
13 | 2647997.6374 | 1227802.4708 | 2648001.0303 | 1227797.6237 | 2648019.3524 | 1227773.3007 | 2648023.3047 | 1227767.5228
14 | 2647966.5307 | 1227856.6712 | 2647969.4805 | 1227847.0112 | 2647971.6837 | 1227842.5484 | 2647979.1171 | 1227827.4997
15 | 2648035.4175 | 1227682.6637 | 2648041.0097 | 1227699.1608
16 | 2648047.2122 | 1227711.765 | 2648041.4978 | 1227700.6009 | 2648041.0097 | 1227699.1608
17 | 2648047.2122 | 1227711.765 | 2648041.814 | 1227720.5714 | 2648039.1772 | 1227730.8565 | 2648036.5656 | 1227742.7206 | 2648036.2808 | 1227743.4008
18 | 2648034.8197 | 1227746.8903 | 2648036.2808 | 1227743.4008
19 | 2648034.8197 | 1227746.8903 | 2648032.571 | 1227752.261 | 2648024.3367 | 1227766.0142 | 2648023.3047 | 1227767.5228
20 | 2647935.7927 | 1227663.957 | 2647820.2152 | 1227622.1068
21 | 2647932.9197 | 1227868.4165 | 2647922.678 | 1227873.4458
22 | 2647900.3425 | 1227884.4617 | 2647907.61 | 1227880.8451 | 2647922.678 | 1227873.4458
23 | 2647932.9197 | 1227868.4165 | 2647954.0318 | 1227858.0492
24 | 2647966.5307 | 1227856.6712 | 2647954.0318 | 1227858.0492 | 2647954.0318 | 1227858.0492
25 | 2647966.5307 | 1227856.6712 | 2647963.7824 | 1227866.5325
26 | 2648034.9015 | 1227793.9724 | 2648031.7441 | 1227805.8765
27 | 2648010.3802 | 1227842.6915 | 2648010.7459 | 1227843.5083 | 2648013.7356 | 1227851.2177
28 | 2648018.0351 | 1227862.3048 | 2648013.7356 | 1227851.2177
29 | 2648022.6625 | 1227874.2373 | 2648018.0351 | 1227862.3048
30 | 2648028.1975 | 1227888.5104 | 2648022.6625 | 1227874.2373
31 | 2648028.1975 | 1227888.5104 | 2648033.8728 | 1227902.6205 | 2648039.0952 | 1227915.5707
32 | 2648050.3709 | 1227938.9874 | 2648039.0952 | 1227915.5707
33 | 2648039.0952 | 1227915.5707 | 2648041.621 | 1227914.3237 | 2648046.9438 | 1227910.1529 | 2648052.7765 | 1227904.7633 | 2648072.1394 | 1227882.906 | 2648073.5414 | 1227880.9788
34 | 2648078.5534 | 1227925.6177 | 2648050.3709 | 1227938.9874
35 | 2648073.5414 | 1227880.9788 | 2648080.5499 | 1227871.3448
36 | 2648087.9414 | 1227859.5494 | 2648085.3345 | 1227864.768 | 2648080.5499 | 1227871.3448
37 | 2648105.5153 | 1227793.5023 | 2648112.0576 | 1227750.8273
38 | 2648105.5153 | 1227793.5023 | 2648103.8172 | 1227804.5789
39 | 2648115.2653 | 1227729.9037 | 2648115.2653 | 1227729.9037 | 2648112.0576 | 1227750.8273
40 | 2648101.8734 | 1227817.2584 | 2648103.8172 | 1227804.5789
41 | 2648136.541 | 1227680.5783 | 2648133.3044 | 1227680.6856 | 2648130.9971 | 1227681.1339 | 2648127.9532 | 1227683.6553 | 2648125.3983 | 1227688.4821 | 2648123.3513 | 1227694.2358 | 2648121.6156 | 1227701.7709 | 2648115.2653 | 1227729.9037
42 | 2648101.8734 | 1227817.2584 | 2648101.33 | 1227820.8032 | 2648095.0701 | 1227845.2789 | 2648092.8273 | 1227849.7685
43 | 2648136.541 | 1227680.5783 | 2648138.3685 | 1227701.962 | 2648142.2233 | 1227737.8266
44 | 2648092.8273 | 1227849.7685 | 2648087.9414 | 1227859.5494
45 | 2648142.2233 | 1227737.8266 | 2648148.2998 | 1227737.9313 | 2648150.7225 | 1227740.0745 | 2648154.1853 | 1227751.3428 | 2648156.4938 | 1227755.4196 | 2648160.3104 | 1227760.4091 | 2648169.4108 | 1227767.2758
46 | 2648087.9414 | 1227859.5494 | 2648149.4138 | 1227884.4669
47 | 2648172.941 | 1227769.9395 | 2648169.4108 | 1227767.2758
48 | 2648149.4138 | 1227884.4669 | 2648148.5988 | 1227885.4477 | 2648144.9813 | 1227898.1322

## bus_geodata
| x | y | coords
0 | 2647963.7768 | 1227763.776
1 | 2647959.1632 | 1227738.6462
2 | 2647968.2505 | 1227788.0158
3 | 2647949.2465 | 1227707.0521
4 | 2647970.8034 | 1227794.7382
5 | 2647947.5802 | 1227702.1879
6 | 2647986.089 | 1227817.1376
7 | 2647937.7109 | 1227671.089
8 | 2648008.1482 | 1227837.706
9 | 2647997.6374 | 1227802.4708
10 | 2647979.1171 | 1227827.4997
11 | 2648035.4175 | 1227682.6637
12 | 2648041.0097 | 1227699.1608
13 | 2648047.2122 | 1227711.765
14 | 2648036.2808 | 1227743.4008
15 | 2648034.8197 | 1227746.8903
16 | 2647935.7927 | 1227663.957
17 | 2647820.2152 | 1227622.1068
18 | 2647922.678 | 1227873.4458
19 | 2647932.9197 | 1227868.4165
20 | 2647900.3425 | 1227884.4617
21 | 2647954.0318 | 1227858.0492
22 | 2647966.5307 | 1227856.6712
23 | 2647963.7824 | 1227866.5325
24 | 2648031.7441 | 1227805.8765
25 | 2648010.3802 | 1227842.6915
26 | 2648023.3047 | 1227767.5228
27 | 2648034.9015 | 1227793.9724
28 | 2648013.7356 | 1227851.2177
29 | 2648022.6625 | 1227874.2373
30 | 2648018.0351 | 1227862.3048
31 | 2648028.1975 | 1227888.5104
32 | 2648039.0952 | 1227915.5707
33 | 2648050.3709 | 1227938.9874
34 | 2648073.5414 | 1227880.9788
35 | 2648078.5534 | 1227925.6177
36 | 2648080.5499 | 1227871.3448
37 | 2648105.5153 | 1227793.5023
38 | 2648112.0576 | 1227750.8273
39 | 2648103.8172 | 1227804.5789
40 | 2648115.2653 | 1227729.9037
41 | 2648101.8734 | 1227817.2584
42 | 2648136.541 | 1227680.5783
43 | 2648092.8273 | 1227849.7685
44 | 2648142.2233 | 1227737.8266
45 | 2648087.9414 | 1227859.5494
46 | 2648169.4108 | 1227767.2758
47 | 2648172.941 | 1227769.9395
48 | 2648149.4138 | 1227884.4669
49 | 2648144.9813 | 1227898.1322
50 | 2648034.9015 | 1227793.9724

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98837 | -0.081465 | 0.0054205 | 0.0013585
1 | 0.98769 | -0.086259 | 0.0033055 | 0.00082845
2 | 0.98922 | -0.075471 | 0.0064701 | 0.0016216
3 | 0.98697 | -0.091366 | 0.0017817 | 0.00044654
4 | 0.98953 | -0.073253 | 0.0062763 | 0.001573
5 | 0.98687 | -0.092065 | 0.0021536 | 0.00053975
6 | 0.99098 | -0.063052 | 0 | 0
7 | 0.98635 | -0.095782 | 0.0008461 | 0.00021205
8 | 0.99507 | -0.034272 | 0 | 0
9 | 0.98977 | -0.071546 | 0.02408 | 0.0060351
10 | 0.99075 | -0.064614 | 0.0012975 | 0.00032518
11 | 0.98723 | -0.089564 | 0.0027393 | 0.00068654
12 | 0.9873 | -0.089075 | 0.0040535 | 0.0010159
13 | 0.98744 | -0.088097 | 0 | 0
14 | 0.98777 | -0.085743 | 0.0084644 | 0.0021214
15 | 0.98785 | -0.085153 | 0.0033414 | 0.00083742
16 | 0.98624 | -0.096559 | 0.0070101 | 0.0017569
17 | 0.98567 | -0.10065 | 0.0032328 | 0.00081022
18 | 0.9898 | -0.071337 | 0.0014116 | 0.00035379
19 | 0.98985 | -0.071008 | 0.0037946 | 0.00095102
20 | 0.98975 | -0.071696 | 0.0014132 | 0.00035418
21 | 0.99007 | -0.069422 | 0.0033457 | 0.00083851
22 | 0.99026 | -0.068145 | 0 | 0
23 | 0.99024 | -0.068241 | 0.00092157 | 0.00023097
24 | 1 | 0 | -0.17533 | -0.043987
25 | 0.9945 | -0.038263 | 0.0042526 | 0.0010658
26 | 0.98849 | -0.080649 | 0.0019677 | 0.00049316
27 | 0.99988 | -0.00084321 | 0.0068587 | 0.0017189
28 | 0.9936 | -0.044574 | 0.0047623 | 0.0011935
29 | 0.99152 | -0.059142 | 0.0081346 | 0.0020387
30 | 0.99251 | -0.052207 | 0.010001 | 0.0025066
31 | 0.99052 | -0.066187 | 0 | 0
32 | 0.98861 | -0.079648 | 0 | 0
33 | 0.98854 | -0.08014 | 0 | 0
34 | 0.98552 | -0.10149 | 0.0066793 | 0.001674
35 | 0.98846 | -0.08073 | 0.0018524 | 0.00046424
36 | 0.98489 | -0.10599 | 0.0038189 | 0.00095711
37 | 0.98272 | -0.12142 | 0.00094377 | 0.00023653
38 | 0.98231 | -0.12436 | 0.0021788 | 0.00054605
39 | 0.98284 | -0.12055 | 0.0053662 | 0.0013449
40 | 0.98218 | -0.12532 | 0.0027061 | 0.00067821
41 | 0.98308 | -0.11884 | 0.0034569 | 0.00086638
42 | 0.98204 | -0.12633 | 0 | 0
43 | 0.98388 | -0.11312 | 0.0049307 | 0.0012358
44 | 0.9819 | -0.12733 | 0 | 0
45 | 0.98422 | -0.11073 | 0.0044861 | 0.0011243
46 | 0.98179 | -0.12809 | 0.00077408 | 0.000194
47 | 0.98178 | -0.12813 | 0.00090197 | 0.00022606
48 | 0.98354 | -0.11561 | 0.0031729 | 0.0007952
49 | 0.98345 | -0.11621 | 0.0039688 | 0.00099467
50 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.018363 | 0.0046036 | -0.01835 | -0.0045992 | 1.2187e-05 | 4.36e-06 | 0.027646 | 0.027646 | 0.027646 | 0.98837 | -0.081465 | 0.98769 | -0.086259 | 10.2393
1 | -0.023783 | -0.0059621 | 0.023803 | 0.0059694 | 1.9763e-05 | 7.2842e-06 | 0.035807 | 0.035807 | 0.035807 | 0.98837 | -0.081465 | 0.98922 | -0.075471 | 13.2617
2 | 0.015045 | 0.0037708 | -0.015034 | -0.0037671 | 1.0631e-05 | 3.6648e-06 | 0.022666 | 0.022666 | 0.022666 | 0.98769 | -0.086259 | 0.98697 | -0.091366 | 8.3949
3 | -0.030273 | -0.0075909 | 0.030282 | 0.0075944 | 9.3053e-06 | 3.4866e-06 | 0.045539 | 0.045539 | 0.045539 | 0.98922 | -0.075471 | 0.98953 | -0.073253 | 16.8663
4 | 0.013253 | 0.0033206 | -0.013251 | -0.0033202 | 1.2808e-06 | 4.2691e-07 | 0.01998 | 0.01998 | 0.01998 | 0.98697 | -0.091366 | 0.98687 | -0.092065 | 7.4
5 | -0.036559 | -0.0091674 | 0.03661 | 0.009187 | 5.1758e-05 | 1.9554e-05 | 0.054977 | 0.054977 | 0.054977 | 0.98953 | -0.073253 | 0.99098 | -0.063052 | 20.3619
6 | 0.011098 | 0.0027804 | -0.011092 | -0.0027786 | 5.7048e-06 | 1.7772e-06 | 0.016733 | 0.016733 | 0.016733 | 0.98687 | -0.092065 | 0.98635 | -0.095782 | 6.1974
7 | -0.093547 | -0.023467 | 0.093922 | 0.023611 | 0.00037496 | 0.00014382 | 0.14048 | 0.14048 | 0.14048 | 0.99098 | -0.063052 | 0.99507 | -0.034272 | 52.0279
8 | 0.044741 | 0.011224 | -0.044689 | -0.011204 | 5.2648e-05 | 2.0009e-05 | 0.067186 | 0.067186 | 0.067186 | 0.99098 | -0.063052 | 0.98977 | -0.071546 | 24.8837
9 | 0.012196 | 0.0030564 | -0.012193 | -0.0030555 | 2.6354e-06 | 8.5139e-07 | 0.018312 | 0.018313 | 0.018313 | 0.99098 | -0.063052 | 0.99075 | -0.064614 | 6.7824
10 | 0.010246 | 0.0025666 | -0.010245 | -0.0025662 | 1.101e-06 | 3.292e-07 | 0.015456 | 0.015457 | 0.015457 | 0.98635 | -0.095782 | 0.98624 | -0.096559 | 5.7246
11 | -0.16687 | -0.041961 | 0.16767 | 0.042268 | 0.00080093 | 0.00030697 | 0.24958 | 0.24958 | 0.24958 | 0.99507 | -0.034272 | 1 | 0 | 46.2193
12 | 0.072948 | 0.01835 | -0.072908 | -0.018335 | 4.0578e-05 | 1.5536e-05 | 0.10911 | 0.10911 | 0.10911 | 0.99507 | -0.034272 | 0.9945 | -0.038263 | 40.4108
13 | 0.020608 | 0.0051689 | -0.020583 | -0.0051594 | 2.598e-05 | 9.4356e-06 | 0.030984 | 0.030984 | 0.030984 | 0.98977 | -0.071546 | 0.98849 | -0.080649 | 11.4756
14 | 0.010895 | 0.0027304 | -0.01089 | -0.0027287 | 5.3239e-06 | 1.6375e-06 | 0.016364 | 0.016364 | 0.016364 | 0.99075 | -0.064614 | 0.99026 | -0.068145 | 6.0607
15 | -0.0027393 | -0.00068654 | 0.0027395 | 0.00068639 | 1.853e-07 | -1.5147e-07 | 0.0041289 | 0.0041288 | 0.0041289 | 0.98723 | -0.089564 | 0.9873 | -0.089075 | 1.5292
16 | -0.006793 | -0.0017023 | 0.0067939 | 0.0017025 | 9.1977e-07 | 1.739e-07 | 0.010238 | 0.010238 | 0.010238 | 0.9873 | -0.089075 | 0.98744 | -0.088097 | 3.7919
17 | -0.0067939 | -0.0017025 | 0.0067962 | 0.0017029 | 2.2128e-06 | 4.1817e-07 | 0.010238 | 0.010238 | 0.010238 | 0.98744 | -0.088097 | 0.98777 | -0.085743 | 3.7919
18 | -0.015261 | -0.0038243 | 0.015262 | 0.0038247 | 1.2476e-06 | 4.3141e-07 | 0.022989 | 0.022989 | 0.022989 | 0.98777 | -0.085743 | 0.98785 | -0.085153 | 8.5145
19 | -0.018603 | -0.0046621 | 0.018615 | 0.0046663 | 1.1603e-05 | 4.1593e-06 | 0.028022 | 0.028022 | 0.028022 | 0.98785 | -0.085153 | 0.98849 | -0.080649 | 10.3786
20 | 0.0032346 | 0.00080935 | -0.0032328 | -0.00081022 | 1.8267e-06 | -8.6507e-07 | 0.0048799 | 0.0048804 | 0.0048804 | 0.98624 | -0.096559 | 0.98567 | -0.10065 | 1.8076
21 | -0.0028249 | -0.00070768 | 0.002825 | 0.00070758 | 1.284e-07 | -9.7275e-08 | 0.0042467 | 0.0042466 | 0.0042467 | 0.9898 | -0.071337 | 0.98985 | -0.071008 | 1.5729
22 | 0.0014133 | 0.00035389 | -0.0014132 | -0.00035418 | 7.0146e-08 | -2.931e-07 | 0.0021245 | 0.0021246 | 0.0021246 | 0.9898 | -0.071337 | 0.98975 | -0.071696 | 0.7869
23 | -0.0066197 | -0.0016586 | 0.0066211 | 0.0016589 | 1.4533e-06 | 2.5656e-07 | 0.009951 | 0.0099509 | 0.009951 | 0.98985 | -0.071008 | 0.99007 | -0.069422 | 3.6856
24 | -0.0099668 | -0.0024974 | 0.0099686 | 0.0024979 | 1.7606e-06 | 5.1541e-07 | 0.014979 | 0.014979 | 0.014979 | 0.99007 | -0.069422 | 0.99026 | -0.068145 | 5.5479
25 | 0.00092158 | 0.00023084 | -0.00092157 | -0.00023097 | 1.225e-08 | -1.2699e-07 | 0.0013848 | 0.0013848 | 0.0013848 | 0.99026 | -0.068145 | 0.99024 | -0.068241 | 0.5129
26 | 0.0068595 | 0.0017191 | -0.0068587 | -0.0017189 | 8.0066e-07 | 1.4639e-07 | 0.010207 | 0.010207 | 0.010207 | 1 | 0 | 0.99988 | -0.00084321 | 3.7804
27 | 0.068655 | 0.017269 | -0.068595 | -0.017246 | 6.0366e-05 | 2.3099e-05 | 0.10275 | 0.10275 | 0.10275 | 0.9945 | -0.038263 | 0.9936 | -0.044574 | 38.0542
28 | 0.063832 | 0.016052 | -0.063764 | -0.016026 | 6.7838e-05 | 2.5938e-05 | 0.095614 | 0.095614 | 0.095614 | 0.9936 | -0.044574 | 0.99251 | -0.052207 | 35.4127
29 | -0.053711 | -0.0135 | 0.053763 | 0.01352 | 5.1906e-05 | 1.9799e-05 | 0.08062 | 0.08062 | 0.08062 | 0.99152 | -0.059142 | 0.99251 | -0.052207 | 29.8592
30 | 0.045576 | 0.011461 | -0.045532 | -0.011444 | 4.4709e-05 | 1.6998e-05 | 0.068412 | 0.068412 | 0.068412 | 0.99152 | -0.059142 | 0.99052 | -0.066187 | 25.3378
31 | 0.045532 | 0.011444 | -0.045447 | -0.011412 | 8.5172e-05 | 3.2384e-05 | 0.068412 | 0.068412 | 0.068412 | 0.99052 | -0.066187 | 0.98861 | -0.079648 | 25.3379
32 | 0.0018526 | 0.00046362 | -0.0018525 | -0.0004639 | 1.2604e-07 | -2.8461e-07 | 0.0027883 | 0.0027884 | 0.0027884 | 0.98861 | -0.079648 | 0.98854 | -0.08014 | 1.0327
33 | 0.043594 | 0.010948 | -0.043462 | -0.010898 | 0.00013196 | 5.0125e-05 | 0.065624 | 0.065624 | 0.065624 | 0.98861 | -0.079648 | 0.98552 | -0.10149 | 24.3052
34 | 0.0018525 | 0.0004639 | -0.0018524 | -0.00046424 | 1.5099e-07 | -3.4086e-07 | 0.0027884 | 0.0027885 | 0.0027885 | 0.98854 | -0.08014 | 0.98846 | -0.08073 | 1.0328
35 | 0.036783 | 0.0092239 | -0.03676 | -0.0092152 | 2.2931e-05 | 8.668e-06 | 0.055539 | 0.055539 | 0.055539 | 0.98552 | -0.10149 | 0.98489 | -0.10599 | 20.5701
36 | 0.032941 | 0.0082581 | -0.032919 | -0.00825 | 2.1587e-05 | 8.1252e-06 | 0.04977 | 0.04977 | 0.04977 | 0.98489 | -0.10599 | 0.98422 | -0.11073 | 18.4332
37 | 0.0065648 | 0.0016429 | -0.0065622 | -0.0016425 | 2.6616e-06 | 4.7691e-07 | 0.0099395 | 0.0099397 | 0.0099397 | 0.98272 | -0.12142 | 0.98231 | -0.12436 | 3.6814
38 | -0.0075086 | -0.0018795 | 0.0075095 | 0.0018797 | 9.0373e-07 | 2.0559e-07 | 0.011369 | 0.011368 | 0.011369 | 0.98272 | -0.12142 | 0.98284 | -0.12055 | 4.2106
39 | 0.0043834 | 0.0010964 | -0.0043828 | -0.0010965 | 5.8225e-07 | -4.3994e-08 | 0.0066392 | 0.0066393 | 0.0066393 | 0.98231 | -0.12436 | 0.98218 | -0.12532 | 2.459
40 | -0.012876 | -0.0032246 | 0.012879 | 0.0032256 | 3.0415e-06 | 1.0072e-06 | 0.019493 | 0.019493 | 0.019493 | 0.98284 | -0.12055 | 0.98308 | -0.11884 | 7.2196
41 | 0.0016767 | 0.00041824 | -0.0016765 | -0.00041888 | 2.3216e-07 | -6.4062e-07 | 0.0025395 | 0.0025398 | 0.0025398 | 0.98218 | -0.12532 | 0.98204 | -0.12633 | 0.94066
42 | -0.016336 | -0.004092 | 0.016349 | 0.0040965 | 1.292e-05 | 4.5394e-06 | 0.024725 | 0.024725 | 0.024725 | 0.98308 | -0.11884 | 0.98388 | -0.11312 | 9.1575
43 | 0.0016765 | 0.00041888 | -0.0016762 | -0.00041952 | 2.316e-07 | -6.3873e-07 | 0.0025398 | 0.00254 | 0.00254 | 0.98204 | -0.12633 | 0.9819 | -0.12733 | 0.94076
44 | -0.021279 | -0.0053323 | 0.021286 | 0.0053348 | 7.0659e-06 | 2.5788e-06 | 0.032182 | 0.032182 | 0.032182 | 0.98388 | -0.11312 | 0.98422 | -0.11073 | 11.9194
45 | 0.0016762 | 0.00041952 | -0.0016761 | -0.00042001 | 1.7501e-07 | -4.8243e-07 | 0.00254 | 0.0025402 | 0.0025402 | 0.9819 | -0.12733 | 0.98179 | -0.12809 | 0.94083
46 | 0.0071469 | 0.0017908 | -0.007142 | -0.0017898 | 4.8324e-06 | 1.0162e-06 | 0.010805 | 0.010805 | 0.010805 | 0.98422 | -0.11073 | 0.98354 | -0.11561 | 4.002
47 | 0.00090198 | 0.000226 | -0.00090197 | -0.00022606 | 5.1571e-09 | -5.3941e-08 | 0.001367 | 0.0013671 | 0.0013671 | 0.98179 | -0.12809 | 0.98178 | -0.12813 | 0.50632
48 | 0.0039691 | 0.00099461 | -0.0039688 | -0.00099467 | 3.2549e-07 | -5.8375e-08 | 0.0060049 | 0.006005 | 0.006005 | 0.98354 | -0.11561 | 0.98345 | -0.11621 | 2.2241

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18615 | 0.046698

## res_load
| p_mw | q_mvar
0 | 0.0054205 | 0.0013585
1 | 0.0033055 | 0.00082845
2 | 0.0064701 | 0.0016216
3 | 0.0017817 | 0.00044654
4 | 0.0062763 | 0.001573
5 | 0.0021536 | 0.00053975
6 | 0.0008461 | 0.00021205
7 | 0.02408 | 0.0060351
8 | 0.0012975 | 0.00032518
9 | 0.0027393 | 0.00068654
10 | 0.0040535 | 0.0010159
11 | 0.0084644 | 0.0021214
12 | 0.0033414 | 0.00083742
13 | 0.0070101 | 0.0017569
14 | 0.0032328 | 0.00081022
15 | 0.0014116 | 0.00035379
16 | 0.0037946 | 0.00095102
17 | 0.0014132 | 0.00035418
18 | 0.0033457 | 0.00083851
19 | 0.00092157 | 0.00023097
20 | 0.010816 | 0.0027107
21 | 0.0042526 | 0.0010658
22 | 0.0019677 | 0.00049316
23 | 0.0068587 | 0.0017189
24 | 0.0047623 | 0.0011935
25 | 0.0081346 | 0.0020387
26 | 0.010001 | 0.0025066
27 | 0.0066793 | 0.001674
28 | 0.0018524 | 0.00046424
29 | 0.0038189 | 0.00095711
30 | 0.00094377 | 0.00023653
31 | 0.0021788 | 0.00054605
32 | 0.0053662 | 0.0013449
33 | 0.0027061 | 0.00067821
34 | 0.0034569 | 0.00086638
35 | 0.0049307 | 0.0012358
36 | 0.0044861 | 0.0011243
37 | 0.00077408 | 0.000194
38 | 0.00090197 | 0.00022606
39 | 0.0031729 | 0.0007952
40 | 0.0039688 | 0.00099467

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1