## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1091-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1091-2_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1091-2_0_4_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_1091-2_0_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_1091-2_0_4_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1091-2_0_4_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1091-2_0_4_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_1091-2_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1091-2_0_4_node_107 | 0.4 | n |  | TRUE
9 | bus_LV_1091-2_0_4_node_53 | 0.4 | n |  | TRUE
10 | bus_LV_1091-2_0_4_node_41 | 0.4 | n |  | TRUE
11 | bus_LV_1091-2_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1091-2_0_4_node_37 | 0.4 | n |  | TRUE
13 | bus_LV_1091-2_0_4_node_113 | 0.4 | n |  | TRUE
14 | bus_LV_1091-2_0_4_node_114 | 0.4 | n |  | TRUE
15 | bus_LV_1091-2_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1091-2_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1091-2_0_4_node_55 | 0.4 | n |  | TRUE
18 | bus_LV_1091-2_0_4_node_51 | 0.4 | n |  | TRUE
19 | bus_LV_1091-2_0_4_node_106 | 0.4 | n |  | TRUE
20 | bus_LV_1091-2_0_4_node_81 | 0.4 | n |  | TRUE
21 | bus_LV_1091-2_0_4_node_38 | 0.4 | n |  | TRUE
22 | bus_LV_1091-2_0_4_node_115 | 0.4 | n |  | TRUE
23 | bus_LV_1091-2_0_4_node_116 | 0.4 | n |  | TRUE
24 | bus_LV_1091-2_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_1091-2_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1091-2_0_4_node_103 | 0.4 | n |  | TRUE
27 | bus_LV_1091-2_0_4_node_104 | 0.4 | n |  | TRUE
28 | bus_LV_1091-2_0_4_node_128 | 0.4 | n |  | TRUE
29 | bus_LV_1091-2_0_4_node_33 | 0.4 | n |  | TRUE
30 | bus_LV_1091-2_0_4_node_102 | 0.4 | n |  | TRUE
31 | bus_LV_1091-2_0_4_node_127 | 0.4 | n |  | TRUE
32 | bus_LV_1091-2_0_4_node_101 | 0.4 | n |  | TRUE
33 | bus_LV_1091-2_0_4_node_117 | 0.4 | n |  | TRUE
34 | bus_LV_1091-2_0_4_node_118 | 0.4 | n |  | TRUE
35 | bus_LV_1091-2_0_4_node_130 | 0.4 | n |  | TRUE
36 | bus_LV_1091-2_0_4_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_1091-2_0_4_node_129 | 0.4 | n |  | TRUE
38 | bus_LV_1091-2_0_4_node_100 | 0.4 | n |  | TRUE
39 | bus_LV_1091-2_0_4_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_1091-2_0_4_node_17 | 0.4 | n |  | TRUE
41 | bus_LV_1091-2_0_4_node_18 | 0.4 | n |  | TRUE
42 | bus_LV_1091-2_0_4_node_19 | 0.4 | n |  | TRUE
43 | bus_LV_1091-2_0_4_node_20 | 0.4 | n |  | TRUE
44 | bus_LV_1091-2_0_4_node_21 | 0.4 | n |  | TRUE
45 | bus_LV_1091-2_0_4_node_23 | 0.4 | n |  | TRUE
46 | bus_LV_1091-2_0_4_node_24 | 0.4 | n |  | TRUE
47 | bus_LV_1091-2_0_4_node_25 | 0.4 | n |  | TRUE
48 | bus_LV_1091-2_0_4_node_131 | 0.4 | n |  | TRUE
49 | bus_LV_1091-2_0_4_node_54 | 0.4 | n |  | TRUE
50 | bus_LV_1091-2_0_4_node_22 | 0.4 | n |  | TRUE
51 | bus_LV_1091-2_0_4_node_132 | 0.4 | n |  | TRUE
52 | bus_LV_1091-2_0_4_node_133 | 0.4 | n |  | TRUE
53 | bus_LV_1091-2_0_4_node_134 | 0.4 | n |  | TRUE
54 | bus_LV_1091-2_0_4_node_135 | 0.4 | n |  | TRUE
55 | bus_LV_1091-2_0_4_node_34 | 0.4 | n |  | TRUE
56 | bus_LV_1091-2_0_4_node_99 | 0.4 | n |  | TRUE
57 | bus_LV_1091-2_0_4_node_52 | 0.4 | n |  | TRUE
58 | bus_LV_1091-2_0_4_node_136 | 0.4 | n |  | TRUE
59 | bus_LV_1091-2_0_4_node_35 | 0.4 | n |  | TRUE
60 | bus_LV_1091-2_0_4_node_36 | 0.4 | n |  | TRUE
61 | bus_LV_1091-2_0_4_node_26 | 0.4 | n |  | TRUE
62 | bus_LV_1091-2_0_4_node_27 | 0.4 | n |  | TRUE
63 | bus_LV_1091-2_0_4_node_28 | 0.4 | n |  | TRUE
64 | bus_LV_1091-2_0_4_node_65 | 0.4 | n |  | TRUE
65 | bus_LV_1091-2_0_4_node_63 | 0.4 | n |  | TRUE
66 | bus_LV_1091-2_0_4_node_64 | 0.4 | n |  | TRUE
67 | bus_LV_1091-2_0_4_node_32 | 0.4 | n |  | TRUE
68 | bus_LV_1091-2_0_4_node_31 | 0.4 | n |  | TRUE
69 | bus_LV_1091-2_0_4_node_123 | 0.4 | n |  | TRUE
70 | bus_LV_1091-2_0_4_node_124 | 0.4 | n |  | TRUE
71 | bus_LV_1091-2_0_4_node_122 | 0.4 | n |  | TRUE
72 | bus_LV_1091-2_0_4_node_119 | 0.4 | n |  | TRUE
73 | bus_LV_1091-2_0_4_node_110 | 0.4 | n |  | TRUE
74 | bus_LV_1091-2_0_4_node_125 | 0.4 | n |  | TRUE
75 | bus_LV_1091-2_0_4_node_126 | 0.4 | n |  | TRUE
76 | bus_LV_1091-2_0_4_node_121 | 0.4 | n |  | TRUE
77 | bus_LV_1091-2_0_4_node_40 | 0.4 | n |  | TRUE
78 | bus_LV_1091-2_0_4_node_44 | 0.4 | n |  | TRUE
79 | bus_LV_1091-2_0_4_node_105 | 0.4 | n |  | TRUE
80 | bus_LV_1091-2_0_4_node_111 | 0.4 | n |  | TRUE
81 | bus_LV_1091-2_0_4_node_112 | 0.4 | n |  | TRUE
82 | bus_LV_1091-2_0_4_node_45 | 0.4 | n |  | TRUE
83 | bus_LV_1091-2_0_4_node_82 | 0.4 | n |  | TRUE
84 | bus_LV_1091-2_0_4_node_79 | 0.4 | n |  | TRUE
85 | bus_LV_1091-2_0_4_node_42 | 0.4 | n |  | TRUE
86 | bus_LV_1091-2_0_4_node_43 | 0.4 | n |  | TRUE
87 | bus_LV_1091-2_0_4_node_61 | 0.4 | n |  | TRUE
88 | bus_LV_1091-2_0_4_node_62 | 0.4 | n |  | TRUE
89 | bus_LV_1091-2_0_4_node_71 | 0.4 | n |  | TRUE
90 | bus_LV_1091-2_0_4_node_80 | 0.4 | n |  | TRUE
91 | bus_LV_1091-2_0_4_node_46 | 0.4 | n |  | TRUE
92 | bus_LV_1091-2_0_4_node_47 | 0.4 | n |  | TRUE
93 | bus_LV_1091-2_0_4_node_48 | 0.4 | n |  | TRUE
94 | bus_LV_1091-2_0_4_node_142 | 0.4 | n |  | TRUE
95 | bus_LV_1091-2_0_4_node_96 | 0.4 | n |  | TRUE
96 | bus_LV_1091-2_0_4_node_49 | 0.4 | n |  | TRUE
97 | bus_LV_1091-2_0_4_node_140 | 0.4 | n |  | TRUE
98 | bus_LV_1091-2_0_4_node_50 | 0.4 | n |  | TRUE
99 | bus_LV_1091-2_0_4_node_137 | 0.4 | n |  | TRUE
100 | bus_LV_1091-2_0_4_node_141 | 0.4 | n |  | TRUE
101 | bus_LV_1091-2_0_4_node_95 | 0.4 | n |  | TRUE
102 | bus_LV_1091-2_0_4_node_98 | 0.4 | n |  | TRUE
103 | bus_LV_1091-2_0_4_node_94 | 0.4 | n |  | TRUE
104 | bus_LV_1091-2_0_4_node_139 | 0.4 | n |  | TRUE
105 | bus_LV_1091-2_0_4_node_97 | 0.4 | n |  | TRUE
106 | bus_LV_1091-2_0_4_node_56 | 0.4 | n |  | TRUE
107 | bus_LV_1091-2_0_4_node_57 | 0.4 | n |  | TRUE
108 | bus_LV_1091-2_0_4_node_58 | 0.4 | n |  | TRUE
109 | bus_LV_1091-2_0_4_node_59 | 0.4 | n |  | TRUE
110 | bus_LV_1091-2_0_4_node_60 | 0.4 | n |  | TRUE
111 | bus_LV_1091-2_0_4_node_73 | 0.4 | n |  | TRUE
112 | bus_LV_1091-2_0_4_node_72 | 0.4 | n |  | TRUE
113 | bus_LV_1091-2_0_4_node_84 | 0.4 | n |  | TRUE
114 | bus_LV_1091-2_0_4_node_74 | 0.4 | n |  | TRUE
115 | bus_LV_1091-2_0_4_node_83 | 0.4 | n |  | TRUE
116 | bus_LV_1091-2_0_4_node_66 | 0.4 | n |  | TRUE
117 | bus_LV_1091-2_0_4_node_67 | 0.4 | n |  | TRUE
118 | bus_LV_1091-2_0_4_node_68 | 0.4 | n |  | TRUE
119 | bus_LV_1091-2_0_4_node_69 | 0.4 | n |  | TRUE
120 | bus_LV_1091-2_0_4_node_70 | 0.4 | n |  | TRUE
121 | bus_LV_1091-2_0_4_node_88 | 0.4 | n |  | TRUE
122 | bus_LV_1091-2_0_4_node_89 | 0.4 | n |  | TRUE
123 | bus_LV_1091-2_0_4_node_87 | 0.4 | n |  | TRUE
124 | bus_LV_1091-2_0_4_node_86 | 0.4 | n |  | TRUE
125 | bus_LV_1091-2_0_4_node_93 | 0.4 | n |  | TRUE
126 | bus_LV_1091-2_0_4_node_75 | 0.4 | n |  | TRUE
127 | bus_LV_1091-2_0_4_node_77 | 0.4 | n |  | TRUE
128 | bus_LV_1091-2_0_4_node_91 | 0.4 | n |  | TRUE
129 | bus_LV_1091-2_0_4_node_90 | 0.4 | n |  | TRUE
130 | bus_LV_1091-2_0_4_node_108 | 0.4 | n |  | TRUE
131 | bus_LV_1091-2_0_4_node_109 | 0.4 | n |  | TRUE
132 | bus_LV_1091-2_0_4_node_158 | 0.4 | n |  | TRUE
133 | bus_LV_1091-2_0_4_node_156 | 0.4 | n |  | TRUE
134 | bus_LV_1091-2_0_4_node_120 | 0.4 | n |  | TRUE
135 | bus_LV_1091-2_0_4_node_138 | 0.4 | n |  | TRUE
136 | bus_LV_1091-2_0_4_node_157 | 0.4 | n |  | TRUE
137 | bus_LV_1091-2_0_4_node_154 | 0.4 | n |  | TRUE
138 | bus_LV_1091-2_0_4_node_152 | 0.4 | n |  | TRUE
139 | bus_LV_1091-2_0_4_node_146 | 0.4 | n |  | TRUE
140 | bus_LV_1091-2_0_4_node_149 | 0.4 | n |  | TRUE
141 | bus_LV_1091-2_0_4_node_143 | 0.4 | n |  | TRUE
142 | bus_LV_1091-2_0_4_node_144 | 0.4 | n |  | TRUE
143 | bus_LV_1091-2_0_4_node_145 | 0.4 | n |  | TRUE
144 | bus_LV_1091-2_0_4_node_147 | 0.4 | n |  | TRUE
145 | bus_LV_1091-2_0_4_node_148 | 0.4 | n |  | TRUE
146 | bus_LV_1091-2_0_4_node_150 | 0.4 | n |  | TRUE
147 | bus_LV_1091-2_0_4_node_151 | 0.4 | n |  | TRUE
148 | bus_LV_1091-2_0_4_node_153 | 0.4 | n |  | TRUE
149 | bus_LV_1091-2_0_4_node_155 | 0.4 | n |  | TRUE
150 | bus_MV_131_1_node_114 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1091-2_0_4_load_0 | 0 | 0.0023967 | 0.00060067 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1091-2_0_4_load_4 | 2 | 0.0065946 | 0.0016528 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1091-2_0_4_load_3 | 5 | 0.0019061 | 0.00047771 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1091-2_0_4_load_12 | 6 | 0.001769 | 0.00044337 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1091-2_0_4_load_8 | 7 | 0.0023128 | 0.00057963 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1091-2_0_4_load_107 | 8 | 0.0021429 | 0.00053707 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1091-2_0_4_load_37 | 12 | 0.0031096 | 0.00077935 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1091-2_0_4_load_114 | 14 | 0.0032856 | 0.00082345 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1091-2_0_4_load_13 | 15 | 0.0019186 | 0.00048084 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1091-2_0_4_load_9 | 16 | 0.0031608 | 0.00079217 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1091-2_0_4_load_55 | 17 | 0.0027113 | 0.00067951 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1091-2_0_4_load_51 | 18 | 0.00083486 | 0.00020924 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1091-2_0_4_load_106 | 19 | 0.0029754 | 0.00074571 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1091-2_0_4_load_38 | 21 | 0.0029316 | 0.00073474 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1091-2_0_4_load_115 | 22 | 0.0032872 | 0.00082386 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1091-2_0_4_load_103 | 26 | 0.0070748 | 0.0017731 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1091-2_0_4_load_128 | 28 | 0.0030627 | 0.00076758 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1091-2_0_4_load_127 | 31 | 0.0090389 | 0.0022654 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1091-2_0_4_load_118 | 34 | 0.0015676 | 0.00039288 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1091-2_0_4_load_130 | 35 | 0.002996 | 0.00075088 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1091-2_0_4_load_129 | 37 | 0.0079195 | 0.0019848 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1091-2_0_4_load_100 | 38 | 0.0033943 | 0.00085069 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1091-2_0_4_load_17 | 40 | 0.00094883 | 0.0002378 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1091-2_0_4_load_18 | 41 | 0.0021749 | 0.00054509 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1091-2_0_4_load_24 | 46 | 0.0044799 | 0.0011228 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1091-2_0_4_load_25 | 47 | 0.0035335 | 0.00088559 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1091-2_0_4_load_131 | 48 | 0.0023517 | 0.00058938 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1091-2_0_4_load_132 | 51 | 0.0027326 | 0.00068485 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1091-2_0_4_load_133 | 52 | 0.0021456 | 0.00053773 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1091-2_0_4_load_135 | 54 | 0.0022446 | 0.00056254 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1091-2_0_4_load_99 | 56 | 0.0035409 | 0.00088742 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1091-2_0_4_load_52 | 57 | 0.0022844 | 0.00057252 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1091-2_0_4_load_136 | 58 | 0.0021766 | 0.0005455 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1091-2_0_4_load_35 | 59 | 0.0039259 | 0.00098393 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1091-2_0_4_load_26 | 61 | 0.0017342 | 0.00043463 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1091-2_0_4_load_27 | 62 | 0.0037546 | 0.000941 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1091-2_0_4_load_63 | 65 | 0.0049532 | 0.0012414 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1091-2_0_4_load_64 | 66 | 0.006077 | 0.001523 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1091-2_0_4_load_124 | 70 | 0.0015474 | 0.00038781 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1091-2_0_4_load_122 | 71 | 0.0016688 | 0.00041825 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1091-2_0_4_load_110 | 73 | 0.0035428 | 0.00088791 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1091-2_0_4_load_125 | 74 | 0.0014948 | 0.00037464 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1091-2_0_4_load_126 | 75 | 0.0016984 | 0.00042565 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1091-2_0_4_load_121 | 76 | 0.0015263 | 0.00038252 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1091-2_0_4_load_40 | 77 | 0.001814 | 0.00045464 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1091-2_0_4_load_44 | 78 | 0.0018036 | 0.00045203 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1091-2_0_4_load_112 | 81 | 0.00031033 | 7.7776e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1091-2_0_4_load_45 | 82 | 0.0017336 | 0.00043448 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1091-2_0_4_load_79 | 84 | 0.0005725 | 0.00014348 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1091-2_0_4_load_42 | 85 | 0.0017342 | 0.00043463 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1091-2_0_4_load_61 | 87 | 0.0017983 | 0.0004507 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1091-2_0_4_load_62 | 88 | 0.0013447 | 0.00033701 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1091-2_0_4_load_71 | 89 | 0.00070646 | 0.00017706 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1091-2_0_4_load_80 | 90 | 0.0011447 | 0.00028688 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1091-2_0_4_load_46 | 91 | 0.0015349 | 0.00038469 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1091-2_0_4_load_142 | 94 | 0.0030952 | 0.00077574 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1091-2_0_4_load_96 | 95 | 0.0037798 | 0.00094732 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1091-2_0_4_load_140 | 97 | 0.0025785 | 0.00064623 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1091-2_0_4_load_141 | 100 | 0.0025697 | 0.00064402 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1091-2_0_4_load_98 | 102 | 0.0031009 | 0.00077716 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1091-2_0_4_load_94 | 103 | 0.0032734 | 0.00082038 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1091-2_0_4_load_139 | 104 | 0.0025701 | 0.00064413 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1091-2_0_4_load_97 | 105 | 0.0025775 | 0.00064599 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1091-2_0_4_load_56 | 106 | 6.8114e-05 | 1.7071e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1091-2_0_4_load_57 | 107 | 0.00032534 | 8.1538e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1091-2_0_4_load_58 | 108 | 0.00060636 | 0.00015197 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1091-2_0_4_load_59 | 109 | 0.000952 | 0.00023859 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1091-2_0_4_load_73 | 111 | 9.1926e-05 | 2.3039e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1091-2_0_4_load_72 | 112 | 0.0011876 | 0.00029763 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1091-2_0_4_load_84 | 113 | 0.00014833 | 3.7176e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1091-2_0_4_load_83 | 115 | 0.0002911 | 7.2958e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1091-2_0_4_load_66 | 116 | 0.0014894 | 0.00037328 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1091-2_0_4_load_67 | 117 | 0.0015301 | 0.00038347 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1091-2_0_4_load_68 | 118 | 0.0014154 | 0.00035473 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1091-2_0_4_load_69 | 119 | 0.0011477 | 0.00028764 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1091-2_0_4_load_70 | 120 | 0.0010456 | 0.00026206 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1091-2_0_4_load_89 | 122 | 0.0033727 | 0.00084528 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1091-2_0_4_load_87 | 123 | 0.0027557 | 0.00069065 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1091-2_0_4_load_86 | 124 | 0.001502 | 0.00037645 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1091-2_0_4_load_93 | 125 | 0.0019414 | 0.00048656 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1091-2_0_4_load_75 | 126 | 0.0016154 | 0.00040485 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1091-2_0_4_load_90 | 129 | 0.0014282 | 0.00035795 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1091-2_0_4_load_108 | 130 | 0.0032856 | 0.00082346 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1091-2_0_4_load_158 | 132 | 0.0025088 | 0.00062876 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1091-2_0_4_load_120 | 134 | 0.0015782 | 0.00039554 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1091-2_0_4_load_138 | 135 | 0.0025789 | 0.00064634 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1091-2_0_4_load_157 | 136 | 0.0032864 | 0.00082366 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1091-2_0_4_load_152 | 138 | 0.0032887 | 0.00082424 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1091-2_0_4_load_149 | 140 | 0.0038069 | 0.00095411 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1091-2_0_4_load_143 | 141 | 0.0098866 | 0.0024778 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1091-2_0_4_load_147 | 144 | 0.0029658 | 0.00074331 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1091-2_0_4_load_151 | 147 | 0.0038069 | 0.00095411 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1091-2_0_4_load_153 | 148 | 0.0029064 | 0.00072842 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1091-2_0_4_load_155 | 149 | 0.0025609 | 0.00064181 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 78 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1091-2_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.017979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1091-2_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.015172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1091-2_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.018299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_1091-2_0_4_line_3 | NAYY 4x150 SE | 1 | 4 | 0.044627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_1091-2_0_4_line_4 | NAYY 4x150 SE | 2 | 7 | 0.025395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1091-2_0_4_line_5 | NAYY 4x150 SE | 3 | 8 | 0.012793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1091-2_0_4_line_6 | NAYY 4x150 SE | 3 | 9 | 0.020712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_1091-2_0_4_line_7 | NAYY 4x150 SE | 4 | 10 | 0.019221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1091-2_0_4_line_8 | NAYY 4x150 SE | 4 | 11 | 0.027719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1091-2_0_4_line_9 | NAYY 4x150 SE | 4 | 12 | 0.028682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_1091-2_0_4_line_10 | NAYY 4x150 SE | 5 | 6 | 0.030609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1091-2_0_4_line_11 | NAYY 4x150 SE | 6 | 15 | 0.0097635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1091-2_0_4_line_12 | NAYY 4x150 SE | 7 | 16 | 0.022351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1091-2_0_4_line_13 | NAYY 4x150 SE | 9 | 17 | 0.007315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1091-2_0_4_line_14 | NAYY 4x150 SE | 9 | 18 | 0.011846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_1091-2_0_4_line_15 | NAYY 4x150 SE | 10 | 19 | 0.024109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1091-2_0_4_line_16 | NAYY 4x150 SE | 10 | 20 | 0.019365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1091-2_0_4_line_17 | NAYY 4x150 SE | 11 | 13 | 0.024428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1091-2_0_4_line_18 | NAYY 4x150 SE | 11 | 14 | 0.00465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1091-2_0_4_line_19 | NAYY 4x150 SE | 12 | 21 | 0.006844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_1091-2_0_4_line_20 | NAYY 4x150 SE | 13 | 22 | 0.005226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1091-2_0_4_line_21 | NAYY 4x150 SE | 13 | 23 | 0.023815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1091-2_0_4_line_22 | NAYY 4x150 SE | 15 | 24 | 0.0077473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1091-2_0_4_line_23 | NAYY 4x150 SE | 18 | 57 | 0.013067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
24 | LV_1091-2_0_4_line_24 | NAYY 4x150 SE | 20 | 83 | 0.017298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1091-2_0_4_line_25 | NAYY 4x150 SE | 20 | 84 | 0.033744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1091-2_0_4_line_26 | NAYY 4x150 SE | 21 | 77 | 0.021549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_1091-2_0_4_line_27 | NAYY 4x150 SE | 23 | 138 | 0.00465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1091-2_0_4_line_28 | NAYY 4x150 SE | 23 | 139 | 0.023743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1091-2_0_4_line_29 | NAYY 4x150 SE | 24 | 25 | 0.024756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1091-2_0_4_line_30 | NAYY 4x150 SE | 25 | 26 | 0.010332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1091-2_0_4_line_31 | NAYY 4x150 SE | 25 | 27 | 0.022133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1091-2_0_4_line_32 | NAYY 4x150 SE | 27 | 28 | 0.003733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1091-2_0_4_line_33 | NAYY 4x150 SE | 27 | 29 | 0.055298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1091-2_0_4_line_34 | NAYY 4x150 SE | 27 | 30 | 0.007719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1091-2_0_4_line_35 | NAYY 4x150 SE | 29 | 31 | 0.003726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1091-2_0_4_line_36 | NAYY 4x150 SE | 30 | 35 | 0.003961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1091-2_0_4_line_37 | NAYY 4x150 SE | 30 | 36 | 0.047278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1091-2_0_4_line_38 | NAYY 4x150 SE | 30 | 32 | 0.023632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1091-2_0_4_line_39 | NAYY 4x150 SE | 32 | 33 | 0.007658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1091-2_0_4_line_40 | NAYY 4x150 SE | 32 | 34 | 0.002909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1091-2_0_4_line_41 | NAYY 4x150 SE | 33 | 134 | 0.004465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1091-2_0_4_line_42 | NAYY 4x150 SE | 33 | 72 | 0.013269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1091-2_0_4_line_43 | NAYY 4x150 SE | 36 | 37 | 0.005685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1091-2_0_4_line_44 | NAYY 4x150 SE | 38 | 39 | 0.022113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1091-2_0_4_line_45 | NAYY 4x150 SE | 39 | 60 | 0.0114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1091-2_0_4_line_46 | NAYY 4x150 SE | 39 | 67 | 0.0297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1091-2_0_4_line_47 | NAYY 4x150 SE | 39 | 63 | 0.038083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1091-2_0_4_line_48 | NAYY 4x150 SE | 40 | 41 | 0.01972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_1091-2_0_4_line_49 | NAYY 4x150 SE | 40 | 42 | 0.0127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_1091-2_0_4_line_50 | NAYY 4x150 SE | 41 | 43 | 0.025362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_1091-2_0_4_line_51 | NAYY 4x150 SE | 42 | 44 | 0.001451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_1091-2_0_4_line_52 | NAYY 4x150 SE | 42 | 45 | 0.043234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1091-2_0_4_line_53 | NAYY 4x150 SE | 43 | 46 | 0.008041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1091-2_0_4_line_54 | NAYY 4x150 SE | 43 | 47 | 0.0097328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_1091-2_0_4_line_55 | NAYY 4x150 SE | 44 | 48 | 0.008983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1091-2_0_4_line_56 | NAYY 4x150 SE | 44 | 49 | 0.022497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
57 | LV_1091-2_0_4_line_57 | NAYY 4x150 SE | 45 | 53 | 0.001576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1091-2_0_4_line_58 | NAYY 4x150 SE | 45 | 54 | 0.009734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1091-2_0_4_line_59 | NAYY 4x150 SE | 45 | 50 | 0.022673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1091-2_0_4_line_60 | NAYY 4x150 SE | 47 | 55 | 0.016348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
61 | LV_1091-2_0_4_line_61 | NAYY 4x150 SE | 49 | 56 | 0.009361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1091-2_0_4_line_62 | NAYY 4x150 SE | 49 | 57 | 0.016475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
63 | LV_1091-2_0_4_line_63 | NAYY 4x150 SE | 50 | 51 | 0.009162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1091-2_0_4_line_64 | NAYY 4x150 SE | 50 | 52 | 0.00961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1091-2_0_4_line_65 | NAYY 4x150 SE | 53 | 58 | 0.008859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1091-2_0_4_line_66 | NAYY 4x150 SE | 55 | 59 | 0.010814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1091-2_0_4_line_67 | NAYY 4x150 SE | 55 | 60 | 0.018489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1091-2_0_4_line_68 | NAYY 4x150 SE | 60 | 73 | 0.026293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1091-2_0_4_line_69 | NAYY 4x150 SE | 61 | 62 | 0.065547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1091-2_0_4_line_70 | NAYY 4x150 SE | 61 | 63 | 0.10271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1091-2_0_4_line_71 | NAYY 4x150 SE | 63 | 64 | 0.25809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1091-2_0_4_line_72 | NAYY 4x150 SE | 64 | 66 | 0.06056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1091-2_0_4_line_73 | NAYY 4x150 SE | 65 | 66 | 0.014553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1091-2_0_4_line_74 | NAYY 4x150 SE | 67 | 71 | 0.001891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1091-2_0_4_line_75 | NAYY 4x150 SE | 67 | 72 | 0.007861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1091-2_0_4_line_76 | NAYY 4x150 SE | 67 | 68 | 0.030532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1091-2_0_4_line_77 | NAYY 4x150 SE | 68 | 69 | 0.007828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1091-2_0_4_line_78 | NAYY 4x150 SE | 68 | 70 | 0.005015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1091-2_0_4_line_79 | NAYY 4x150 SE | 69 | 74 | 0.012154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1091-2_0_4_line_80 | NAYY 4x150 SE | 69 | 75 | 0.004284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1091-2_0_4_line_81 | NAYY 4x150 SE | 72 | 76 | 0.003822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1091-2_0_4_line_82 | NAYY 4x150 SE | 77 | 78 | 0.012944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
83 | LV_1091-2_0_4_line_83 | NAYY 4x150 SE | 78 | 82 | 0.01992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1091-2_0_4_line_84 | NAYY 4x150 SE | 79 | 80 | 0.009232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1091-2_0_4_line_85 | NAYY 4x150 SE | 79 | 81 | 0.004939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1091-2_0_4_line_86 | NAYY 4x150 SE | 80 | 135 | 0.005208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1091-2_0_4_line_87 | NAYY 4x150 SE | 80 | 99 | 0.019303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1091-2_0_4_line_88 | NAYY 4x150 SE | 82 | 91 | 0.02814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1091-2_0_4_line_89 | NAYY 4x150 SE | 83 | 130 | 0.00443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1091-2_0_4_line_90 | NAYY 4x150 SE | 83 | 131 | 0.015976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1091-2_0_4_line_91 | NAYY 4x150 SE | 84 | 90 | 0.04415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1091-2_0_4_line_92 | NAYY 4x150 SE | 85 | 86 | 0.052066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1091-2_0_4_line_93 | NAYY 4x150 SE | 86 | 87 | 0.018452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1091-2_0_4_line_94 | NAYY 4x150 SE | 86 | 88 | 0.010636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1091-2_0_4_line_95 | NAYY 4x150 SE | 87 | 89 | 0.02096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1091-2_0_4_line_96 | NAYY 4x150 SE | 88 | 90 | 0.0093367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1091-2_0_4_line_97 | NAYY 4x150 SE | 89 | 112 | 0.0016256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1091-2_0_4_line_98 | NAYY 4x150 SE | 91 | 92 | 0.0024936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1091-2_0_4_line_99 | NAYY 4x150 SE | 92 | 93 | 0.016568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1091-2_0_4_line_100 | NAYY 4x150 SE | 93 | 94 | 0.007436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1091-2_0_4_line_101 | NAYY 4x150 SE | 93 | 95 | 0.007526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1091-2_0_4_line_102 | NAYY 4x150 SE | 95 | 102 | 0.007575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1091-2_0_4_line_103 | NAYY 4x150 SE | 95 | 103 | 0.024669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1091-2_0_4_line_104 | NAYY 4x150 SE | 96 | 97 | 0.005289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1091-2_0_4_line_105 | NAYY 4x150 SE | 96 | 98 | 0.030081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1091-2_0_4_line_106 | NAYY 4x150 SE | 96 | 99 | 0.009196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1091-2_0_4_line_107 | NAYY 4x150 SE | 98 | 100 | 0.004336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1091-2_0_4_line_108 | NAYY 4x150 SE | 98 | 101 | 0.008993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1091-2_0_4_line_109 | NAYY 4x150 SE | 99 | 104 | 0.004901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1091-2_0_4_line_110 | NAYY 4x150 SE | 101 | 105 | 0.005756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1091-2_0_4_line_111 | NAYY 4x150 SE | 101 | 103 | 0.024697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1091-2_0_4_line_112 | NAYY 4x150 SE | 106 | 107 | 0.0081653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1091-2_0_4_line_113 | NAYY 4x150 SE | 106 | 108 | 0.0076864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1091-2_0_4_line_114 | NAYY 4x150 SE | 107 | 109 | 0.00020071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1091-2_0_4_line_115 | NAYY 4x150 SE | 108 | 110 | 0.020778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1091-2_0_4_line_116 | NAYY 4x150 SE | 109 | 111 | 0.023574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1091-2_0_4_line_117 | NAYY 4x150 SE | 110 | 112 | 0.027188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1091-2_0_4_line_118 | NAYY 4x150 SE | 110 | 113 | 0.029302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1091-2_0_4_line_119 | NAYY 4x150 SE | 111 | 114 | 0.012322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1091-2_0_4_line_120 | NAYY 4x150 SE | 113 | 115 | 0.0083496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1091-2_0_4_line_121 | NAYY 4x150 SE | 114 | 124 | 0.032817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_1091-2_0_4_line_122 | NAYY 4x150 SE | 114 | 120 | 0.010923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_1091-2_0_4_line_123 | NAYY 4x150 SE | 116 | 117 | 0.010873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_1091-2_0_4_line_124 | NAYY 4x150 SE | 116 | 118 | 0.020674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_1091-2_0_4_line_125 | NAYY 4x150 SE | 117 | 119 | 0.040513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_1091-2_0_4_line_126 | NAYY 4x150 SE | 118 | 120 | 0.01418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_1091-2_0_4_line_127 | NAYY 4x150 SE | 119 | 121 | 0.011806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_1091-2_0_4_line_128 | NAYY 4x150 SE | 121 | 122 | 0.030097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_1091-2_0_4_line_129 | NAYY 4x150 SE | 121 | 123 | 0.03282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_1091-2_0_4_line_130 | NAYY 4x150 SE | 124 | 125 | 0.0045133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_1091-2_0_4_line_131 | NAYY 4x150 SE | 125 | 128 | 0.061733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_1091-2_0_4_line_132 | NAYY 4x150 SE | 126 | 127 | 0.14283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_1091-2_0_4_line_133 | NAYY 4x150 SE | 127 | 128 | 0.4128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_1091-2_0_4_line_134 | NAYY 4x150 SE | 128 | 129 | 0.051128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_1091-2_0_4_line_135 | NAYY 4x150 SE | 131 | 132 | 0.016045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_1091-2_0_4_line_136 | NAYY 4x150 SE | 131 | 133 | 0.012194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_1091-2_0_4_line_137 | NAYY 4x150 SE | 133 | 136 | 0.004377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_1091-2_0_4_line_138 | NAYY 4x150 SE | 133 | 137 | 0.013306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_1091-2_0_4_line_139 | NAYY 4x150 SE | 137 | 149 | 0.014431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_1091-2_0_4_line_140 | NAYY 4x150 SE | 137 | 146 | 0.009856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_1091-2_0_4_line_141 | NAYY 4x150 SE | 139 | 140 | 0.005107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_1091-2_0_4_line_142 | NAYY 4x150 SE | 141 | 142 | 0.038115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_1091-2_0_4_line_143 | NAYY 4x150 SE | 142 | 143 | 0.007397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_1091-2_0_4_line_144 | NAYY 4x150 SE | 143 | 144 | 0.014429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_1091-2_0_4_line_145 | NAYY 4x150 SE | 143 | 145 | 0.018728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_1091-2_0_4_line_146 | NAYY 4x150 SE | 145 | 146 | 0.007196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_1091-2_0_4_line_147 | NAYY 4x150 SE | 145 | 147 | 0.00465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_1091-2_0_4_line_148 | NAYY 4x150 SE | 146 | 148 | 0.016322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1091-2_0_4_trafo_44 | 0.25 MVA 20/0.4 kV | 150 | 78 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2649399.3471 | 1224686.9663 | 2649415.4026 | 1224695.0581
1 | 2649399.3471 | 1224686.9663 | 2649405.8874 | 1224673.2762
2 | 2649391.1596 | 1224703.3307 | 2649397.5802 | 1224690.6651 | 2649399.3471 | 1224686.9663
3 | 2649362.8397 | 1224669.8198 | 2649368.7807 | 1224672.9265 | 2649397.5802 | 1224690.6651 | 2649399.3471 | 1224686.9663
4 | 2649405.8874 | 1224673.2762 | 2649416.8344 | 1224650.3621
5 | 2649391.1596 | 1224703.3307 | 2649402.059 | 1224710.0809
6 | 2649391.1596 | 1224703.3307 | 2649385.98 | 1224713.5497 | 2649380.5876 | 1224721.0874
7 | 2649349.453 | 1224656.7119 | 2649353.3618 | 1224658.9456 | 2649359.284 | 1224663.4086 | 2649362.8397 | 1224669.8198
8 | 2649362.8397 | 1224669.8198 | 2649368.7807 | 1224672.9265 | 2649377.0457 | 1224653.6053
9 | 2649362.8397 | 1224669.8198 | 2649353.765 | 1224666.0867 | 2649346.9584 | 1224665.8857 | 2649341.413 | 1224667.185 | 2649337.038 | 1224671.8072
10 | 2649435.3162 | 1224739.0138 | 2649419.5148 | 1224765.2287
11 | 2649419.5148 | 1224765.2287 | 2649414.4746 | 1224773.5906
12 | 2649426.4693 | 1224630.1944 | 2649416.8344 | 1224650.3621
13 | 2649374.7486 | 1224716.6585 | 2649380.5876 | 1224721.0874
14 | 2649380.5876 | 1224721.0874 | 2649373.6939 | 1224730.7208
15 | 2649355.9923 | 1224636.12 | 2649358.417 | 1224637.2074 | 2649349.453 | 1224656.7119
16 | 2649332.6183 | 1224647.0553 | 2649349.453 | 1224656.7119
17 | 2649387.487 | 1224631.5116 | 2649377.0457 | 1224653.6053
18 | 2649372.8162 | 1224651.6468 | 2649377.0457 | 1224653.6053
19 | 2649334.4834 | 1224678.1566 | 2649337.038 | 1224671.8072
20 | 2649382.6437 | 1224629.5146 | 2649387.487 | 1224631.5116
21 | 2649397.3715 | 1224609.8357 | 2649387.487 | 1224631.5116
22 | 2649411.2989 | 1224780.6566 | 2649414.4351 | 1224773.6561 | 2649414.4746 | 1224773.5906
23 | 2649373.6939 | 1224730.7208 | 2649366.0894 | 1224741.3474
24 | 2649332.6183 | 1224647.0553 | 2649331.8829 | 1224641.5681 | 2649332.6982 | 1224637.4167 | 2649335.9162 | 1224630.6058
25 | 2649332.6183 | 1224647.0553 | 2649314.0574 | 1224638.0183 | 2649302.9232 | 1224631.1158
26 | 2649334.4834 | 1224678.1566 | 2649330.3146 | 1224688.0838 | 2649325.8876 | 1224696.241 | 2649324.9824 | 1224697.4378
27 | 2649393.142 | 1224607.8772 | 2649397.3715 | 1224609.8357
28 | 2649407.8067 | 1224588.498 | 2649397.3715 | 1224609.8357
29 | 2649425.897 | 1224797.5659 | 2649424.4055 | 1224797.3201 | 2649417.5613 | 1224794.3503 | 2649413.6003 | 1224790.2038 | 2649411.5462 | 1224786.4845 | 2649411.2989 | 1224780.6566
30 | 2649429.5255 | 1224787.8901 | 2649425.897 | 1224797.5659
31 | 2649425.897 | 1224797.5659 | 2649430.7046 | 1224798.3619 | 2649431.9936 | 1224808.3899 | 2649427.1433 | 1224813.6418
32 | 2649423.9372 | 1224811.714 | 2649427.1433 | 1224813.6418
33 | 2649427.1433 | 1224813.6418 | 2649431.9936 | 1224808.3899 | 2649448.9599 | 1224820.3826 | 2649446.7626 | 1224823.8665 | 2649454.6327 | 1224834.7496 | 2649449.9062 | 1224843.3601
34 | 2649427.1433 | 1224813.6418 | 2649422.1738 | 1224819.5597
35 | 2649446.6692 | 1224841.4988 | 2649449.9062 | 1224843.3601
36 | 2649418.6561 | 1224817.7183 | 2649422.1738 | 1224819.5597
37 | 2649420.5264 | 1224859.0927 | 2649426.7206 | 1224848.1151 | 2649420.5433 | 1224845.1842 | 2649416.3321 | 1224829.1727 | 2649418.5448 | 1224824.7328 | 2649422.1738 | 1224819.5597
38 | 2649407.0922 | 1224828.9404 | 2649411.8687 | 1224820.7083 | 2649418.5448 | 1224824.7328 | 2649422.1738 | 1224819.5597
39 | 2649407.0922 | 1224828.9404 | 2649404.0464 | 1224834.1961 | 2649403.2465 | 1224835.5681
40 | 2649404.5414 | 1224827.5295 | 2649407.0922 | 1224828.9404
41 | 2649399.2604 | 1224833.5338 | 2649403.2465 | 1224835.5681
42 | 2649403.2465 | 1224835.5681 | 2649396.5857 | 1224847.0533
43 | 2649415.3375 | 1224856.7371 | 2649420.5264 | 1224859.0927
44 | 2649369.7385 | 1224851.7781 | 2649377.4738 | 1224831.0622
45 | 2649360.9668 | 1224844.4675 | 2649369.7385 | 1224851.7781
46 | 2649369.7385 | 1224851.7781 | 2649388.2173 | 1224861.4928 | 2649392.6399 | 1224853.8581
47 | 2649358.4826 | 1224888.0516 | 2649364.0765 | 1224865.3395 | 2649369.7385 | 1224851.7781
48 | 2649334.4416 | 1224784.0399 | 2649322.6359 | 1224799.8351
49 | 2649342.045 | 1224773.8672 | 2649334.4416 | 1224784.0399
50 | 2649323.4107 | 1224820.3971 | 2649319.3083 | 1224817.7615 | 2649316.8041 | 1224814.372 | 2649316.6344 | 1224810.1458 | 2649318.4168 | 1224805.4799 | 2649322.6359 | 1224799.8351
51 | 2649342.9189 | 1224772.707 | 2649342.045 | 1224773.8672
52 | 2649342.045 | 1224773.8672 | 2649370.5429 | 1224790.4469 | 2649376.0884 | 1224781.8098
53 | 2649323.4107 | 1224820.3971 | 2649319.7275 | 1224827.5488
54 | 2649323.4107 | 1224820.3971 | 2649331.6061 | 1224825.6472
55 | 2649335.524 | 1224767.576 | 2649342.9189 | 1224772.707
56 | 2649356.4043 | 1224754.6743 | 2649342.9189 | 1224772.707
57 | 2649376.9409 | 1224780.4827 | 2649376.0884 | 1224781.8098
58 | 2649367.676 | 1224776.8703 | 2649376.0884 | 1224781.8098
59 | 2649376.0884 | 1224781.8098 | 2649370.5429 | 1224790.4469 | 2649364.0866 | 1224801.0444
60 | 2649345.3713 | 1224834.4655 | 2649331.6061 | 1224825.6472
61 | 2649348.5545 | 1224749.5394 | 2649356.4043 | 1224754.6743
62 | 2649356.4043 | 1224754.6743 | 2649360 | 1224749.8567 | 2649366.0894 | 1224741.3474
63 | 2649364.0866 | 1224801.0444 | 2649371.9394 | 1224805.8013
64 | 2649355.4872 | 1224796.7038 | 2649364.0866 | 1224801.0444
65 | 2649376.9409 | 1224780.4827 | 2649384.3223 | 1224785.4136
66 | 2649345.3713 | 1224834.4655 | 2649339.2775 | 1224843.4094
67 | 2649360.9668 | 1224844.4675 | 2649345.3713 | 1224834.4655
68 | 2649360.9668 | 1224844.4675 | 2649358.0061 | 1224850.4244 | 2649363.2373 | 1224854.0812 | 2649364.7433 | 1224857.1511 | 2649363.5072 | 1224860.8543 | 2649361.1803 | 1224864.4372 | 2649359.7087 | 1224863.6134
69 | 2649276.8213 | 1224828.9498 | 2649221.8328 | 1224793.2746
70 | 2649358.4826 | 1224888.0516 | 2649353.4216 | 1224877.5921 | 2649349.2102 | 1224872.5541 | 2649296.8187 | 1224841.9236 | 2649276.8213 | 1224828.9498
71 | 2649358.4826 | 1224888.0516 | 2649192.7863 | 1225085.9251
72 | 2649192.7863 | 1225085.9251 | 2649185.204 | 1225085.1509 | 2649179.6013 | 1225084.2708 | 2649164.6701 | 1225081.0789 | 2649159.1275 | 1225102.2795 | 2649149.4987 | 1225099.2809
73 | 2649135.6043 | 1225094.9539 | 2649149.4987 | 1225099.2809
74 | 2649391.0257 | 1224852.8663 | 2649392.6399 | 1224853.8581
75 | 2649396.5857 | 1224847.0533 | 2649392.6399 | 1224853.8581
76 | 2649392.6399 | 1224853.8581 | 2649388.2173 | 1224861.4928 | 2649399.4478 | 1224868.5014 | 2649400.909 | 1224870.5703 | 2649396.0214 | 1224873.943
77 | 2649396.0214 | 1224873.943 | 2649389.563 | 1224878.3922
78 | 2649391.6831 | 1224871.4055 | 2649396.0214 | 1224873.943
79 | 2649389.563 | 1224878.3922 | 2649382.1592 | 1224883.4895 | 2649379.3822 | 1224881.9211
80 | 2649385.9661 | 1224876.0498 | 2649389.563 | 1224878.3922
81 | 2649393.2503 | 1224845.1689 | 2649396.5857 | 1224847.0533
82 | 2649324.9824 | 1224697.4378 | 2649317.1741 | 1224707.761
83 | 2649305.9295 | 1224724.2016 | 2649316.252 | 1224708.9802 | 2649317.1741 | 1224707.761
84 | 2649289.6308 | 1224699.1649 | 2649284.3368 | 1224706.7369
85 | 2649285.5294 | 1224696.3959 | 2649289.6308 | 1224699.1649
86 | 2649280.0705 | 1224703.7331 | 2649284.3368 | 1224706.7369
87 | 2649284.3368 | 1224706.7369 | 2649273.0695 | 1224722.4311
88 | 2649305.9295 | 1224724.2016 | 2649290.1355 | 1224747.4915
89 | 2649331.8675 | 1224628.7823 | 2649335.9162 | 1224630.6058
90 | 2649342.7382 | 1224616.1534 | 2649335.9162 | 1224630.6058
91 | 2649302.9232 | 1224631.1158 | 2649289.8822 | 1224623.0312 | 2649263.4432 | 1224611.5946
92 | 2649244.2571 | 1224607.2552 | 2649244.998 | 1224612.9982 | 2649243.6287 | 1224619.0572 | 2649228.6825 | 1224637.7119 | 2649218.3799 | 1224650.1622
93 | 2649244.2571 | 1224607.2552 | 2649241.2592 | 1224603.0389 | 2649236.7635 | 1224598.4322 | 2649231.1915 | 1224594.4614
94 | 2649244.2571 | 1224607.2552 | 2649254.8738 | 1224607.8878
95 | 2649214.1226 | 1224582.2975 | 2649231.1915 | 1224594.4614
96 | 2649254.8738 | 1224607.8878 | 2649263.4432 | 1224611.5946
97 | 2649214.1226 | 1224582.2975 | 2649212.7987 | 1224581.3541
98 | 2649288.736 | 1224749.5552 | 2649290.1355 | 1224747.4915
99 | 2649288.736 | 1224749.5552 | 2649284.2306 | 1224756.1998 | 2649278.6048 | 1224762.6462
100 | 2649273.3872 | 1224757.3331 | 2649278.6048 | 1224762.6462
101 | 2649278.6048 | 1224762.6462 | 2649273.66 | 1224768.331
102 | 2649267.9393 | 1224763.3473 | 2649273.66 | 1224768.331
103 | 2649273.66 | 1224768.331 | 2649272.8181 | 1224769.2913 | 2649266.9659 | 1224773.7901 | 2649252.6085 | 1224780.8757
104 | 2649263.5702 | 1224726.9665 | 2649267.889 | 1224730.0374
105 | 2649267.889 | 1224730.0374 | 2649265.4975 | 1224733.1862 | 2649252.5497 | 1224751.3237 | 2649250.7778 | 1224754.7333
106 | 2649273.0695 | 1224722.4311 | 2649267.889 | 1224730.0374
107 | 2649247.4728 | 1224751.9154 | 2649250.7778 | 1224754.7333
108 | 2649250.7778 | 1224754.7333 | 2649246.6253 | 1224762.715
109 | 2649269.0289 | 1224719.6404 | 2649273.0695 | 1224722.4311
110 | 2649242.014 | 1224759.2526 | 2649246.6253 | 1224762.715
111 | 2649246.6253 | 1224762.715 | 2649246.3711 | 1224763.2021 | 2649243.8298 | 1224772.5424 | 2649245.1201 | 1224778.7792 | 2649248.3327 | 1224780.8515 | 2649252.6085 | 1224780.8757
112 | 2649175.6246 | 1224543.4085 | 2649178.347 | 1224535.7104
113 | 2649175.6246 | 1224543.4085 | 2649175.4066 | 1224544.0251 | 2649175.8783 | 1224550.244 | 2649176.3005 | 1224550.9184
114 | 2649178.4139 | 1224535.5212 | 2649178.347 | 1224535.7104
115 | 2649190.6575 | 1224565.5755 | 2649180.1811 | 1224557.1171 | 2649176.3005 | 1224550.9184
116 | 2649178.4139 | 1224535.5212 | 2649183.2707 | 1224521.7875 | 2649187.6676 | 1224513.9268
117 | 2649190.6575 | 1224565.5755 | 2649212.7987 | 1224581.3541
118 | 2649190.6575 | 1224565.5755 | 2649172.0877 | 1224588.2418
119 | 2649193.6827 | 1224503.1731 | 2649187.6676 | 1224513.9268
120 | 2649166.7962 | 1224594.7006 | 2649172.0877 | 1224588.2418
121 | 2649193.6827 | 1224503.1731 | 2649169.6448 | 1224480.8321
122 | 2649193.6827 | 1224503.1731 | 2649197.7513 | 1224497.103 | 2649200.0127 | 1224494.282
123 | 2649221.9815 | 1224467.2445 | 2649230.0131 | 1224459.9159
124 | 2649221.9815 | 1224467.2445 | 2649220.8872 | 1224468.243 | 2649208.8823 | 1224483.218
125 | 2649263.8617 | 1224437.6932 | 2649231.2235 | 1224458.8115 | 2649230.0131 | 1224459.9159
126 | 2649200.0127 | 1224494.282 | 2649208.8823 | 1224483.218
127 | 2649273.7736 | 1224431.2797 | 2649263.8617 | 1224437.6932
128 | 2649273.7736 | 1224431.2797 | 2649255.3968 | 1224417.3191 | 2649249.673 | 1224413.2576
129 | 2649273.7736 | 1224431.2797 | 2649300.6436 | 1224450.1249
130 | 2649169.6448 | 1224480.8321 | 2649166.3388 | 1224477.7596
131 | 2649121.1197 | 1224435.7327 | 2649166.3388 | 1224477.7596
132 | 2648740.6806 | 1224275.5201 | 2648729.2722 | 1224220.5374 | 2648711.0828 | 1224135.7918
133 | 2649121.1197 | 1224435.7327 | 2648740.6806 | 1224275.5201
134 | 2649121.1197 | 1224435.7327 | 2649149.2177 | 1224393.0173
135 | 2649342.7382 | 1224616.1534 | 2649353.9915 | 1224621.3943 | 2649355.6034 | 1224618.1057
136 | 2649347.9473 | 1224605.1231 | 2649342.7382 | 1224616.1534
137 | 2649343.9362 | 1224603.3443 | 2649347.9473 | 1224605.1231
138 | 2649353.6273 | 1224593.085 | 2649347.9473 | 1224605.1231
139 | 2649353.6273 | 1224593.085 | 2649364.178 | 1224598.031 | 2649362.9063 | 1224600.5331
140 | 2649357.6143 | 1224584.068 | 2649353.6273 | 1224593.085
141 | 2649403.3005 | 1224586.0702 | 2649407.8067 | 1224588.498
142 | 2649393.6996 | 1224533.3581 | 2649384.083 | 1224529.1313 | 2649375.4441 | 1224546.8929 | 2649372.0791 | 1224554.036
143 | 2649372.0791 | 1224554.036 | 2649368.9378 | 1224560.7364
144 | 2649368.9378 | 1224560.7364 | 2649379.4886 | 1224565.6713 | 2649378.2093 | 1224568.1734
145 | 2649368.9378 | 1224560.7364 | 2649360.7537 | 1224577.59
146 | 2649360.7537 | 1224577.59 | 2649357.6143 | 1224584.068
147 | 2649356.5242 | 1224575.6316 | 2649360.7537 | 1224577.59
148 | 2649357.6143 | 1224584.068 | 2649369.2945 | 1224589.0345 | 2649370.9063 | 1224585.7459

## bus_geodata
| x | y | coords
0 | 2649415.4026 | 1224695.0581
1 | 2649399.3471 | 1224686.9663
2 | 2649405.8874 | 1224673.2762
3 | 2649391.1596 | 1224703.3307
4 | 2649362.8397 | 1224669.8198
5 | 2649435.3162 | 1224739.0138
6 | 2649419.5148 | 1224765.2287
7 | 2649416.8344 | 1224650.3621
8 | 2649402.059 | 1224710.0809
9 | 2649380.5876 | 1224721.0874
10 | 2649349.453 | 1224656.7119
11 | 2649377.0457 | 1224653.6053
12 | 2649337.038 | 1224671.8072
13 | 2649387.487 | 1224631.5116
14 | 2649372.8162 | 1224651.6468
15 | 2649414.4746 | 1224773.5906
16 | 2649426.4693 | 1224630.1944
17 | 2649374.7486 | 1224716.6585
18 | 2649373.6939 | 1224730.7208
19 | 2649355.9923 | 1224636.12
20 | 2649332.6183 | 1224647.0553
21 | 2649334.4834 | 1224678.1566
22 | 2649382.6437 | 1224629.5146
23 | 2649397.3715 | 1224609.8357
24 | 2649411.2989 | 1224780.6566
25 | 2649425.897 | 1224797.5659
26 | 2649429.5255 | 1224787.8901
27 | 2649427.1433 | 1224813.6418
28 | 2649423.9372 | 1224811.714
29 | 2649449.9062 | 1224843.3601
30 | 2649422.1738 | 1224819.5597
31 | 2649446.6692 | 1224841.4988
32 | 2649407.0922 | 1224828.9404
33 | 2649403.2465 | 1224835.5681
34 | 2649404.5414 | 1224827.5295
35 | 2649418.6561 | 1224817.7183
36 | 2649420.5264 | 1224859.0927
37 | 2649415.3375 | 1224856.7371
38 | 2649377.4738 | 1224831.0622
39 | 2649369.7385 | 1224851.7781
40 | 2649334.4416 | 1224784.0399
41 | 2649322.6359 | 1224799.8351
42 | 2649342.045 | 1224773.8672
43 | 2649323.4107 | 1224820.3971
44 | 2649342.9189 | 1224772.707
45 | 2649376.0884 | 1224781.8098
46 | 2649319.7275 | 1224827.5488
47 | 2649331.6061 | 1224825.6472
48 | 2649335.524 | 1224767.576
49 | 2649356.4043 | 1224754.6743
50 | 2649364.0866 | 1224801.0444
51 | 2649371.9394 | 1224805.8013
52 | 2649355.4872 | 1224796.7038
53 | 2649376.9409 | 1224780.4827
54 | 2649367.676 | 1224776.8703
55 | 2649345.3713 | 1224834.4655
56 | 2649348.5545 | 1224749.5394
57 | 2649366.0894 | 1224741.3474
58 | 2649384.3223 | 1224785.4136
59 | 2649339.2775 | 1224843.4094
60 | 2649360.9668 | 1224844.4675
61 | 2649276.8213 | 1224828.9498
62 | 2649221.8328 | 1224793.2746
63 | 2649358.4826 | 1224888.0516
64 | 2649192.7863 | 1225085.9251
65 | 2649135.6043 | 1225094.9539
66 | 2649149.4987 | 1225099.2809
67 | 2649392.6399 | 1224853.8581
68 | 2649396.0214 | 1224873.943
69 | 2649389.563 | 1224878.3922
70 | 2649391.6831 | 1224871.4055
71 | 2649391.0257 | 1224852.8663
72 | 2649396.5857 | 1224847.0533
73 | 2649359.7087 | 1224863.6134
74 | 2649379.3822 | 1224881.9211
75 | 2649385.9661 | 1224876.0498
76 | 2649393.2503 | 1224845.1689
77 | 2649324.9824 | 1224697.4378
78 | 2649317.1741 | 1224707.761
79 | 2649289.6308 | 1224699.1649
80 | 2649284.3368 | 1224706.7369
81 | 2649285.5294 | 1224696.3959
82 | 2649305.9295 | 1224724.2016
83 | 2649335.9162 | 1224630.6058
84 | 2649302.9232 | 1224631.1158
85 | 2649218.3799 | 1224650.1622
86 | 2649244.2571 | 1224607.2552
87 | 2649231.1915 | 1224594.4614
88 | 2649254.8738 | 1224607.8878
89 | 2649214.1226 | 1224582.2975
90 | 2649263.4432 | 1224611.5946
91 | 2649290.1355 | 1224747.4915
92 | 2649288.736 | 1224749.5553
93 | 2649278.6048 | 1224762.6462
94 | 2649273.3872 | 1224757.3331
95 | 2649273.66 | 1224768.331
96 | 2649267.889 | 1224730.0374
97 | 2649263.5702 | 1224726.9665
98 | 2649250.7778 | 1224754.7333
99 | 2649273.0695 | 1224722.4311
100 | 2649247.4728 | 1224751.9154
101 | 2649246.6253 | 1224762.715
102 | 2649267.9393 | 1224763.3473
103 | 2649252.6085 | 1224780.8757
104 | 2649269.0289 | 1224719.6404
105 | 2649242.014 | 1224759.2526
106 | 2649175.6246 | 1224543.4085
107 | 2649178.347 | 1224535.7104
108 | 2649176.3005 | 1224550.9184
109 | 2649178.4139 | 1224535.5212
110 | 2649190.6575 | 1224565.5755
111 | 2649187.6676 | 1224513.9268
112 | 2649212.7987 | 1224581.3541
113 | 2649172.0877 | 1224588.2418
114 | 2649193.6827 | 1224503.1731
115 | 2649166.7962 | 1224594.7006
116 | 2649221.9815 | 1224467.2445
117 | 2649230.0131 | 1224459.9159
118 | 2649208.8823 | 1224483.218
119 | 2649263.8617 | 1224437.6932
120 | 2649200.0127 | 1224494.282
121 | 2649273.7736 | 1224431.2797
122 | 2649249.673 | 1224413.2576
123 | 2649300.6436 | 1224450.1249
124 | 2649169.6448 | 1224480.8321
125 | 2649166.3389 | 1224477.7596
126 | 2648711.0828 | 1224135.7918
127 | 2648740.6806 | 1224275.5201
128 | 2649121.1197 | 1224435.7327
129 | 2649149.2177 | 1224393.0173
130 | 2649331.8675 | 1224628.7823
131 | 2649342.7382 | 1224616.1534
132 | 2649355.6034 | 1224618.1057
133 | 2649347.9473 | 1224605.1231
134 | 2649399.2604 | 1224833.5338
135 | 2649280.0705 | 1224703.7331
136 | 2649343.9362 | 1224603.3443
137 | 2649353.6273 | 1224593.085
138 | 2649393.142 | 1224607.8772
139 | 2649407.8067 | 1224588.498
140 | 2649403.3005 | 1224586.0702
141 | 2649393.6996 | 1224533.3581
142 | 2649372.0791 | 1224554.036
143 | 2649368.9378 | 1224560.7364
144 | 2649378.2093 | 1224568.1734
145 | 2649360.7537 | 1224577.59
146 | 2649357.6142 | 1224584.068
147 | 2649356.5242 | 1224575.6316
148 | 2649370.9063 | 1224585.7459
149 | 2649362.9063 | 1224600.5331
150 | 2649317.1741 | 1224707.761

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99034 | -0.06709 | 0.0023967 | 0.00060067
1 | 0.99041 | -0.066652 | 0 | 0
2 | 0.99014 | -0.068516 | 0.0065946 | 0.0016528
3 | 0.98944 | -0.073399 | 0 | 0
4 | 0.99307 | -0.048071 | 0 | 0
5 | 0.97238 | -0.19454 | 0.0019061 | 0.00047771
6 | 0.97247 | -0.19392 | 0.001769 | 0.00044337
7 | 0.98994 | -0.069932 | 0.0023128 | 0.00057963
8 | 0.9894 | -0.073678 | 0.0021429 | 0.00053707
9 | 0.98837 | -0.0809 | 0 | 0
10 | 0.99128 | -0.060648 | 0 | 0
11 | 0.99252 | -0.05191 | 0 | 0
12 | 0.99586 | -0.028647 | 0.0031096 | 0.00077935
13 | 0.99216 | -0.054483 | 0 | 0
14 | 0.9925 | -0.052065 | 0.0032856 | 0.00082345
15 | 0.97252 | -0.19355 | 0.0019186 | 0.00048084
16 | 0.98984 | -0.070652 | 0.0031608 | 0.00079217
17 | 0.98834 | -0.081103 | 0.0027113 | 0.00067951
18 | 0.98778 | -0.085088 | 0.00083486 | 0.00020924
19 | 0.99117 | -0.061377 | 0.0029754 | 0.00074571
20 | 0.98955 | -0.072776 | 0 | 0
21 | 0.99653 | -0.023957 | 0.0029316 | 0.00073474
22 | 0.99213 | -0.054657 | 0.0032872 | 0.00082386
23 | 0.99192 | -0.056198 | 0 | 0
24 | 0.97258 | -0.19309 | 0 | 0
25 | 0.97279 | -0.19163 | 0 | 0
26 | 0.97268 | -0.1924 | 0.0070748 | 0.0017731
27 | 0.9732 | -0.18867 | 0 | 0
28 | 0.97318 | -0.18879 | 0.0030627 | 0.00076758
29 | 0.97246 | -0.19394 | 0 | 0
30 | 0.97348 | -0.18665 | 0 | 0
31 | 0.97242 | -0.1943 | 0.0090389 | 0.0022654
32 | 0.97471 | -0.17778 | 0 | 0
33 | 0.97513 | -0.17478 | 0 | 0
34 | 0.97471 | -0.17782 | 0.0015676 | 0.00039288
35 | 0.97346 | -0.18678 | 0.002996 | 0.00075088
36 | 0.97293 | -0.1906 | 0 | 0
37 | 0.97286 | -0.19107 | 0.0079195 | 0.0019848
38 | 0.97827 | -0.15231 | 0.0033943 | 0.00085069
39 | 0.97838 | -0.15152 | 0 | 0
40 | 0.98466 | -0.10701 | 0.00094883 | 0.0002378
41 | 0.98385 | -0.11272 | 0.0021749 | 0.00054509
42 | 0.98519 | -0.10329 | 0 | 0
43 | 0.98284 | -0.1199 | 0 | 0
44 | 0.98526 | -0.10282 | 0 | 0
45 | 0.98461 | -0.10743 | 0 | 0
46 | 0.98278 | -0.12028 | 0.0044799 | 0.0011228
47 | 0.98228 | -0.12382 | 0.0035335 | 0.00088559
48 | 0.98523 | -0.10303 | 0.0023517 | 0.00058938
49 | 0.98632 | -0.09534 | 0 | 0
50 | 0.98445 | -0.10857 | 0 | 0
51 | 0.98441 | -0.10882 | 0.0027326 | 0.00068485
52 | 0.98442 | -0.10878 | 0.0021456 | 0.00053773
53 | 0.9846 | -0.10746 | 0 | 0
54 | 0.98458 | -0.10765 | 0.0022446 | 0.00056254
55 | 0.9814 | -0.1301 | 0 | 0
56 | 0.98627 | -0.09568 | 0.0035409 | 0.00088742
57 | 0.98712 | -0.089675 | 0.0022844 | 0.00057252
58 | 0.98457 | -0.10766 | 0.0021766 | 0.0005455
59 | 0.98134 | -0.13054 | 0.0039259 | 0.00098393
60 | 0.9795 | -0.1436 | 0 | 0
61 | 0.97664 | -0.16401 | 0.0017342 | 0.00043463
62 | 0.97628 | -0.16659 | 0.0037546 | 0.000941
63 | 0.97746 | -0.15811 | 0 | 0
64 | 0.97329 | -0.18802 | 0 | 0
65 | 0.97221 | -0.19583 | 0.0049532 | 0.0012414
66 | 0.97231 | -0.19507 | 0.006077 | 0.001523
67 | 0.97635 | -0.16605 | 0 | 0
68 | 0.97614 | -0.16756 | 0 | 0
69 | 0.9761 | -0.16783 | 0 | 0
70 | 0.97613 | -0.16764 | 0.0015474 | 0.00038781
71 | 0.97635 | -0.16608 | 0.0016688 | 0.00041825
72 | 0.97589 | -0.16937 | 0 | 0
73 | 0.97936 | -0.14457 | 0.0035428 | 0.00088791
74 | 0.97608 | -0.16802 | 0.0014948 | 0.00037464
75 | 0.97609 | -0.1679 | 0.0016984 | 0.00042565
76 | 0.97588 | -0.16943 | 0.0015263 | 0.00038252
77 | 0.99869 | -0.0090197 | 0.001814 | 0.00045464
78 | 1 | 0 | -0.24308 | -0.061172
79 | 0.99537 | -0.032471 | 0 | 0
80 | 0.99537 | -0.032443 | 0 | 0
81 | 0.99537 | -0.032487 | 0.00031033 | 7.7776e-05
82 | 0.99915 | -0.0059148 | 0.0017336 | 0.00043448
83 | 0.98877 | -0.078286 | 0 | 0
84 | 0.98807 | -0.083222 | 0.0005725 | 0.00014348
85 | 0.98524 | -0.10333 | 0.0017342 | 0.00043463
86 | 0.98537 | -0.1024 | 0 | 0
87 | 0.98469 | -0.10724 | 0.0017983 | 0.0004507
88 | 0.98579 | -0.099417 | 0.0013447 | 0.00033701
89 | 0.98397 | -0.11236 | 0.00070646 | 0.00017706
90 | 0.98617 | -0.096676 | 0.0011447 | 0.00028688
91 | 0.99803 | -0.013798 | 0.0015349 | 0.00038469
92 | 0.99793 | -0.014459 | 0 | 0
93 | 0.99731 | -0.018854 | 0 | 0
94 | 0.99727 | -0.019085 | 0.0030952 | 0.00077574
95 | 0.99706 | -0.020618 | 0.0037798 | 0.00094732
96 | 0.99553 | -0.031374 | 0 | 0
97 | 0.99551 | -0.031512 | 0.0025785 | 0.00064623
98 | 0.99587 | -0.028938 | 0 | 0
99 | 0.99545 | -0.03188 | 0 | 0
100 | 0.99586 | -0.02905 | 0.0025697 | 0.00064402
101 | 0.99601 | -0.027977 | 0 | 0
102 | 0.99702 | -0.020854 | 0.0031009 | 0.00077716
103 | 0.99647 | -0.0247 | 0.0032734 | 0.00082038
104 | 0.99544 | -0.032007 | 0.0025701 | 0.00064413
105 | 0.99599 | -0.028127 | 0.0025775 | 0.00064599
106 | 0.98218 | -0.12511 | 6.8114e-05 | 1.7071e-05
107 | 0.98193 | -0.12686 | 0.00032534 | 8.1538e-05
108 | 0.98241 | -0.12346 | 0.00060636 | 0.00015197
109 | 0.98193 | -0.1269 | 0.000952 | 0.00023859
110 | 0.98305 | -0.11887 | 0 | 0
111 | 0.98127 | -0.13164 | 9.1926e-05 | 2.3039e-05
112 | 0.98391 | -0.11275 | 0.0011876 | 0.00029763
113 | 0.98303 | -0.119 | 0.00014833 | 3.7176e-05
114 | 0.98092 | -0.13411 | 0 | 0
115 | 0.98303 | -0.11903 | 0.0002911 | 7.2958e-05
116 | 0.98017 | -0.1395 | 0.0014894 | 0.00037328
117 | 0.98003 | -0.14049 | 0.0015301 | 0.00038347
118 | 0.98048 | -0.13728 | 0.0014154 | 0.00035473
119 | 0.9796 | -0.14356 | 0.0011477 | 0.00028764
120 | 0.98072 | -0.13556 | 0.0010456 | 0.00026206
121 | 0.97949 | -0.14431 | 0 | 0
122 | 0.97935 | -0.14537 | 0.0033727 | 0.00084528
123 | 0.97936 | -0.14526 | 0.0027557 | 0.00069065
124 | 0.98061 | -0.13634 | 0.001502 | 0.00037645
125 | 0.98058 | -0.13658 | 0.0019414 | 0.00048656
126 | 0.979 | -0.14805 | 0.0016154 | 0.00040485
127 | 0.97934 | -0.14564 | 0 | 0
128 | 0.98031 | -0.13857 | 0 | 0
129 | 0.9802 | -0.13933 | 0.0014282 | 0.00035795
130 | 0.98875 | -0.078435 | 0.0032856 | 0.00082346
131 | 0.98813 | -0.082846 | 0 | 0
132 | 0.98807 | -0.083257 | 0.0025088 | 0.00062876
133 | 0.98768 | -0.086016 | 0 | 0
134 | 0.97512 | -0.17485 | 0.0015782 | 0.00039554
135 | 0.99535 | -0.032578 | 0.0025789 | 0.00064634
136 | 0.98766 | -0.086164 | 0.0032864 | 0.00082366
137 | 0.98726 | -0.089032 | 0 | 0
138 | 0.99189 | -0.056353 | 0.0032887 | 0.00082424
139 | 0.99179 | -0.057115 | 0 | 0
140 | 0.99176 | -0.057312 | 0.0038069 | 0.00095411
141 | 0.98581 | -0.099325 | 0.0098866 | 0.0024778
142 | 0.98635 | -0.095456 | 0 | 0
143 | 0.98646 | -0.094706 | 0 | 0
144 | 0.9864 | -0.095145 | 0.0029658 | 0.00074331
145 | 0.9868 | -0.092237 | 0 | 0
146 | 0.98698 | -0.091008 | 0 | 0
147 | 0.98678 | -0.092418 | 0.0038069 | 0.00095411
148 | 0.98691 | -0.091494 | 0.0029064 | 0.00072842
149 | 0.9872 | -0.08941 | 0.0025609 | 0.00064181
150 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0023967 | -0.00060067 | 0.0023968 | 0.00060049 | 1.4548e-07 | -1.754e-07 | 0.0036011 | 0.003601 | 0.0036011 | 0.99034 | -0.06709 | 0.99041 | -0.066652 | 1.3337
1 | 0.012073 | 0.0030255 | -0.01207 | -0.0030245 | 3.1147e-06 | 1.0028e-06 | 0.018138 | 0.018138 | 0.018138 | 0.99041 | -0.066652 | 0.99014 | -0.068516 | 6.7179
2 | 0.10981 | 0.027682 | -0.10971 | -0.027643 | 0.00010368 | 3.9169e-05 | 0.16504 | 0.16504 | 0.16504 | 0.99041 | -0.066652 | 0.98944 | -0.073399 | 20.3754
3 | -0.12428 | -0.031308 | 0.1246 | 0.031431 | 0.00032383 | 0.00012282 | 0.18678 | 0.18678 | 0.18678 | 0.99041 | -0.066652 | 0.99307 | -0.048071 | 23.0592
4 | 0.0054749 | 0.0013717 | -0.0054739 | -0.0013716 | 1.0727e-06 | 8.6036e-08 | 0.0082278 | 0.0082279 | 0.0082279 | 0.99014 | -0.068516 | 0.98994 | -0.069932 | 3.0474
5 | 0.002143 | 0.00053694 | -0.0021429 | -0.00053707 | 8.2915e-08 | -1.3241e-07 | 0.0032228 | 0.0032229 | 0.0032229 | 0.98944 | -0.073399 | 0.9894 | -0.073678 | 1.1937
6 | 0.10756 | 0.027106 | -0.10745 | -0.027063 | 0.00011281 | 4.259e-05 | 0.16182 | 0.16182 | 0.16182 | 0.98944 | -0.073399 | 0.98837 | -0.0809 | 19.9775
7 | 0.064936 | 0.016328 | -0.064822 | -0.016284 | 0.00011359 | 4.3442e-05 | 0.097319 | 0.097319 | 0.097319 | 0.99307 | -0.048071 | 0.99128 | -0.060648 | 36.0441
8 | 0.013682 | 0.0034293 | -0.013675 | -0.0034269 | 7.2698e-06 | 2.4377e-06 | 0.020501 | 0.020501 | 0.020501 | 0.99307 | -0.048071 | 0.99252 | -0.05191 | 7.5931
9 | -0.20322 | -0.051188 | 0.20378 | 0.0514 | 0.00055352 | 0.00021177 | 0.3046 | 0.3046 | 0.3046 | 0.99307 | -0.048071 | 0.99586 | -0.028647 | 37.6048
10 | -0.0019061 | -0.00047771 | 0.0019062 | 0.00047739 | 1.6249e-07 | -3.1723e-07 | 0.0029168 | 0.0029167 | 0.0029168 | 0.97238 | -0.19454 | 0.97247 | -0.19392 | 1.0803
11 | -0.0036753 | -0.00092076 | 0.0036755 | 0.00092071 | 1.9267e-07 | -4.7036e-08 | 0.0056236 | 0.0056236 | 0.0056236 | 0.97247 | -0.19392 | 0.97252 | -0.19355 | 2.0828
12 | 0.0031611 | 0.000792 | -0.0031608 | -0.00079217 | 3.1488e-07 | -1.6622e-07 | 0.0047515 | 0.0047516 | 0.0047516 | 0.98994 | -0.069932 | 0.98984 | -0.070652 | 1.7598
13 | 0.0027113 | 0.00067944 | -0.0027113 | -0.00067951 | 7.6057e-08 | -6.4493e-08 | 0.004082 | 0.004082 | 0.004082 | 0.98837 | -0.0809 | 0.98834 | -0.081103 | 1.5118
14 | 0.10474 | 0.026384 | -0.10468 | -0.026361 | 6.1305e-05 | 2.3124e-05 | 0.15774 | 0.15774 | 0.15774 | 0.98837 | -0.0809 | 0.98778 | -0.085088 | 19.4736
15 | 0.0029757 | 0.00074552 | -0.0029754 | -0.00074571 | 3.0017e-07 | -1.9532e-07 | 0.0044668 | 0.0044669 | 0.0044669 | 0.99128 | -0.060648 | 0.99117 | -0.061377 | 1.6544
16 | 0.061847 | 0.015539 | -0.061742 | -0.015499 | 0.00010418 | 3.982e-05 | 0.092852 | 0.092852 | 0.092852 | 0.99128 | -0.060648 | 0.98955 | -0.072776 | 34.3898
17 | 0.010389 | 0.0026034 | -0.010385 | -0.0026023 | 3.6979e-06 | 1.1067e-06 | 0.015575 | 0.015576 | 0.015576 | 0.99252 | -0.05191 | 0.99216 | -0.054483 | 5.7687
18 | 0.0032857 | 0.00082342 | -0.0032856 | -0.00082345 | 7.0408e-08 | -3.3015e-08 | 0.004926 | 0.004926 | 0.004926 | 0.99252 | -0.05191 | 0.9925 | -0.052065 | 1.8244
19 | -0.20689 | -0.052179 | 0.20702 | 0.052231 | 0.00013614 | 5.2094e-05 | 0.30925 | 0.30925 | 0.30925 | 0.99586 | -0.028647 | 0.99653 | -0.023957 | 38.1784
20 | 0.0032873 | 0.00082383 | -0.0032872 | -0.00082386 | 7.9267e-08 | -3.7002e-08 | 0.0049302 | 0.0049303 | 0.0049303 | 0.99216 | -0.054483 | 0.99213 | -0.054657 | 1.826
21 | 0.007098 | 0.0017785 | -0.0070963 | -0.0017782 | 1.684e-06 | 3.4023e-07 | 0.010645 | 0.010645 | 0.010645 | 0.99216 | -0.054483 | 0.99192 | -0.056198 | 3.9427
22 | -0.0055941 | -0.0014016 | 0.0055944 | 0.0014016 | 3.5415e-07 | 4.0077e-08 | 0.0085591 | 0.0085591 | 0.0085591 | 0.97252 | -0.19355 | 0.97258 | -0.19309 | 3.17
23 | 0.10384 | 0.026151 | -0.10378 | -0.026126 | 6.6552e-05 | 2.5095e-05 | 0.15648 | 0.15648 | 0.15648 | 0.98778 | -0.085088 | 0.98712 | -0.089675 | 19.3184
24 | 0.031289 | 0.0078501 | -0.031265 | -0.0078411 | 2.3898e-05 | 8.9695e-06 | 0.047053 | 0.047053 | 0.047053 | 0.98955 | -0.072776 | 0.98877 | -0.078286 | 17.4272
25 | 0.030453 | 0.0076489 | -0.030409 | -0.0076324 | 4.4167e-05 | 1.6554e-05 | 0.045799 | 0.045799 | 0.045799 | 0.98955 | -0.072776 | 0.98807 | -0.083222 | 16.9626
26 | -0.20995 | -0.052966 | 0.21039 | 0.053134 | 0.00044086 | 0.00016872 | 0.31362 | 0.31362 | 0.31362 | 0.99653 | -0.023957 | 0.99869 | -0.0090197 | 38.7188
27 | 0.0032888 | 0.0008242 | -0.0032887 | -0.00082424 | 7.0628e-08 | -3.2856e-08 | 0.0049337 | 0.0049337 | 0.0049337 | 0.99192 | -0.056198 | 0.99189 | -0.056353 | 1.8273
28 | 0.0038075 | 0.00095396 | -0.003807 | -0.00095408 | 4.8335e-07 | -1.2053e-07 | 0.0057117 | 0.0057118 | 0.0057118 | 0.99192 | -0.056198 | 0.99179 | -0.057115 | 2.1155
29 | -0.0055944 | -0.0014016 | 0.0055956 | 0.0014017 | 1.1317e-06 | 1.2797e-07 | 0.0085591 | 0.008559 | 0.0085591 | 0.97258 | -0.19309 | 0.97279 | -0.19163 | 3.17
30 | 0.0070755 | 0.0017733 | -0.0070748 | -0.0017731 | 7.5521e-07 | 1.6221e-07 | 0.010823 | 0.010823 | 0.010823 | 0.97279 | -0.19163 | 0.97268 | -0.1924 | 4.0085
31 | -0.012671 | -0.003175 | 0.012676 | 0.0031767 | 5.1881e-06 | 1.7205e-06 | 0.019382 | 0.019382 | 0.019382 | 0.97279 | -0.19163 | 0.9732 | -0.18867 | 7.1785
32 | 0.0030627 | 0.00076756 | -0.0030627 | -0.00076758 | 5.1083e-08 | -2.6736e-08 | 0.0046829 | 0.0046829 | 0.0046829 | 0.9732 | -0.18867 | 0.97318 | -0.18879 | 1.7344
33 | 0.0090459 | 0.0022673 | -0.0090393 | -0.0022655 | 6.6012e-06 | 1.8523e-06 | 0.013831 | 0.013831 | 0.013831 | 0.9732 | -0.18867 | 0.97246 | -0.19394 | 5.1228
34 | -0.024785 | -0.0062116 | 0.024792 | 0.0062142 | 6.9172e-06 | 2.5645e-06 | 0.037896 | 0.037896 | 0.037896 | 0.9732 | -0.18867 | 0.97348 | -0.18665 | 14.0356
35 | 0.0090393 | 0.0022655 | -0.0090389 | -0.0022654 | 4.448e-07 | 1.2485e-07 | 0.013831 | 0.013832 | 0.013832 | 0.97246 | -0.19394 | 0.97242 | -0.1943 | 5.1228
36 | 0.0029961 | 0.00075085 | -0.002996 | -0.00075088 | 5.184e-08 | -2.9306e-08 | 0.0045797 | 0.0045797 | 0.0045797 | 0.97348 | -0.18665 | 0.97346 | -0.18678 | 1.6962
37 | 0.0079243 | 0.001986 | -0.00792 | -0.0019849 | 4.3285e-06 | 1.0774e-06 | 0.012113 | 0.012113 | 0.012113 | 0.97348 | -0.18665 | 0.97293 | -0.1906 | 4.4863
38 | -0.035712 | -0.008951 | 0.035756 | 0.0089676 | 4.3942e-05 | 1.6607e-05 | 0.054588 | 0.054588 | 0.054588 | 0.97348 | -0.18665 | 0.97471 | -0.17778 | 20.218
39 | -0.037324 | -0.0093605 | 0.037339 | 0.0093663 | 1.5516e-05 | 5.872e-06 | 0.056982 | 0.056981 | 0.056982 | 0.97471 | -0.17778 | 0.97513 | -0.17478 | 21.1043
40 | 0.0015676 | 0.00039285 | -0.0015676 | -0.00039288 | 1.0396e-08 | -3.226e-08 | 0.0023931 | 0.0023931 | 0.0023931 | 0.97471 | -0.17778 | 0.97471 | -0.17782 | 0.88635
41 | 0.0015782 | 0.00039549 | -0.0015782 | -0.00039554 | 1.616e-08 | -4.9484e-08 | 0.0024083 | 0.0024083 | 0.0024083 | 0.97513 | -0.17478 | 0.97512 | -0.17485 | 0.89198
42 | -0.038918 | -0.0097618 | 0.038947 | 0.0097729 | 2.9204e-05 | 1.1067e-05 | 0.05939 | 0.05939 | 0.05939 | 0.97513 | -0.17478 | 0.97589 | -0.16937 | 21.9962
43 | 0.00792 | 0.0019849 | -0.0079195 | -0.0019848 | 5.205e-07 | 1.296e-07 | 0.012113 | 0.012113 | 0.012113 | 0.97293 | -0.1906 | 0.97286 | -0.19107 | 4.4863
44 | -0.0033943 | -0.00085069 | 0.0033946 | 0.00085055 | 3.678e-07 | -1.3621e-07 | 0.0051629 | 0.0051628 | 0.0051629 | 0.97827 | -0.15231 | 0.97838 | -0.15152 | 1.9122
45 | -0.066989 | -0.016819 | 0.067063 | 0.016847 | 7.3855e-05 | 2.8263e-05 | 0.10189 | 0.10189 | 0.10189 | 0.97838 | -0.15152 | 0.9795 | -0.1436 | 37.7383
46 | 0.046997 | 0.011805 | -0.046902 | -0.011769 | 9.4709e-05 | 3.6054e-05 | 0.071487 | 0.071487 | 0.071487 | 0.97838 | -0.15152 | 0.97635 | -0.16605 | 26.4766
47 | 0.016597 | 0.0041634 | -0.016582 | -0.004158 | 1.5144e-05 | 5.3467e-06 | 0.025244 | 0.025244 | 0.025244 | 0.97838 | -0.15152 | 0.97746 | -0.15811 | 9.3497
48 | 0.085113 | 0.02142 | -0.085045 | -0.021395 | 6.789e-05 | 2.536e-05 | 0.12865 | 0.12865 | 0.12865 | 0.98466 | -0.10701 | 0.98385 | -0.11272 | 15.8832
49 | -0.086061 | -0.021658 | 0.086106 | 0.021674 | 4.4704e-05 | 1.6709e-05 | 0.13009 | 0.13009 | 0.13009 | 0.98466 | -0.10701 | 0.98519 | -0.10329 | 16.0601
50 | 0.08287 | 0.020849 | -0.082787 | -0.020819 | 8.2908e-05 | 3.0922e-05 | 0.12536 | 0.12536 | 0.12536 | 0.98385 | -0.11272 | 0.98284 | -0.1199 | 15.4771
51 | -0.095412 | -0.024006 | 0.095418 | 0.024008 | 6.2706e-06 | 2.3563e-06 | 0.14414 | 0.14414 | 0.14414 | 0.98519 | -0.10329 | 0.98526 | -0.10282 | 17.7953
52 | 0.0093057 | 0.0023317 | -0.0093003 | -0.0023302 | 5.3294e-06 | 1.4996e-06 | 0.014055 | 0.014055 | 0.014055 | 0.98519 | -0.10329 | 0.98461 | -0.10743 | 5.2056
53 | 0.0044801 | 0.0011228 | -0.0044799 | -0.0011228 | 2.3085e-07 | -1.3108e-08 | 0.0067829 | 0.006783 | 0.006783 | 0.98284 | -0.1199 | 0.98278 | -0.12028 | 2.5122
54 | 0.078307 | 0.019696 | -0.078264 | -0.01968 | 4.27e-05 | 1.6176e-05 | 0.11858 | 0.11858 | 0.11858 | 0.98284 | -0.1199 | 0.98228 | -0.12382 | 21.9596
55 | 0.0023517 | 0.00058929 | -0.0023517 | -0.00058938 | 7.0712e-08 | -8.7201e-08 | 0.0035517 | 0.0035518 | 0.0035518 | 0.98526 | -0.10282 | 0.98523 | -0.10303 | 1.3155
56 | -0.09777 | -0.024598 | 0.097872 | 0.024636 | 0.00010207 | 3.8398e-05 | 0.14769 | 0.14769 | 0.14769 | 0.98526 | -0.10282 | 0.98632 | -0.09534 | 18.2338
57 | 0.0021766 | 0.00054539 | -0.0021766 | -0.00054541 | 1.0641e-08 | -1.5952e-08 | 0.0032895 | 0.0032895 | 0.0032895 | 0.98461 | -0.10743 | 0.9846 | -0.10746 | 1.2183
58 | 0.0022446 | 0.00056244 | -0.0022446 | -0.00056254 | 6.9895e-08 | -9.6915e-08 | 0.0033922 | 0.0033923 | 0.0033923 | 0.98461 | -0.10743 | 0.98458 | -0.10765 | 1.2564
59 | 0.0048791 | 0.0012224 | -0.0048783 | -0.0012224 | 7.6923e-07 | 7.5323e-09 | 0.0073735 | 0.0073736 | 0.0073736 | 0.98461 | -0.10743 | 0.98445 | -0.10857 | 2.731
60 | 0.07473 | 0.018794 | -0.074665 | -0.018769 | 6.5392e-05 | 2.4737e-05 | 0.11323 | 0.11323 | 0.11323 | 0.98228 | -0.12382 | 0.9814 | -0.1301 | 20.9683
61 | 0.003541 | 0.00088737 | -0.0035409 | -0.00088742 | 1.667e-07 | -5.5349e-08 | 0.0053422 | 0.0053422 | 0.0053422 | 0.98632 | -0.09534 | 0.98627 | -0.09568 | 1.9786
62 | -0.10141 | -0.025524 | 0.10149 | 0.025554 | 8.0256e-05 | 3.0236e-05 | 0.15304 | 0.15304 | 0.15304 | 0.98632 | -0.09534 | 0.98712 | -0.089675 | 18.8933
63 | 0.0027327 | 0.00068477 | -0.0027326 | -0.00068485 | 9.7539e-08 | -7.897e-08 | 0.0041305 | 0.0041305 | 0.0041305 | 0.98445 | -0.10857 | 0.98441 | -0.10882 | 1.5298
64 | 0.0021456 | 0.00053763 | -0.0021456 | -0.00053773 | 6.3073e-08 | -9.7923e-08 | 0.0032431 | 0.0032432 | 0.0032432 | 0.98445 | -0.10857 | 0.98442 | -0.10878 | 1.2012
65 | 0.0021766 | 0.00054541 | -0.0021766 | -0.0005455 | 5.9817e-08 | -8.9662e-08 | 0.0032895 | 0.0032895 | 0.0032895 | 0.9846 | -0.10746 | 0.98457 | -0.10766 | 1.2183
66 | 0.0039262 | 0.00098389 | -0.0039259 | -0.00098393 | 2.3913e-07 | -4.4661e-08 | 0.0059529 | 0.005953 | 0.005953 | 0.9814 | -0.1301 | 0.98134 | -0.13054 | 2.2048
67 | 0.070739 | 0.017785 | -0.070606 | -0.017735 | 0.00013277 | 5.0833e-05 | 0.10728 | 0.10728 | 0.10728 | 0.9814 | -0.1301 | 0.9795 | -0.1436 | 39.7319
68 | 0.0035433 | 0.00088776 | -0.0035428 | -0.00088791 | 4.7537e-07 | -1.4806e-07 | 0.0053827 | 0.0053828 | 0.0053828 | 0.9795 | -0.1436 | 0.97936 | -0.14457 | 1.9936
69 | 0.003756 | 0.00094069 | -0.0037546 | -0.000941 | 1.3394e-06 | -3.0477e-07 | 0.0057224 | 0.0057227 | 0.0057227 | 0.97664 | -0.16401 | 0.97628 | -0.16659 | 2.1195
70 | -0.0054902 | -0.0013753 | 0.0054947 | 0.0013758 | 4.4841e-06 | 4.3828e-07 | 0.0083646 | 0.0083642 | 0.0083646 | 0.97664 | -0.16401 | 0.97746 | -0.15811 | 3.098
71 | 0.011087 | 0.0027823 | -0.011042 | -0.0027678 | 4.589e-05 | 1.4429e-05 | 0.01688 | 0.016881 | 0.016881 | 0.97746 | -0.15811 | 0.97329 | -0.18802 | 6.2522
72 | 0.011042 | 0.0027678 | -0.011031 | -0.0027645 | 1.0769e-05 | 3.3901e-06 | 0.016881 | 0.016881 | 0.016881 | 0.97329 | -0.18802 | 0.97231 | -0.19507 | 6.2523
73 | -0.0049532 | -0.0012414 | 0.0049538 | 0.0012414 | 5.2192e-07 | 2.0263e-08 | 0.0075812 | 0.0075812 | 0.0075812 | 0.97221 | -0.19583 | 0.97231 | -0.19507 | 2.8079
74 | 0.0016689 | 0.00041823 | -0.0016688 | -0.00041825 | 7.6334e-09 | -2.0713e-08 | 0.0025434 | 0.0025434 | 0.0025434 | 0.97635 | -0.16605 | 0.97635 | -0.16608 | 0.94201
75 | 0.040492 | 0.010162 | -0.040473 | -0.010155 | 1.8684e-05 | 7.0879e-06 | 0.061717 | 0.061717 | 0.061717 | 0.97635 | -0.16605 | 0.97589 | -0.16937 | 22.8581
76 | 0.0047418 | 0.0011878 | -0.0047408 | -0.0011878 | 9.9498e-07 | 9.2386e-10 | 0.0072265 | 0.0072267 | 0.0072267 | 0.97635 | -0.16605 | 0.97614 | -0.16756 | 2.6765
77 | 0.0031934 | 0.00080005 | -0.0031933 | -0.00080011 | 1.1575e-07 | -5.3334e-08 | 0.0048678 | 0.0048679 | 0.0048679 | 0.97614 | -0.16756 | 0.9761 | -0.16783 | 1.8029
78 | 0.0015474 | 0.00038775 | -0.0015474 | -0.00038781 | 1.7412e-08 | -5.5993e-08 | 0.0023588 | 0.0023588 | 0.0023588 | 0.97614 | -0.16756 | 0.97613 | -0.16764 | 0.87365
79 | 0.0014949 | 0.0003745 | -0.0014948 | -0.00037464 | 3.9385e-08 | -1.3677e-07 | 0.0022788 | 0.0022789 | 0.0022789 | 0.9761 | -0.16783 | 0.97608 | -0.16802 | 0.84402
80 | 0.0016984 | 0.0004256 | -0.0016984 | -0.00042565 | 1.7919e-08 | -4.6656e-08 | 0.0025891 | 0.0025891 | 0.0025891 | 0.9761 | -0.16783 | 0.97609 | -0.1679 | 0.95892
81 | 0.0015263 | 0.00038248 | -0.0015263 | -0.00038252 | 1.2917e-08 | -4.2784e-08 | 0.0023273 | 0.0023273 | 0.0023273 | 0.97589 | -0.16937 | 0.97588 | -0.16943 | 0.86195
82 | -0.21221 | -0.053589 | 0.21248 | 0.053692 | 0.0002694 | 0.0001031 | 0.31633 | 0.31632 | 0.31633 | 0.99869 | -0.0090197 | 1 | 0 | 39.0525
83 | 0.029803 | 0.0074794 | -0.029778 | -0.0074703 | 2.445e-05 | 9.1426e-06 | 0.04435 | 0.044351 | 0.044351 | 1 | 0 | 0.99915 | -0.0059148 | 16.4261
84 | -0.00031033 | -7.7712e-05 | 0.00031033 | 7.7592e-05 | 1.2396e-09 | -1.1952e-07 | 0.0004639 | 0.00046386 | 0.0004639 | 0.99537 | -0.032471 | 0.99537 | -0.032443 | 0.17181
85 | 0.00031033 | 7.7712e-05 | -0.00031033 | -7.7776e-05 | 6.6329e-10 | -6.3942e-08 | 0.0004639 | 0.00046392 | 0.00046392 | 0.99537 | -0.032471 | 0.99537 | -0.032487 | 0.17182
86 | 0.002579 | 0.00064629 | -0.0025789 | -0.00064634 | 4.8304e-08 | -4.9115e-08 | 0.0038554 | 0.0038554 | 0.0038554 | 0.99537 | -0.032443 | 0.99535 | -0.032578 | 1.4279
87 | -0.0028893 | -0.00072388 | 0.0028895 | 0.00072372 | 2.247e-07 | -1.645e-07 | 0.0043192 | 0.0043191 | 0.0043192 | 0.99537 | -0.032443 | 0.99545 | -0.03188 | 1.5997
88 | 0.028045 | 0.0070358 | -0.028014 | -0.0070244 | 3.0635e-05 | 1.1414e-05 | 0.041769 | 0.041769 | 0.041769 | 0.99915 | -0.0059148 | 0.99803 | -0.013798 | 15.4699
89 | 0.0032857 | 0.00082343 | -0.0032856 | -0.00082346 | 6.7587e-08 | -3.0825e-08 | 0.0049447 | 0.0049447 | 0.0049447 | 0.98877 | -0.078286 | 0.98875 | -0.078435 | 1.8314
90 | 0.02798 | 0.0070177 | -0.027962 | -0.0070111 | 1.7677e-05 | 6.5939e-06 | 0.042109 | 0.042109 | 0.042109 | 0.98877 | -0.078286 | 0.98813 | -0.082846 | 15.5959
91 | 0.029836 | 0.0074889 | -0.029781 | -0.007468 | 5.5632e-05 | 2.0833e-05 | 0.044937 | 0.044937 | 0.044937 | 0.98807 | -0.083222 | 0.98617 | -0.096676 | 16.6434
92 | -0.0017342 | -0.00043463 | 0.0017344 | 0.00043406 | 2.2286e-07 | -5.7743e-07 | 0.0026192 | 0.002619 | 0.0026192 | 0.98524 | -0.10333 | 0.98537 | -0.1024 | 0.97007
93 | 0.025535 | 0.0064018 | -0.025518 | -0.0063955 | 1.7121e-05 | 6.3503e-06 | 0.038561 | 0.038561 | 0.038561 | 0.98537 | -0.1024 | 0.98469 | -0.10724 | 14.282
94 | -0.027269 | -0.0068359 | 0.027281 | 0.0068401 | 1.1254e-05 | 4.1931e-06 | 0.04118 | 0.04118 | 0.04118 | 0.98537 | -0.1024 | 0.98579 | -0.099417 | 15.252
95 | 0.023719 | 0.0059448 | -0.023703 | -0.0059386 | 1.6804e-05 | 6.1965e-06 | 0.035844 | 0.035844 | 0.035844 | 0.98469 | -0.10724 | 0.98397 | -0.11236 | 13.2756
96 | -0.028625 | -0.0071771 | 0.028636 | 0.0071812 | 1.0878e-05 | 4.0648e-06 | 0.04321 | 0.04321 | 0.04321 | 0.98579 | -0.099417 | 0.98617 | -0.096676 | 16.0037
97 | 0.022996 | 0.0057615 | -0.022995 | -0.0057611 | 1.2268e-06 | 4.5118e-07 | 0.034776 | 0.034776 | 0.034776 | 0.98397 | -0.11236 | 0.98391 | -0.11275 | 12.8799
98 | 0.026479 | 0.0066397 | -0.026477 | -0.0066388 | 2.4253e-06 | 9.0024e-07 | 0.03948 | 0.03948 | 0.03948 | 0.99803 | -0.013798 | 0.99793 | -0.014459 | 14.6223
99 | 0.026477 | 0.0066388 | -0.026461 | -0.0066328 | 1.6115e-05 | 5.9816e-06 | 0.03948 | 0.03948 | 0.03948 | 0.99793 | -0.014459 | 0.99731 | -0.018854 | 14.6224
100 | 0.0030953 | 0.00077568 | -0.0030952 | -0.00077574 | 9.8968e-08 | -5.8962e-08 | 0.0046183 | 0.0046184 | 0.0046184 | 0.99731 | -0.018854 | 0.99727 | -0.019085 | 1.7105
101 | 0.023365 | 0.0058571 | -0.023359 | -0.005855 | 5.7076e-06 | 2.0971e-06 | 0.034862 | 0.034862 | 0.034862 | 0.99731 | -0.018854 | 0.99706 | -0.020618 | 12.9119
102 | 0.003101 | 0.0007771 | -0.0031009 | -0.00077716 | 1.0124e-07 | -5.9853e-08 | 0.0046279 | 0.004628 | 0.004628 | 0.99706 | -0.020618 | 0.99702 | -0.020854 | 1.7141
103 | 0.016479 | 0.0041306 | -0.016469 | -0.0041274 | 9.3105e-06 | 3.2594e-06 | 0.024593 | 0.024593 | 0.024593 | 0.99706 | -0.020618 | 0.99647 | -0.0247 | 9.1086
104 | 0.0025785 | 0.00064618 | -0.0025785 | -0.00064623 | 4.9024e-08 | -4.9911e-08 | 0.0038541 | 0.0038541 | 0.0038541 | 0.99553 | -0.031374 | 0.99551 | -0.031512 | 1.4275
105 | -0.0080386 | -0.002014 | 0.0080413 | 0.0020147 | 2.7098e-06 | 6.5096e-07 | 0.012015 | 0.012015 | 0.012015 | 0.99553 | -0.031374 | 0.99587 | -0.028938 | 4.45
106 | 0.00546 | 0.0013678 | -0.0054597 | -0.0013678 | 3.8218e-07 | 2.7433e-08 | 0.0081609 | 0.008161 | 0.008161 | 0.99553 | -0.031374 | 0.99545 | -0.03188 | 3.0226
107 | 0.0025697 | 0.00064398 | -0.0025697 | -0.00064402 | 3.9889e-08 | -4.1074e-08 | 0.0038396 | 0.0038396 | 0.0038396 | 0.99587 | -0.028938 | 0.99586 | -0.02905 | 1.4221
108 | -0.010611 | -0.0026586 | 0.010612 | 0.0026591 | 1.4106e-06 | 4.255e-07 | 0.015855 | 0.015854 | 0.015855 | 0.99587 | -0.028938 | 0.99601 | -0.027977 | 5.8721
109 | 0.0025701 | 0.00064408 | -0.0025701 | -0.00064413 | 4.5139e-08 | -4.6352e-08 | 0.0038419 | 0.0038419 | 0.0038419 | 0.99545 | -0.03188 | 0.99544 | -0.032007 | 1.4229
110 | 0.0025776 | 0.00064593 | -0.0025775 | -0.00064599 | 5.3262e-08 | -5.4426e-08 | 0.0038508 | 0.0038509 | 0.0038509 | 0.99601 | -0.027977 | 0.99599 | -0.028127 | 1.4262
111 | -0.01319 | -0.003305 | 0.013196 | 0.003307 | 5.984e-06 | 1.98e-06 | 0.019705 | 0.019705 | 0.019705 | 0.99601 | -0.027977 | 0.99647 | -0.0247 | 7.2983
112 | 0.020657 | 0.0051713 | -0.020652 | -0.0051695 | 4.9895e-06 | 1.8157e-06 | 0.031293 | 0.031293 | 0.031293 | 0.98218 | -0.12511 | 0.98193 | -0.12686 | 11.5901
113 | -0.020725 | -0.0051884 | 0.02073 | 0.0051901 | 4.7279e-06 | 1.7211e-06 | 0.031396 | 0.031396 | 0.031396 | 0.98218 | -0.12511 | 0.98241 | -0.12346 | 11.6283
114 | 0.020326 | 0.005088 | -0.020326 | -0.0050879 | 1.1881e-07 | 4.3159e-08 | 0.0308 | 0.0308 | 0.0308 | 0.98193 | -0.12686 | 0.98193 | -0.1269 | 11.4075
115 | -0.021336 | -0.0053421 | 0.02135 | 0.005347 | 1.3539e-05 | 4.9441e-06 | 0.032315 | 0.032315 | 0.032315 | 0.98241 | -0.12346 | 0.98305 | -0.11887 | 11.9685
116 | 0.019374 | 0.0048493 | -0.019362 | -0.0048448 | 1.2678e-05 | 4.5783e-06 | 0.029358 | 0.029358 | 0.029358 | 0.98193 | -0.1269 | 0.98127 | -0.13164 | 10.8732
117 | -0.021789 | -0.0054567 | 0.021807 | 0.0054635 | 1.8453e-05 | 6.7522e-06 | 0.03298 | 0.03298 | 0.03298 | 0.98305 | -0.11887 | 0.98391 | -0.11275 | 12.2147
118 | 0.00043945 | 0.00010966 | -0.00043944 | -0.00011003 | 8.0876e-09 | -3.6838e-07 | 0.00066501 | 0.00066514 | 0.00066514 | 0.98305 | -0.11887 | 0.98303 | -0.119 | 0.24635
119 | 0.01927 | 0.0048217 | -0.019263 | -0.0048194 | 6.564e-06 | 2.369e-06 | 0.029218 | 0.029218 | 0.029218 | 0.98127 | -0.13164 | 0.98092 | -0.13411 | 10.8216
120 | 0.00029111 | 7.2852e-05 | -0.0002911 | -7.2958e-05 | 1.0116e-09 | -1.0547e-07 | 0.00044061 | 0.00044065 | 0.00044065 | 0.98303 | -0.119 | 0.98303 | -0.11903 | 0.1632
121 | 0.0064922 | 0.0016189 | -0.0064903 | -0.0016186 | 1.985e-06 | 3.4934e-07 | 0.0098455 | 0.0098457 | 0.0098457 | 0.98092 | -0.13411 | 0.98061 | -0.13634 | 3.6466
122 | 0.012771 | 0.0032004 | -0.012768 | -0.0031996 | 2.5581e-06 | 8.4602e-07 | 0.019373 | 0.019373 | 0.019373 | 0.98092 | -0.13411 | 0.98072 | -0.13556 | 7.1752
123 | 0.008812 | 0.0022077 | -0.0088108 | -0.0022074 | 1.2141e-06 | 3.2996e-07 | 0.013377 | 0.013377 | 0.013377 | 0.98017 | -0.1395 | 0.98003 | -0.14049 | 4.9546
124 | -0.010301 | -0.002581 | 0.010305 | 0.0025819 | 3.155e-06 | 9.5282e-07 | 0.015639 | 0.015638 | 0.015639 | 0.98017 | -0.1395 | 0.98048 | -0.13728 | 5.792
125 | 0.0072807 | 0.0018239 | -0.0072776 | -0.0018232 | 3.0892e-06 | 6.7791e-07 | 0.011054 | 0.011054 | 0.011054 | 0.98003 | -0.14049 | 0.9796 | -0.14356 | 4.0943
126 | -0.01172 | -0.0029366 | 0.011723 | 0.0029375 | 2.7993e-06 | 8.9777e-07 | 0.017786 | 0.017786 | 0.017786 | 0.98048 | -0.13728 | 0.98072 | -0.13556 | 6.5876
127 | 0.0061299 | 0.0015356 | -0.0061293 | -0.0015355 | 6.3869e-07 | 9.7036e-08 | 0.0093111 | 0.0093112 | 0.0093112 | 0.9796 | -0.14356 | 0.97949 | -0.14431 | 3.4486
128 | 0.0033732 | 0.00084509 | -0.0033727 | -0.00084528 | 4.9316e-07 | -1.8908e-07 | 0.0051243 | 0.0051245 | 0.0051245 | 0.97949 | -0.14431 | 0.97935 | -0.14537 | 1.898
129 | 0.0027561 | 0.00069037 | -0.0027557 | -0.00069065 | 3.5901e-07 | -2.7496e-07 | 0.0041868 | 0.004187 | 0.004187 | 0.97949 | -0.14431 | 0.97936 | -0.14526 | 1.5507
130 | 0.0049882 | 0.0012421 | -0.0049881 | -0.0012421 | 1.6124e-07 | 5.0785e-09 | 0.0075664 | 0.0075665 | 0.0075665 | 0.98061 | -0.13634 | 0.98058 | -0.13658 | 2.8024
131 | 0.0030467 | 0.00075555 | -0.0030458 | -0.00075602 | 8.2242e-07 | -4.6221e-07 | 0.0046204 | 0.0046207 | 0.0046207 | 0.98058 | -0.13658 | 0.98031 | -0.13857 | 1.7114
132 | -0.0016154 | -0.00040485 | 0.0016159 | 0.00040326 | 5.3714e-07 | -1.59e-06 | 0.0024553 | 0.0024546 | 0.0024553 | 0.979 | -0.14805 | 0.97934 | -0.14564 | 0.90936
133 | -0.0016159 | -0.00040326 | 0.0016175 | 0.00039866 | 1.5508e-06 | -4.6028e-06 | 0.0024546 | 0.0024528 | 0.0024546 | 0.97934 | -0.14564 | 0.98031 | -0.13857 | 0.90912
134 | 0.0014284 | 0.00035736 | -0.0014282 | -0.00035795 | 1.4996e-07 | -5.8686e-07 | 0.0021679 | 0.0021681 | 0.0021681 | 0.98031 | -0.13857 | 0.9802 | -0.13933 | 0.80302
135 | 0.0025089 | 0.00062861 | -0.0025088 | -0.00062876 | 1.4291e-07 | -1.5055e-07 | 0.0037781 | 0.0037782 | 0.0037782 | 0.98813 | -0.082846 | 0.98807 | -0.083257 | 1.3993
136 | 0.025453 | 0.0063825 | -0.025442 | -0.0063783 | 1.118e-05 | 4.1437e-06 | 0.038331 | 0.038331 | 0.038331 | 0.98813 | -0.082846 | 0.98768 | -0.086016 | 14.1966
137 | 0.0032865 | 0.00082363 | -0.0032864 | -0.00082366 | 6.6959e-08 | -3.0262e-08 | 0.0049514 | 0.0049514 | 0.0049514 | 0.98768 | -0.086016 | 0.98766 | -0.086164 | 1.8338
138 | 0.022155 | 0.0055547 | -0.022146 | -0.0055513 | 9.2511e-06 | 3.3879e-06 | 0.03338 | 0.03338 | 0.03338 | 0.98768 | -0.086016 | 0.98726 | -0.089032 | 12.3628
139 | 0.002561 | 0.00064168 | -0.0025609 | -0.00064181 | 1.3417e-07 | -1.3292e-07 | 0.0038599 | 0.00386 | 0.00386 | 0.98726 | -0.089032 | 0.9872 | -0.08941 | 1.4296
140 | 0.019585 | 0.0049096 | -0.01958 | -0.0049077 | 5.3593e-06 | 1.9353e-06 | 0.02952 | 0.02952 | 0.02952 | 0.98726 | -0.089032 | 0.98698 | -0.091008 | 10.9332
141 | 0.003807 | 0.00095408 | -0.0038069 | -0.00095411 | 1.0397e-07 | -2.5914e-08 | 0.0057118 | 0.0057119 | 0.0057119 | 0.99179 | -0.057115 | 0.99176 | -0.057312 | 2.1155
142 | -0.0098866 | -0.0024778 | 0.0098919 | 0.0024794 | 5.2967e-06 | 1.551e-06 | 0.014923 | 0.014923 | 0.014923 | 0.98581 | -0.099325 | 0.98635 | -0.095456 | 5.5271
143 | -0.0098919 | -0.0024794 | 0.0098929 | 0.0024797 | 1.0279e-06 | 3.0093e-07 | 0.014923 | 0.014923 | 0.014923 | 0.98635 | -0.095456 | 0.98646 | -0.094706 | 5.5271
144 | 0.002966 | 0.00074319 | -0.0029658 | -0.00074331 | 1.8023e-07 | -1.1488e-07 | 0.004474 | 0.0044741 | 0.0044741 | 0.98646 | -0.094706 | 0.9864 | -0.095145 | 1.6571
145 | -0.012859 | -0.0032229 | 0.012863 | 0.0032243 | 4.3969e-06 | 1.4519e-06 | 0.019397 | 0.019397 | 0.019397 | 0.98646 | -0.094706 | 0.9868 | -0.092237 | 7.1841
146 | -0.01667 | -0.0041784 | 0.016673 | 0.0041794 | 2.8374e-06 | 9.9937e-07 | 0.025138 | 0.025138 | 0.025138 | 0.9868 | -0.092237 | 0.98698 | -0.091008 | 9.3102
147 | 0.003807 | 0.00095409 | -0.0038069 | -0.00095411 | 9.5623e-08 | -2.2626e-08 | 0.0057407 | 0.0057407 | 0.0057407 | 0.9868 | -0.092237 | 0.98678 | -0.092418 | 2.1262
148 | 0.0029066 | 0.00072829 | -0.0029064 | -0.00072842 | 1.9558e-07 | -1.3335e-07 | 0.0043821 | 0.0043822 | 0.0043822 | 0.98698 | -0.091008 | 0.98691 | -0.091494 | 1.623

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24488 | 0.061624

## res_load
| p_mw | q_mvar
0 | 0.0023967 | 0.00060067
1 | 0.0065946 | 0.0016528
2 | 0.0019061 | 0.00047771
3 | 0.001769 | 0.00044337
4 | 0.0023128 | 0.00057963
5 | 0.0021429 | 0.00053707
6 | 0.0031096 | 0.00077935
7 | 0.0032856 | 0.00082345
8 | 0.0019186 | 0.00048084
9 | 0.0031608 | 0.00079217
10 | 0.0027113 | 0.00067951
11 | 0.00083486 | 0.00020924
12 | 0.0029754 | 0.00074571
13 | 0.0029316 | 0.00073474
14 | 0.0032872 | 0.00082386
15 | 0.0070748 | 0.0017731
16 | 0.0030627 | 0.00076758
17 | 0.0090389 | 0.0022654
18 | 0.0015676 | 0.00039288
19 | 0.002996 | 0.00075088
20 | 0.0079195 | 0.0019848
21 | 0.0033943 | 0.00085069
22 | 0.00094883 | 0.0002378
23 | 0.0021749 | 0.00054509
24 | 0.0044799 | 0.0011228
25 | 0.0035335 | 0.00088559
26 | 0.0023517 | 0.00058938
27 | 0.0027326 | 0.00068485
28 | 0.0021456 | 0.00053773
29 | 0.0022446 | 0.00056254
30 | 0.0035409 | 0.00088742
31 | 0.0022844 | 0.00057252
32 | 0.0021766 | 0.0005455
33 | 0.0039259 | 0.00098393
34 | 0.0017342 | 0.00043463
35 | 0.0037546 | 0.000941
36 | 0.0049532 | 0.0012414
37 | 0.006077 | 0.001523
38 | 0.0015474 | 0.00038781
39 | 0.0016688 | 0.00041825
40 | 0.0035428 | 0.00088791
41 | 0.0014948 | 0.00037464
42 | 0.0016984 | 0.00042565
43 | 0.0015263 | 0.00038252
44 | 0.001814 | 0.00045464
45 | 0.0018036 | 0.00045203
46 | 0.00031033 | 7.7776e-05
47 | 0.0017336 | 0.00043448
48 | 0.0005725 | 0.00014348
49 | 0.0017342 | 0.00043463
50 | 0.0017983 | 0.0004507
51 | 0.0013447 | 0.00033701
52 | 0.00070646 | 0.00017706
53 | 0.0011447 | 0.00028688
54 | 0.0015349 | 0.00038469
55 | 0.0030952 | 0.00077574
56 | 0.0037798 | 0.00094732
57 | 0.0025785 | 0.00064623
58 | 0.0025697 | 0.00064402
59 | 0.0031009 | 0.00077716
60 | 0.0032734 | 0.00082038
61 | 0.0025701 | 0.00064413
62 | 0.0025775 | 0.00064599
63 | 6.8114e-05 | 1.7071e-05
64 | 0.00032534 | 8.1538e-05
65 | 0.00060636 | 0.00015197
66 | 0.000952 | 0.00023859
67 | 9.1926e-05 | 2.3039e-05
68 | 0.0011876 | 0.00029763
69 | 0.00014833 | 3.7176e-05
70 | 0.0002911 | 7.2958e-05
71 | 0.0014894 | 0.00037328
72 | 0.0015301 | 0.00038347
73 | 0.0014154 | 0.00035473
74 | 0.0011477 | 0.00028764
75 | 0.0010456 | 0.00026206
76 | 0.0033727 | 0.00084528
77 | 0.0027557 | 0.00069065
78 | 0.001502 | 0.00037645
79 | 0.0019414 | 0.00048656
80 | 0.0016154 | 0.00040485
81 | 0.0014282 | 0.00035795
82 | 0.0032856 | 0.00082346
83 | 0.0025088 | 0.00062876
84 | 0.0015782 | 0.00039554
85 | 0.0025789 | 0.00064634
86 | 0.0032864 | 0.00082366
87 | 0.0032887 | 0.00082424
88 | 0.0038069 | 0.00095411
89 | 0.0098866 | 0.0024778
90 | 0.0029658 | 0.00074331
91 | 0.0038069 | 0.00095411
92 | 0.0029064 | 0.00072842
93 | 0.0025609 | 0.00064181

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1