## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1091-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1091-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1091-5_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1091-5_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1091-5_0_4_node_14 | 0.4 | n |  | TRUE
5 | bus_LV_1091-5_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1091-5_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1091-5_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1091-5_0_4_node_58 | 0.4 | n |  | TRUE
9 | bus_LV_1091-5_0_4_node_57 | 0.4 | n |  | TRUE
10 | bus_LV_1091-5_0_4_node_64 | 0.4 | n |  | TRUE
11 | bus_LV_1091-5_0_4_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_1091-5_0_4_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_1091-5_0_4_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_1091-5_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1091-5_0_4_node_36 | 0.4 | n |  | TRUE
16 | bus_LV_1091-5_0_4_node_112 | 0.4 | n |  | TRUE
17 | bus_LV_1091-5_0_4_node_113 | 0.4 | n |  | TRUE
18 | bus_LV_1091-5_0_4_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1091-5_0_4_node_34 | 0.4 | n |  | TRUE
20 | bus_LV_1091-5_0_4_node_43 | 0.4 | n |  | TRUE
21 | bus_LV_1091-5_0_4_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_1091-5_0_4_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_1091-5_0_4_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_1091-5_0_4_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_1091-5_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1091-5_0_4_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_1091-5_0_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_1091-5_0_4_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_1091-5_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1091-5_0_4_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_1091-5_0_4_node_51 | 0.4 | n |  | TRUE
32 | bus_LV_1091-5_0_4_node_59 | 0.4 | n |  | TRUE
33 | bus_LV_1091-5_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_1091-5_0_4_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_1091-5_0_4_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_1091-5_0_4_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_1091-5_0_4_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_1091-5_0_4_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_1091-5_0_4_node_115 | 0.4 | n |  | TRUE
40 | bus_LV_1091-5_0_4_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_1091-5_0_4_node_114 | 0.4 | n |  | TRUE
42 | bus_LV_1091-5_0_4_node_116 | 0.4 | n |  | TRUE
43 | bus_LV_1091-5_0_4_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_1091-5_0_4_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_1091-5_0_4_node_32 | 0.4 | n |  | TRUE
46 | bus_LV_1091-5_0_4_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_1091-5_0_4_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_1091-5_0_4_node_67 | 0.4 | n |  | TRUE
49 | bus_LV_1091-5_0_4_node_66 | 0.4 | n |  | TRUE
50 | bus_LV_1091-5_0_4_node_56 | 0.4 | n |  | TRUE
51 | bus_LV_1091-5_0_4_node_54 | 0.4 | n |  | TRUE
52 | bus_LV_1091-5_0_4_node_39 | 0.4 | n |  | TRUE
53 | bus_LV_1091-5_0_4_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_1091-5_0_4_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_1091-5_0_4_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_1091-5_0_4_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_1091-5_0_4_node_111 | 0.4 | n |  | TRUE
58 | bus_LV_1091-5_0_4_node_110 | 0.4 | n |  | TRUE
59 | bus_LV_1091-5_0_4_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_1091-5_0_4_node_46 | 0.4 | n |  | TRUE
61 | bus_LV_1091-5_0_4_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_1091-5_0_4_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_1091-5_0_4_node_49 | 0.4 | n |  | TRUE
64 | bus_LV_1091-5_0_4_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_1091-5_0_4_node_65 | 0.4 | n |  | TRUE
66 | bus_LV_1091-5_0_4_node_68 | 0.4 | n |  | TRUE
67 | bus_LV_1091-5_0_4_node_99 | 0.4 | n |  | TRUE
68 | bus_LV_1091-5_0_4_node_63 | 0.4 | n |  | TRUE
69 | bus_LV_1091-5_0_4_node_100 | 0.4 | n |  | TRUE
70 | bus_LV_1091-5_0_4_node_52 | 0.4 | n |  | TRUE
71 | bus_LV_1091-5_0_4_node_53 | 0.4 | n |  | TRUE
72 | bus_LV_1091-5_0_4_node_55 | 0.4 | n |  | TRUE
73 | bus_LV_1091-5_0_4_node_62 | 0.4 | n |  | TRUE
74 | bus_LV_1091-5_0_4_node_60 | 0.4 | n |  | TRUE
75 | bus_LV_1091-5_0_4_node_61 | 0.4 | n |  | TRUE
76 | bus_LV_1091-5_0_4_node_69 | 0.4 | n |  | TRUE
77 | bus_LV_1091-5_0_4_node_70 | 0.4 | n |  | TRUE
78 | bus_LV_1091-5_0_4_node_71 | 0.4 | n |  | TRUE
79 | bus_LV_1091-5_0_4_node_72 | 0.4 | n |  | TRUE
80 | bus_LV_1091-5_0_4_node_73 | 0.4 | n |  | TRUE
81 | bus_LV_1091-5_0_4_node_86 | 0.4 | n |  | TRUE
82 | bus_LV_1091-5_0_4_node_88 | 0.4 | n |  | TRUE
83 | bus_LV_1091-5_0_4_node_82 | 0.4 | n |  | TRUE
84 | bus_LV_1091-5_0_4_node_84 | 0.4 | n |  | TRUE
85 | bus_LV_1091-5_0_4_node_78 | 0.4 | n |  | TRUE
86 | bus_LV_1091-5_0_4_node_90 | 0.4 | n |  | TRUE
87 | bus_LV_1091-5_0_4_node_80 | 0.4 | n |  | TRUE
88 | bus_LV_1091-5_0_4_node_74 | 0.4 | n |  | TRUE
89 | bus_LV_1091-5_0_4_node_75 | 0.4 | n |  | TRUE
90 | bus_LV_1091-5_0_4_node_76 | 0.4 | n |  | TRUE
91 | bus_LV_1091-5_0_4_node_77 | 0.4 | n |  | TRUE
92 | bus_LV_1091-5_0_4_node_95 | 0.4 | n |  | TRUE
93 | bus_LV_1091-5_0_4_node_89 | 0.4 | n |  | TRUE
94 | bus_LV_1091-5_0_4_node_96 | 0.4 | n |  | TRUE
95 | bus_LV_1091-5_0_4_node_101 | 0.4 | n |  | TRUE
96 | bus_LV_1091-5_0_4_node_79 | 0.4 | n |  | TRUE
97 | bus_LV_1091-5_0_4_node_102 | 0.4 | n |  | TRUE
98 | bus_LV_1091-5_0_4_node_91 | 0.4 | n |  | TRUE
99 | bus_LV_1091-5_0_4_node_92 | 0.4 | n |  | TRUE
100 | bus_LV_1091-5_0_4_node_85 | 0.4 | n |  | TRUE
101 | bus_LV_1091-5_0_4_node_87 | 0.4 | n |  | TRUE
102 | bus_LV_1091-5_0_4_node_94 | 0.4 | n |  | TRUE
103 | bus_LV_1091-5_0_4_node_97 | 0.4 | n |  | TRUE
104 | bus_LV_1091-5_0_4_node_93 | 0.4 | n |  | TRUE
105 | bus_LV_1091-5_0_4_node_103 | 0.4 | n |  | TRUE
106 | bus_LV_1091-5_0_4_node_98 | 0.4 | n |  | TRUE
107 | bus_LV_1091-5_0_4_node_105 | 0.4 | n |  | TRUE
108 | bus_LV_1091-5_0_4_node_104 | 0.4 | n |  | TRUE
109 | bus_LV_1091-5_0_4_node_106 | 0.4 | n |  | TRUE
110 | bus_LV_1091-5_0_4_node_108 | 0.4 | n |  | TRUE
111 | bus_LV_1091-5_0_4_node_107 | 0.4 | n |  | TRUE
112 | bus_LV_1091-5_0_4_node_109 | 0.4 | n |  | TRUE
113 | bus_LV_1091-5_0_4_node_117 | 0.4 | n |  | TRUE
114 | bus_MV_131_1_node_200 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1091-5_0_4_load_0 | 0 | 0.00012788 | 3.205e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1091-5_0_4_load_1 | 1 | 0.0034578 | 0.00086661 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1091-5_0_4_load_4 | 3 | 7.9078e-05 | 1.9819e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1091-5_0_4_load_14 | 4 | 0.0027322 | 0.00068474 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1091-5_0_4_load_5 | 7 | 0.0010723 | 0.00026875 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1091-5_0_4_load_58 | 8 | 0.00030179 | 7.5637e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1091-5_0_4_load_64 | 10 | 0.00022581 | 5.6594e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1091-5_0_4_load_13 | 11 | 0.0024468 | 0.00061323 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1091-5_0_4_load_24 | 12 | 0.0020329 | 0.0005095 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1091-5_0_4_load_18 | 13 | 0.0026533 | 0.00066497 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1091-5_0_4_load_112 | 16 | 0.00013483 | 3.3792e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1091-5_0_4_load_113 | 17 | 0.0033227 | 0.00083276 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1091-5_0_4_load_16 | 18 | 0.00065257 | 0.00016355 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1091-5_0_4_load_34 | 19 | 0.00065834 | 0.00016499 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1091-5_0_4_load_43 | 20 | 0.00013477 | 3.3777e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1091-5_0_4_load_9 | 21 | 0.00035646 | 8.9338e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1091-5_0_4_load_10 | 22 | 0.00032005 | 8.0211e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1091-5_0_4_load_11 | 23 | 0.0023934 | 0.00059984 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1091-5_0_4_load_20 | 26 | 0.006089 | 0.001526 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1091-5_0_4_load_23 | 27 | 0.0037507 | 0.00094001 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1091-5_0_4_load_15 | 28 | 0.0014857 | 0.00037234 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1091-5_0_4_load_17 | 29 | 0.00078455 | 0.00019663 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1091-5_0_4_load_19 | 30 | 0.0012024 | 0.00030135 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1091-5_0_4_load_51 | 31 | 0.0010362 | 0.0002597 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1091-5_0_4_load_59 | 32 | 0.0010848 | 0.00027188 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1091-5_0_4_load_25 | 33 | 0.0012105 | 0.00030339 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1091-5_0_4_load_26 | 34 | 0.00075474 | 0.00018916 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1091-5_0_4_load_28 | 36 | 0.00078794 | 0.00019748 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1091-5_0_4_load_29 | 37 | 0.00045614 | 0.00011432 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1091-5_0_4_load_30 | 38 | 0.00075537 | 0.00018931 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1091-5_0_4_load_115 | 39 | 0.00076298 | 0.00019122 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1091-5_0_4_load_114 | 41 | 0.0024129 | 0.00060474 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1091-5_0_4_load_116 | 42 | 0.00077795 | 0.00019497 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1091-5_0_4_load_38 | 43 | 0.0020482 | 0.00051331 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1091-5_0_4_load_31 | 44 | 0.00033536 | 8.4049e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1091-5_0_4_load_32 | 45 | 0.00022316 | 5.5929e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1091-5_0_4_load_33 | 46 | 0.0012815 | 0.00032117 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1091-5_0_4_load_35 | 47 | 0.0014155 | 0.00035477 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1091-5_0_4_load_67 | 48 | 0.00073385 | 0.00018392 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1091-5_0_4_load_66 | 49 | 0.0031988 | 0.00080169 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1091-5_0_4_load_54 | 51 | 0.0010348 | 0.00025935 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1091-5_0_4_load_39 | 52 | 0.000188 | 4.7118e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1091-5_0_4_load_40 | 53 | 0.00015515 | 3.8885e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1091-5_0_4_load_42 | 55 | 0.00085732 | 0.00021486 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1091-5_0_4_load_44 | 56 | 0.0010003 | 0.0002507 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1091-5_0_4_load_111 | 57 | 0.00010682 | 2.6771e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1091-5_0_4_load_110 | 58 | 0.0007087 | 0.00017762 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1091-5_0_4_load_45 | 59 | 0.007703 | 0.0019306 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1091-5_0_4_load_46 | 60 | 0.0015268 | 0.00038266 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1091-5_0_4_load_48 | 62 | 0.0051531 | 0.0012915 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1091-5_0_4_load_49 | 63 | 0.0030267 | 0.00075857 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1091-5_0_4_load_50 | 64 | 0.0015556 | 0.00038988 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1091-5_0_4_load_65 | 65 | 0.0009704 | 0.00024321 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1091-5_0_4_load_68 | 66 | 0.0010969 | 0.0002749 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1091-5_0_4_load_99 | 67 | 0.0010535 | 0.00026404 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1091-5_0_4_load_63 | 68 | 0.0012128 | 0.00030397 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1091-5_0_4_load_100 | 69 | 0.0024006 | 0.00060165 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1091-5_0_4_load_52 | 70 | 0.002698 | 0.00067618 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1091-5_0_4_load_53 | 71 | 0.0013083 | 0.00032788 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1091-5_0_4_load_55 | 72 | 0.0071731 | 0.0017977 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1091-5_0_4_load_62 | 73 | 0.0023133 | 0.00057977 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1091-5_0_4_load_60 | 74 | 0.0062289 | 0.0015611 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1091-5_0_4_load_61 | 75 | 0.0022454 | 0.00056275 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1091-5_0_4_load_69 | 76 | 0.002597 | 0.00065087 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1091-5_0_4_load_70 | 77 | 0.001892 | 0.00047418 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1091-5_0_4_load_73 | 80 | 0.0015541 | 0.00038948 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1091-5_0_4_load_86 | 81 | 0.0019995 | 0.00050113 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1091-5_0_4_load_88 | 82 | 0.002584 | 0.0006476 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1091-5_0_4_load_84 | 84 | 0.0019053 | 0.00047751 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1091-5_0_4_load_90 | 86 | 0.0040622 | 0.0010181 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1091-5_0_4_load_80 | 87 | 0.0042721 | 0.0010707 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1091-5_0_4_load_74 | 88 | 0.0015261 | 0.00038247 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1091-5_0_4_load_75 | 89 | 0.0028414 | 0.00071212 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1091-5_0_4_load_76 | 90 | 0.0035062 | 0.00087874 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1091-5_0_4_load_77 | 91 | 0.0022885 | 0.00057355 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1091-5_0_4_load_95 | 92 | 0.0023896 | 0.00059889 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1091-5_0_4_load_96 | 94 | 0.0016381 | 0.00041055 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1091-5_0_4_load_101 | 95 | 0.0012719 | 0.00031877 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1091-5_0_4_load_79 | 96 | 0.0039749 | 0.00099622 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1091-5_0_4_load_102 | 97 | 0.00402 | 0.0010075 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1091-5_0_4_load_91 | 98 | 0.0033801 | 0.00084713 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1091-5_0_4_load_92 | 99 | 0.0034733 | 0.00087048 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1091-5_0_4_load_85 | 100 | 0.0019475 | 0.0004881 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1091-5_0_4_load_87 | 101 | 0.002025 | 0.00050751 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1091-5_0_4_load_94 | 102 | 0.001946 | 0.00048771 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1091-5_0_4_load_97 | 103 | 0.0012326 | 0.00030891 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1091-5_0_4_load_93 | 104 | 0.0039762 | 0.00099654 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1091-5_0_4_load_103 | 105 | 0.0038158 | 0.00095633 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1091-5_0_4_load_98 | 106 | 0.003929 | 0.00098469 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1091-5_0_4_load_104 | 108 | 0.003593 | 0.0009005 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1091-5_0_4_load_106 | 109 | 0.00080227 | 0.00020107 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1091-5_0_4_load_108 | 110 | 0.00078747 | 0.00019736 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1091-5_0_4_load_107 | 111 | 0.0010033 | 0.00025145 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1091-5_0_4_load_109 | 112 | 0.0012917 | 0.00032373 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1091-5_0_4_load_117 | 113 | 0.0015785 | 0.0003956 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 107 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1091-5_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.075927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1091-5_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.061477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1091-5_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.10646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_1091-5_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.14196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_1091-5_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.15886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_1091-5_0_4_line_5 | NAYY 4x150 SE | 4 | 10 | 0.25418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_1091-5_0_4_line_6 | NAYY 4x150 SE | 5 | 6 | 0.031401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_1091-5_0_4_line_7 | NAYY 4x150 SE | 5 | 7 | 0.066698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1091-5_0_4_line_8 | NAYY 4x150 SE | 6 | 12 | 0.019583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1091-5_0_4_line_9 | NAYY 4x150 SE | 6 | 13 | 0.0054496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_1091-5_0_4_line_10 | NAYY 4x150 SE | 8 | 9 | 0.01461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1091-5_0_4_line_11 | NAYY 4x150 SE | 9 | 15 | 0.004737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1091-5_0_4_line_12 | NAYY 4x150 SE | 10 | 11 | 0.44973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_1091-5_0_4_line_13 | NAYY 4x150 SE | 11 | 23 | 0.013577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_1091-5_0_4_line_14 | NAYY 4x150 SE | 12 | 17 | 0.016202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1091-5_0_4_line_15 | NAYY 4x150 SE | 13 | 18 | 0.010132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_1091-5_0_4_line_16 | NAYY 4x150 SE | 14 | 15 | 0.017628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_1091-5_0_4_line_17 | NAYY 4x150 SE | 14 | 16 | 0.034222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_1091-5_0_4_line_18 | NAYY 4x150 SE | 15 | 19 | 0.045279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_1091-5_0_4_line_19 | NAYY 4x150 SE | 16 | 20 | 0.00023235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_1091-5_0_4_line_20 | NAYY 4x150 SE | 18 | 28 | 0.01237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_1091-5_0_4_line_21 | NAYY 4x150 SE | 19 | 45 | 0.045036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_1091-5_0_4_line_22 | NAYY 4x150 SE | 20 | 54 | 0.010708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_1091-5_0_4_line_23 | NAYY 4x150 SE | 21 | 22 | 0.045481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
24 | LV_1091-5_0_4_line_24 | NAYY 4x150 SE | 21 | 23 | 0.055287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_1091-5_0_4_line_25 | NAYY 4x150 SE | 22 | 24 | 0.031894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_1091-5_0_4_line_26 | NAYY 4x150 SE | 24 | 25 | 0.15622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_1091-5_0_4_line_27 | NAYY 4x150 SE | 25 | 27 | 0.023249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1091-5_0_4_line_28 | NAYY 4x150 SE | 25 | 26 | 0.070572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1091-5_0_4_line_29 | NAYY 4x150 SE | 28 | 29 | 0.0049454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_1091-5_0_4_line_30 | NAYY 4x150 SE | 29 | 30 | 0.017011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_1091-5_0_4_line_31 | NAYY 4x150 SE | 30 | 31 | 0.00085778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_1091-5_0_4_line_32 | NAYY 4x150 SE | 31 | 32 | 0.017763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_1091-5_0_4_line_33 | NAYY 4x150 SE | 32 | 56 | 0.017971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_1091-5_0_4_line_34 | NAYY 4x150 SE | 33 | 34 | 0.002786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1091-5_0_4_line_35 | NAYY 4x150 SE | 33 | 35 | 0.013433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1091-5_0_4_line_36 | NAYY 4x150 SE | 34 | 36 | 0.019726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1091-5_0_4_line_37 | NAYY 4x150 SE | 35 | 37 | 0.02345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1091-5_0_4_line_38 | NAYY 4x150 SE | 35 | 38 | 0.02109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1091-5_0_4_line_39 | NAYY 4x150 SE | 36 | 39 | 0.018923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1091-5_0_4_line_40 | NAYY 4x150 SE | 37 | 40 | 0.010035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1091-5_0_4_line_41 | NAYY 4x150 SE | 38 | 41 | 0.00024395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1091-5_0_4_line_42 | NAYY 4x150 SE | 39 | 42 | 0.017495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1091-5_0_4_line_43 | NAYY 4x150 SE | 40 | 43 | 0.022734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1091-5_0_4_line_44 | NAYY 4x150 SE | 42 | 113 | 0.01009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1091-5_0_4_line_45 | NAYY 4x150 SE | 43 | 50 | 0.021024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1091-5_0_4_line_46 | NAYY 4x150 SE | 44 | 45 | 0.020885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_1091-5_0_4_line_47 | NAYY 4x150 SE | 44 | 46 | 0.050347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_1091-5_0_4_line_48 | NAYY 4x150 SE | 46 | 47 | 0.047638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_1091-5_0_4_line_49 | NAYY 4x150 SE | 47 | 48 | 0.0045329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_1091-5_0_4_line_50 | NAYY 4x150 SE | 48 | 49 | 0.0026543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_1091-5_0_4_line_51 | NAYY 4x150 SE | 49 | 66 | 0.010941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_1091-5_0_4_line_52 | NAYY 4x150 SE | 50 | 51 | 0.017262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1091-5_0_4_line_53 | NAYY 4x150 SE | 51 | 70 | 0.039412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1091-5_0_4_line_54 | NAYY 4x150 SE | 52 | 53 | 0.021949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1091-5_0_4_line_55 | NAYY 4x150 SE | 52 | 54 | 0.027343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1091-5_0_4_line_56 | NAYY 4x150 SE | 53 | 55 | 0.0039047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1091-5_0_4_line_57 | NAYY 4x150 SE | 54 | 56 | 0.027418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
58 | LV_1091-5_0_4_line_58 | NAYY 4x150 SE | 55 | 57 | 0.01612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1091-5_0_4_line_59 | NAYY 4x150 SE | 57 | 58 | 0.016335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1091-5_0_4_line_60 | NAYY 4x150 SE | 59 | 60 | 0.0010214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1091-5_0_4_line_61 | NAYY 4x150 SE | 59 | 61 | 0.018572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1091-5_0_4_line_62 | NAYY 4x150 SE | 60 | 62 | 0.035567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1091-5_0_4_line_63 | NAYY 4x150 SE | 61 | 63 | 0.073759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
64 | LV_1091-5_0_4_line_64 | NAYY 4x150 SE | 61 | 64 | 0.014169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
65 | LV_1091-5_0_4_line_65 | NAYY 4x150 SE | 62 | 65 | 0.016314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1091-5_0_4_line_66 | NAYY 4x150 SE | 63 | 66 | 0.036491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
67 | LV_1091-5_0_4_line_67 | NAYY 4x150 SE | 64 | 67 | 0.037128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
68 | LV_1091-5_0_4_line_68 | NAYY 4x150 SE | 65 | 68 | 0.012702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1091-5_0_4_line_69 | NAYY 4x150 SE | 67 | 69 | 0.026163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
70 | LV_1091-5_0_4_line_70 | NAYY 4x150 SE | 68 | 75 | 0.012935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1091-5_0_4_line_71 | NAYY 4x150 SE | 69 | 107 | 0.041074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
72 | LV_1091-5_0_4_line_72 | NAYY 4x150 SE | 70 | 71 | 0.009437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1091-5_0_4_line_73 | NAYY 4x150 SE | 71 | 72 | 0.018891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1091-5_0_4_line_74 | NAYY 4x150 SE | 72 | 73 | 0.011853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1091-5_0_4_line_75 | NAYY 4x150 SE | 73 | 74 | 0.0069408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1091-5_0_4_line_76 | NAYY 4x150 SE | 74 | 75 | 0.0027292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1091-5_0_4_line_77 | NAYY 4x150 SE | 76 | 77 | 0.0026345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1091-5_0_4_line_78 | NAYY 4x150 SE | 76 | 78 | 0.012313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1091-5_0_4_line_79 | NAYY 4x150 SE | 78 | 79 | 0.025876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1091-5_0_4_line_80 | NAYY 4x150 SE | 78 | 80 | 0.015076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1091-5_0_4_line_81 | NAYY 4x150 SE | 79 | 81 | 0.0095412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1091-5_0_4_line_82 | NAYY 4x150 SE | 79 | 82 | 0.016388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1091-5_0_4_line_83 | NAYY 4x150 SE | 80 | 83 | 0.034584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1091-5_0_4_line_84 | NAYY 4x150 SE | 81 | 84 | 0.020487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1091-5_0_4_line_85 | NAYY 4x150 SE | 82 | 85 | 0.018637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1091-5_0_4_line_86 | NAYY 4x150 SE | 83 | 86 | 0.00073301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1091-5_0_4_line_87 | NAYY 4x150 SE | 83 | 87 | 0.012503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1091-5_0_4_line_88 | NAYY 4x150 SE | 84 | 100 | 0.021528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1091-5_0_4_line_89 | NAYY 4x150 SE | 85 | 93 | 0.04358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1091-5_0_4_line_90 | NAYY 4x150 SE | 85 | 90 | 0.0178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1091-5_0_4_line_91 | NAYY 4x150 SE | 86 | 97 | 0.017584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1091-5_0_4_line_92 | NAYY 4x150 SE | 87 | 96 | 0.042779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1091-5_0_4_line_93 | NAYY 4x150 SE | 88 | 89 | 0.017434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1091-5_0_4_line_94 | NAYY 4x150 SE | 88 | 90 | 0.024833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1091-5_0_4_line_95 | NAYY 4x150 SE | 89 | 91 | 0.023791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1091-5_0_4_line_96 | NAYY 4x150 SE | 91 | 92 | 0.027246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1091-5_0_4_line_97 | NAYY 4x150 SE | 92 | 94 | 0.02122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1091-5_0_4_line_98 | NAYY 4x150 SE | 93 | 95 | 0.010455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1091-5_0_4_line_99 | NAYY 4x150 SE | 95 | 104 | 0.021251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1091-5_0_4_line_100 | NAYY 4x150 SE | 97 | 105 | 0.015762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1091-5_0_4_line_101 | NAYY 4x150 SE | 98 | 99 | 0.016503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1091-5_0_4_line_102 | NAYY 4x150 SE | 99 | 104 | 0.017924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1091-5_0_4_line_103 | NAYY 4x150 SE | 100 | 101 | 0.02099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1091-5_0_4_line_104 | NAYY 4x150 SE | 101 | 102 | 0.022875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1091-5_0_4_line_105 | NAYY 4x150 SE | 102 | 103 | 0.026258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1091-5_0_4_line_106 | NAYY 4x150 SE | 103 | 106 | 0.0020369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1091-5_0_4_line_107 | NAYY 4x150 SE | 105 | 109 | 0.026396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1091-5_0_4_line_108 | NAYY 4x150 SE | 105 | 108 | 0.048034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1091-5_0_4_line_109 | NAYY 4x150 SE | 107 | 108 | 0.11663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1091-5_0_4_line_110 | NAYY 4x150 SE | 109 | 110 | 0.0088419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1091-5_0_4_line_111 | NAYY 4x150 SE | 110 | 111 | 0.02176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1091-5_0_4_line_112 | NAYY 4x150 SE | 111 | 112 | 0.016539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1091-5_0_4_trafo_105 | 0.25 MVA 20/0.4 kV | 114 | 107 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2646458.3483 | 1225936.9217 | 2646533.2809 | 1225924.6711
1 | 2646399.0476 | 1225929.1468 | 2646410.0633 | 1225926.9535 | 2646419.6889 | 1225927.0731 | 2646430.7706 | 1225930.9952 | 2646440.3243 | 1225935.4836 | 2646452.942 | 1225937.8056 | 2646458.3483 | 1225936.9217
2 | 2646399.0476 | 1225929.1468 | 2646404.2773 | 1225933.1011 | 2646406.5026 | 1225937.3989 | 2646411.3975 | 1225970.6797 | 2646414.1979 | 1225980.9301 | 2646419.0158 | 1225985.1925 | 2646442.4401 | 1225994.6031 | 2646460.3696 | 1226001.2577
3 | 2646399.0476 | 1225929.1468 | 2646341.2427 | 1225799.493
4 | 2646483.6917 | 1226158.3925 | 2646460.3696 | 1226001.2577
5 | 2646341.2427 | 1225799.493 | 2646087.2779 | 1225789.1404
6 | 2646486.0925 | 1226189.6972 | 2646483.6917 | 1226158.3925
7 | 2646483.6917 | 1226158.3925 | 2646417.1382 | 1226162.7794
8 | 2646486.0925 | 1226189.6972 | 2646466.6072 | 1226191.6502
9 | 2646486.0925 | 1226189.6972 | 2646491.5307 | 1226189.3435
10 | 2646628.4031 | 1226143.9149 | 2646628.5177 | 1226136.0554 | 2646626.2572 | 1226129.6959
11 | 2646628.4031 | 1226143.9149 | 2646628.3356 | 1226148.6506
12 | 2645761.0615 | 1226098.7229 | 2646087.2779 | 1225789.1404
13 | 2645761.0615 | 1226098.7229 | 2645762.2768 | 1226112.2458
14 | 2646450.4858 | 1226193.266 | 2646466.6072 | 1226191.6502
15 | 2646501.641 | 1226188.6859 | 2646491.5307 | 1226189.3435
16 | 2646610.6695 | 1226149.3461 | 2646628.3356 | 1226148.6506
17 | 2646610.6695 | 1226149.3461 | 2646610.9354 | 1226154.1067 | 2646611.0083 | 1226155.4414 | 2646597.9944 | 1226156.3512 | 2646599.0229 | 1226171.3881
18 | 2646628.3356 | 1226148.6506 | 2646647.8685 | 1226147.6919 | 2646669.5084 | 1226145.7825 | 2646673.3804 | 1226144.7823
19 | 2646599.0229 | 1226171.3881 | 2646599.0388 | 1226171.6199
20 | 2646501.641 | 1226188.6859 | 2646513.9847 | 1226187.883
21 | 2646716.5068 | 1226131.8799 | 2646690.3949 | 1226140.3873 | 2646673.3804 | 1226144.7823
22 | 2646599.7695 | 1226182.3033 | 2646599.0388 | 1226171.6199
23 | 2645801.9784 | 1226144.2783 | 2645826.0374 | 1226154.7934 | 2645832.3729 | 1226158.878 | 2645837.2023 | 1226165.6082 | 2645837.796 | 1226168.9589
24 | 2645801.9784 | 1226144.2783 | 2645771.7371 | 1226131.0612 | 2645765.5308 | 1226125.9437 | 2645762.9415 | 1226119.6422 | 2645762.2768 | 1226112.2458
25 | 2645840.2518 | 1226200.72 | 2645838.8948 | 1226175.1604 | 2645837.796 | 1226168.9589
26 | 2645840.2518 | 1226200.72 | 2645709.6783 | 1226286.4802
27 | 2645709.6783 | 1226286.4802 | 2645710.8706 | 1226290.1361 | 2645709.2144 | 1226294.5816 | 2645701.8494 | 1226300.2064 | 2645697.3461 | 1226303.1723
28 | 2645709.6783 | 1226286.4802 | 2645706.0379 | 1226283.8173 | 2645695.7037 | 1226280.2914 | 2645676.4126 | 1226276.4966 | 2645652.8512 | 1226274.0922 | 2645641.0572 | 1226274.3976
29 | 2646518.9197 | 1226187.562 | 2646513.9847 | 1226187.883
30 | 2646518.9197 | 1226187.562 | 2646535.8944 | 1226186.458
31 | 2646536.7503 | 1226186.4023 | 2646535.8944 | 1226186.458
32 | 2646554.4759 | 1226185.2493 | 2646536.7503 | 1226186.4023
33 | 2646572.4093 | 1226184.0829 | 2646554.4759 | 1226185.2493
34 | 2647073.9236 | 1225949.0103 | 2647072.9831 | 1225946.3878
35 | 2647078.4582 | 1225961.6544 | 2647073.9236 | 1225949.0103
36 | 2647066.3242 | 1225927.8201 | 2647072.9831 | 1225946.3878
37 | 2647078.4582 | 1225961.6544 | 2647100.6229 | 1225953.997
38 | 2647078.4582 | 1225961.6544 | 2647058.524 | 1225968.5419
39 | 2647066.3242 | 1225927.8201 | 2647059.9363 | 1225910.0083
40 | 2647110.1077 | 1225950.7202 | 2647100.6229 | 1225953.997
41 | 2647058.524 | 1225968.5419 | 2647058.2935 | 1225968.6216
42 | 2647059.9363 | 1225910.0083 | 2647054.0304 | 1225893.5402
43 | 2647110.1077 | 1225950.7202 | 2647114.9187 | 1225958.6632 | 2647123.5395 | 1225968.9846
44 | 2647050.6241 | 1225884.0422 | 2647054.0304 | 1225893.5402
45 | 2647137.017 | 1225985.121 | 2647123.5395 | 1225968.9846
46 | 2646736.3647 | 1226125.4101 | 2646716.5068 | 1226131.8799
47 | 2646736.3647 | 1226125.4101 | 2646767.5342 | 1226115.2549 | 2646784.4866 | 1226110.658
48 | 2646784.4866 | 1226110.658 | 2646792.9958 | 1226108.3506 | 2646812.4916 | 1226104.4236 | 2646831.0874 | 1226100.8628
49 | 2646835.5394 | 1226100.0103 | 2646831.0874 | 1226100.8628
50 | 2646838.1463 | 1226099.5111 | 2646835.5394 | 1226100.0103
51 | 2646838.1463 | 1226099.5111 | 2646848.8918 | 1226097.4535
52 | 2647137.017 | 1225985.121 | 2647123.9803 | 1225996.435
53 | 2647093.0897 | 1226020.8564 | 2647110.5861 | 1226008.0593 | 2647123.9803 | 1225996.435
54 | 2646627.0552 | 1226180.5281 | 2646648.9578 | 1226179.103
55 | 2646599.7695 | 1226182.3033 | 2646627.0552 | 1226180.5281
56 | 2646652.8543 | 1226178.8495 | 2646648.9578 | 1226179.103
57 | 2646599.7695 | 1226182.3033 | 2646572.4093 | 1226184.0829
58 | 2646652.8543 | 1226178.8495 | 2646668.9406 | 1226177.8029
59 | 2646685.1323 | 1226176.01 | 2646680.7541 | 1226177.0343 | 2646668.9406 | 1226177.8029
60 | 2646973.7121 | 1226065.8198 | 2646974.6959 | 1226065.5455
61 | 2646955.7954 | 1226070.7088 | 2646966.8703 | 1226067.7276 | 2646973.7121 | 1226065.8198
62 | 2646974.6959 | 1226065.5455 | 2647008.9555 | 1226055.9922
63 | 2646955.7954 | 1226070.7088 | 2646884.6348 | 1226090.1157 | 2646884.6348 | 1226090.1157
64 | 2646955.7954 | 1226070.7088 | 2646957.0708 | 1226077.1895 | 2646954.2715 | 1226084.2162
65 | 2647024.67 | 1226051.6102 | 2647008.9555 | 1226055.9922
66 | 2646848.8918 | 1226097.4535 | 2646866.0856 | 1226094.1611 | 2646884.6348 | 1226090.1157
67 | 2646954.2715 | 1226084.2162 | 2646954.2715 | 1226084.2162 | 2646947.8735 | 1226092.9378 | 2646923.5913 | 1226103.0692
68 | 2647024.67 | 1226051.6102 | 2647035.1103 | 1226048.6989 | 2647036.8712 | 1226048.0881
69 | 2646923.5913 | 1226103.0692 | 2646911.8876 | 1226107.9524 | 2646900.3423 | 1226114.9142
70 | 2647036.8712 | 1226048.0881 | 2647045.0444 | 1226045.253 | 2647049.0915 | 1226043.8466
71 | 2646870.2535 | 1226142.4014 | 2646890.2659 | 1226120.9902 | 2646900.3423 | 1226114.9142
72 | 2647093.0897 | 1226020.8564 | 2647085.4726 | 1226026.4276 | 2647085.4726 | 1226026.4276
73 | 2647085.4726 | 1226026.4276 | 2647068.7236 | 1226035.1658
74 | 2647068.7236 | 1226035.1658 | 2647058.2152 | 1226040.6482
75 | 2647051.6694 | 1226042.9507 | 2647058.0568 | 1226040.7308 | 2647058.2152 | 1226040.6482
76 | 2647051.6694 | 1226042.9507 | 2647049.0915 | 1226043.8466
77 | 2647059.7621 | 1226222.1273 | 2647062.3761 | 1226221.7992
78 | 2647047.5452 | 1226223.6606 | 2647059.7621 | 1226222.1273
79 | 2647022.2925 | 1226228.1306 | 2647026.3958 | 1226225.8727 | 2647047.5452 | 1226223.6606
80 | 2647047.5452 | 1226223.6606 | 2647046.2598 | 1226208.6399
81 | 2647022.2925 | 1226228.1306 | 2647018.8517 | 1226227.125 | 2647012.9203 | 1226227.6708
82 | 2647022.2925 | 1226228.1306 | 2647024.9184 | 1226230.5862 | 2647026.5099 | 1226234.4456 | 2647027.4104 | 1226243.0162
83 | 2647059.1447 | 1226184.0167 | 2647055.1714 | 1226190.934 | 2647044.7048 | 1226192.7302 | 2647045.5677 | 1226200.553 | 2647046.2598 | 1226208.6399
84 | 2646992.5199 | 1226229.5481 | 2647012.9203 | 1226227.6708
85 | 2647029.3579 | 1226261.5515 | 2647027.4104 | 1226243.0162
86 | 2647058.4536 | 1226183.7726 | 2647059.1447 | 1226184.0167
87 | 2647059.1447 | 1226184.0167 | 2647070.9335 | 1226188.1826
88 | 2646992.5199 | 1226229.5481 | 2646971.0826 | 1226231.5208
89 | 2647072.8812 | 1226257.5484 | 2647029.3579 | 1226261.5515
90 | 2647029.3579 | 1226261.5515 | 2647011.6325 | 1226263.18
91 | 2647058.4536 | 1226183.7726 | 2647041.873 | 1226177.9175
92 | 2647110.4762 | 1226204.3806 | 2647108.4797 | 1226203.3187 | 2647089.2353 | 1226194.65 | 2647070.9335 | 1226188.1826
93 | 2646986.904 | 1226265.4519 | 2646969.5434 | 1226267.0469
94 | 2646986.904 | 1226265.4519 | 2647011.6325 | 1226263.18
95 | 2646969.5434 | 1226267.0469 | 2646967.2892 | 1226267.254 | 2646946.0259 | 1226270.6156
96 | 2646919.3075 | 1226275.8302 | 2646930.6494 | 1226273.0465 | 2646946.0259 | 1226270.6156
97 | 2646919.3075 | 1226275.8302 | 2646898.6991 | 1226280.8882
98 | 2647072.8812 | 1226257.5484 | 2647083.2686 | 1226256.3626
99 | 2647104.3828 | 1226253.9522 | 2647083.2686 | 1226256.3626
100 | 2647027.0753 | 1226172.4896 | 2647038.7593 | 1226176.8179 | 2647041.873 | 1226177.9175
101 | 2647138.5876 | 1226250.0474 | 2647122.1911 | 1226251.9192
102 | 2647104.3828 | 1226253.9522 | 2647122.1911 | 1226251.9192
103 | 2646971.0826 | 1226231.5208 | 2646950.1808 | 1226233.4442
104 | 2646927.4024 | 1226235.5403 | 2646950.1808 | 1226233.4442
105 | 2646927.4024 | 1226235.5403 | 2646901.2552 | 1226237.9463
106 | 2646899.2268 | 1226238.133 | 2646901.2552 | 1226237.9463
107 | 2647027.0753 | 1226172.4896 | 2647024.9168 | 1226176.1081 | 2647022.7153 | 1226177.4916 | 2647018.6699 | 1226178.1823 | 2647013.9083 | 1226177.422 | 2647007.1912 | 1226175.6901 | 2647003.4746 | 1226175.8527
108 | 2647027.0753 | 1226172.4896 | 2647015.2432 | 1226167.7155 | 2647002.055 | 1226164.7762 | 2646980.3872 | 1226162.7359
109 | 2646870.2535 | 1226142.4014 | 2646872.008 | 1226148.6857 | 2646878.3729 | 1226152.7939 | 2646888.3182 | 1226153.6728 | 2646908.6144 | 1226154.9223 | 2646930.7754 | 1226158.0655 | 2646959.5266 | 1226160.7716 | 2646980.3872 | 1226162.7359
110 | 2647003.4746 | 1226175.8527 | 2647001.8078 | 1226175.9256 | 2646994.7111 | 1226176.9728
111 | 2646973.1844 | 1226180.1493 | 2646994.7111 | 1226176.9728
112 | 2646956.823 | 1226182.5637 | 2646973.1844 | 1226180.1493

## bus_geodata
| x | y | coords
0 | 2646458.3483 | 1225936.9217
1 | 2646533.2809 | 1225924.6711
2 | 2646399.0476 | 1225929.1468
3 | 2646460.3696 | 1226001.2577
4 | 2646341.2427 | 1225799.493
5 | 2646483.6917 | 1226158.3925
6 | 2646486.0925 | 1226189.6972
7 | 2646417.1382 | 1226162.7794
8 | 2646626.2572 | 1226129.6959
9 | 2646628.4031 | 1226143.9149
10 | 2646087.2779 | 1225789.1404
11 | 2645761.0615 | 1226098.7229
12 | 2646466.6072 | 1226191.6502
13 | 2646491.5307 | 1226189.3435
14 | 2646610.6695 | 1226149.3461
15 | 2646628.3356 | 1226148.6506
16 | 2646599.0229 | 1226171.3881
17 | 2646450.4858 | 1226193.266
18 | 2646501.641 | 1226188.6859
19 | 2646673.3804 | 1226144.7823
20 | 2646599.0388 | 1226171.6199
21 | 2645801.9784 | 1226144.2783
22 | 2645837.796 | 1226168.9589
23 | 2645762.2768 | 1226112.2458
24 | 2645840.2518 | 1226200.72
25 | 2645709.6783 | 1226286.4802
26 | 2645641.0572 | 1226274.3976
27 | 2645697.3461 | 1226303.1723
28 | 2646513.9847 | 1226187.883
29 | 2646518.9197 | 1226187.562
30 | 2646535.8944 | 1226186.458
31 | 2646536.7503 | 1226186.4023
32 | 2646554.4759 | 1226185.2493
33 | 2647073.9236 | 1225949.0103
34 | 2647072.9831 | 1225946.3878
35 | 2647078.4582 | 1225961.6544
36 | 2647066.3242 | 1225927.8201
37 | 2647100.6229 | 1225953.997
38 | 2647058.524 | 1225968.5419
39 | 2647059.9363 | 1225910.0083
40 | 2647110.1077 | 1225950.7202
41 | 2647058.2935 | 1225968.6216
42 | 2647054.0304 | 1225893.5402
43 | 2647123.5395 | 1225968.9846
44 | 2646736.3647 | 1226125.4101
45 | 2646716.5068 | 1226131.8799
46 | 2646784.4866 | 1226110.658
47 | 2646831.0874 | 1226100.8628
48 | 2646835.5394 | 1226100.0103
49 | 2646838.1463 | 1226099.5111
50 | 2647137.017 | 1225985.121
51 | 2647123.9803 | 1225996.435
52 | 2646627.0552 | 1226180.5281
53 | 2646648.9578 | 1226179.103
54 | 2646599.7695 | 1226182.3033
55 | 2646652.8543 | 1226178.8495
56 | 2646572.4093 | 1226184.0829
57 | 2646668.9406 | 1226177.8029
58 | 2646685.1323 | 1226176.01
59 | 2646973.7121 | 1226065.8198
60 | 2646974.6959 | 1226065.5455
61 | 2646955.7954 | 1226070.7088
62 | 2647008.9555 | 1226055.9922
63 | 2646884.6348 | 1226090.1157
64 | 2646954.2715 | 1226084.2162
65 | 2647024.67 | 1226051.6102
66 | 2646848.8918 | 1226097.4535
67 | 2646923.5913 | 1226103.0692
68 | 2647036.8712 | 1226048.0881
69 | 2646900.3423 | 1226114.9142
70 | 2647093.0897 | 1226020.8564
71 | 2647085.4726 | 1226026.4276
72 | 2647068.7236 | 1226035.1658
73 | 2647058.2152 | 1226040.6482
74 | 2647051.6694 | 1226042.9507
75 | 2647049.0915 | 1226043.8466
76 | 2647059.7621 | 1226222.1273
77 | 2647062.3761 | 1226221.7992
78 | 2647047.5452 | 1226223.6606
79 | 2647022.2925 | 1226228.1306
80 | 2647046.2598 | 1226208.6399
81 | 2647012.9203 | 1226227.6708
82 | 2647027.4104 | 1226243.0162
83 | 2647059.1448 | 1226184.0167
84 | 2646992.5199 | 1226229.5481
85 | 2647029.3579 | 1226261.5515
86 | 2647058.4536 | 1226183.7726
87 | 2647070.9335 | 1226188.1826
88 | 2646986.904 | 1226265.4519
89 | 2646969.5434 | 1226267.0469
90 | 2647011.6325 | 1226263.18
91 | 2646946.0259 | 1226270.6156
92 | 2646919.3075 | 1226275.8302
93 | 2647072.8812 | 1226257.5484
94 | 2646898.6991 | 1226280.8882
95 | 2647083.2686 | 1226256.3626
96 | 2647110.4762 | 1226204.3806
97 | 2647041.873 | 1226177.9175
98 | 2647138.5876 | 1226250.0474
99 | 2647122.1911 | 1226251.9192
100 | 2646971.0826 | 1226231.5208
101 | 2646950.1808 | 1226233.4442
102 | 2646927.4024 | 1226235.5403
103 | 2646901.2552 | 1226237.9463
104 | 2647104.3828 | 1226253.9522
105 | 2647027.0753 | 1226172.4896
106 | 2646899.2268 | 1226238.133
107 | 2646870.2535 | 1226142.4014
108 | 2646980.3872 | 1226162.7359
109 | 2647003.4746 | 1226175.8527
110 | 2646994.7111 | 1226176.9728
111 | 2646973.1844 | 1226180.1493
112 | 2646956.823 | 1226182.5637
113 | 2647050.6241 | 1225884.0422
114 | 2646955.7954 | 1226070.7088

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97976 | -0.14333 | 0.00012788 | 3.205e-05
1 | 0.97938 | -0.14607 | 0.0034578 | 0.00086661
2 | 0.98008 | -0.14103 | 0 | 0
3 | 0.98122 | -0.13284 | 7.9078e-05 | 1.9819e-05
4 | 0.97881 | -0.1502 | 0.0027322 | 0.00068474
5 | 0.98292 | -0.12059 | 0 | 0
6 | 0.98327 | -0.11805 | 0 | 0
7 | 0.98282 | -0.12133 | 0.0010723 | 0.00026875
8 | 0.98644 | -0.095396 | 0.00030179 | 7.5637e-05
9 | 0.98645 | -0.09535 | 0 | 0
10 | 0.97688 | -0.16419 | 0.00022581 | 5.6594e-05
11 | 0.9735 | -0.18857 | 0.0024468 | 0.00061323
12 | 0.98312 | -0.11914 | 0.0020329 | 0.0005095
13 | 0.98335 | -0.11751 | 0.0026533 | 0.00066497
14 | 0.9861 | -0.097812 | 0 | 0
15 | 0.98645 | -0.095336 | 0 | 0
16 | 0.98543 | -0.10262 | 0.00013483 | 3.3792e-05
17 | 0.98304 | -0.11969 | 0.0033227 | 0.00083276
18 | 0.9835 | -0.11642 | 0.00065257 | 0.00016355
19 | 0.98735 | -0.088935 | 0.00065834 | 0.00016499
20 | 0.98542 | -0.10266 | 0.00013477 | 3.3777e-05
21 | 0.97313 | -0.19124 | 0.00035646 | 8.9338e-05
22 | 0.97291 | -0.19287 | 0.00032005 | 8.0211e-05
23 | 0.97342 | -0.18919 | 0.0023934 | 0.00059984
24 | 0.97275 | -0.19398 | 0 | 0
25 | 0.97163 | -0.20212 | 0 | 0
26 | 0.971 | -0.20667 | 0.006089 | 0.001526
27 | 0.9715 | -0.20304 | 0.0037507 | 0.00094001
28 | 0.98369 | -0.11505 | 0.0014857 | 0.00037234
29 | 0.98377 | -0.11448 | 0.00078455 | 0.00019663
30 | 0.98405 | -0.11247 | 0.0012024 | 0.00030135
31 | 0.98407 | -0.11236 | 0.0010362 | 0.0002597
32 | 0.98438 | -0.11012 | 0.0010848 | 0.00027188
33 | 0.98446 | -0.10931 | 0.0012105 | 0.00030339
34 | 0.98444 | -0.10944 | 0.00075474 | 0.00018916
35 | 0.98457 | -0.10849 | 0 | 0
36 | 0.98433 | -0.11024 | 0.00078794 | 0.00019748
37 | 0.98488 | -0.10631 | 0.00045614 | 0.00011432
38 | 0.98447 | -0.10918 | 0.00075537 | 0.00018931
39 | 0.98424 | -0.11085 | 0.00076298 | 0.00019122
40 | 0.98502 | -0.10533 | 0 | 0
41 | 0.98447 | -0.10919 | 0.0024129 | 0.00060474
42 | 0.98418 | -0.11127 | 0.00077795 | 0.00019497
43 | 0.98533 | -0.1031 | 0.0020482 | 0.00051331
44 | 0.98868 | -0.079471 | 0.00033536 | 8.4049e-05
45 | 0.98826 | -0.082478 | 0.00022316 | 5.5929e-05
46 | 0.98971 | -0.072174 | 0.0012815 | 0.00032117
47 | 0.99071 | -0.065074 | 0.0014155 | 0.00035477
48 | 0.99081 | -0.064377 | 0.00073385 | 0.00018392
49 | 0.99087 | -0.063962 | 0.0031988 | 0.00080169
50 | 0.98568 | -0.10061 | 0 | 0
51 | 0.98597 | -0.098557 | 0.0010348 | 0.00025935
52 | 0.98514 | -0.10472 | 0.000188 | 4.7118e-05
53 | 0.98508 | -0.10513 | 0.00015515 | 3.8885e-05
54 | 0.98521 | -0.10415 | 0 | 0
55 | 0.98507 | -0.1052 | 0.00085732 | 0.00021486
56 | 0.9847 | -0.1078 | 0.0010003 | 0.0002507
57 | 0.98505 | -0.10534 | 0.00010682 | 2.6771e-05
58 | 0.98503 | -0.10546 | 0.0007087 | 0.00017762
59 | 0.99253 | -0.052226 | 0.007703 | 0.0019306
60 | 0.99246 | -0.052676 | 0.0015268 | 0.00038266
61 | 0.9939 | -0.042616 | 0 | 0
62 | 0.99031 | -0.067815 | 0.0051531 | 0.0012915
63 | 0.99201 | -0.055914 | 0.0030267 | 0.00075857
64 | 0.99461 | -0.037628 | 0.0015556 | 0.00038988
65 | 0.98945 | -0.073923 | 0.0009704 | 0.00024321
66 | 0.99113 | -0.062136 | 0.0010969 | 0.0002749
67 | 0.9965 | -0.024399 | 0.0010535 | 0.00026404
68 | 0.98879 | -0.07856 | 0.0012128 | 0.00030397
69 | 0.99784 | -0.015013 | 0.0024006 | 0.00060165
70 | 0.98669 | -0.093462 | 0.002698 | 0.00067618
71 | 0.98689 | -0.091982 | 0.0013083 | 0.00032788
72 | 0.98735 | -0.088768 | 0.0071731 | 0.0017977
73 | 0.98775 | -0.085883 | 0.0023133 | 0.00057977
74 | 0.98802 | -0.084031 | 0.0062289 | 0.0015611
75 | 0.98814 | -0.083129 | 0.0022454 | 0.00056275
76 | 0.9747 | -0.17713 | 0.002597 | 0.00065087
77 | 0.9747 | -0.17718 | 0.001892 | 0.00047418
78 | 0.97478 | -0.17655 | 0 | 0
79 | 0.97312 | -0.1885 | 0 | 0
80 | 0.97585 | -0.16889 | 0.0015541 | 0.00038948
81 | 0.97291 | -0.19001 | 0.0019995 | 0.00050113
82 | 0.97242 | -0.1935 | 0.002584 | 0.0006476
83 | 0.97838 | -0.15084 | 0 | 0
84 | 0.97252 | -0.19282 | 0.0019053 | 0.00047751
85 | 0.9717 | -0.19868 | 0 | 0
86 | 0.97845 | -0.15039 | 0.0040622 | 0.0010181
87 | 0.97823 | -0.15191 | 0.0042721 | 0.0010707
88 | 0.97094 | -0.20416 | 0.0015261 | 0.00038247
89 | 0.97071 | -0.20585 | 0.0028414 | 0.00071212
90 | 0.97133 | -0.20135 | 0.0035062 | 0.00087874
91 | 0.97049 | -0.20744 | 0.0022885 | 0.00057355
92 | 0.97033 | -0.20861 | 0.0023896 | 0.00059889
93 | 0.97093 | -0.20426 | 0 | 0
94 | 0.97028 | -0.20898 | 0.0016381 | 0.00041055
95 | 0.97074 | -0.2056 | 0.0012719 | 0.00031877
96 | 0.97799 | -0.15369 | 0.0039749 | 0.00099622
97 | 0.98005 | -0.139 | 0.00402 | 0.0010075
98 | 0.97014 | -0.20993 | 0.0033801 | 0.00084713
99 | 0.97022 | -0.20934 | 0.0034733 | 0.00087048
100 | 0.97217 | -0.19534 | 0.0019475 | 0.0004881
101 | 0.97189 | -0.19736 | 0.002025 | 0.00050751
102 | 0.97165 | -0.19908 | 0.001946 | 0.00048771
103 | 0.97145 | -0.20051 | 0.0012326 | 0.00030891
104 | 0.9704 | -0.20804 | 0.0039762 | 0.00099654
105 | 0.98158 | -0.12816 | 0.0038158 | 0.00095633
106 | 0.97144 | -0.2006 | 0.003929 | 0.00098469
107 | 1 | 0 | -0.19085 | -0.048008
108 | 0.98678 | -0.091536 | 0.003593 | 0.0009005
109 | 0.98143 | -0.12922 | 0.00080227 | 0.00020107
110 | 0.98139 | -0.12951 | 0.00078747 | 0.00019736
111 | 0.98132 | -0.13002 | 0.0010033 | 0.00025145
112 | 0.98129 | -0.13025 | 0.0012917 | 0.00032373
113 | 0.98416 | -0.11143 | 0.0015785 | 0.0003956
114 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0034591 | 0.00086616 | -0.0034578 | -0.00086661 | 1.3076e-06 | -4.5291e-07 | 0.0052533 | 0.0052536 | 0.0052536 | 0.97976 | -0.14333 | 0.97938 | -0.14607 | 1.9458
1 | -0.003587 | -0.00089821 | 0.0035881 | 0.00089787 | 1.1383e-06 | -3.3665e-07 | 0.0054475 | 0.0054472 | 0.0054475 | 0.97976 | -0.14333 | 0.98008 | -0.14103 | 2.0176
2 | -0.022031 | -0.0054949 | 0.022055 | 0.0055004 | 2.4759e-05 | 5.4933e-06 | 0.033439 | 0.033437 | 0.033439 | 0.98008 | -0.14103 | 0.98122 | -0.13284 | 4.1282
3 | 0.018442 | 0.004597 | -0.018419 | -0.0045935 | 2.3136e-05 | 3.5389e-06 | 0.027991 | 0.027993 | 0.027993 | 0.98008 | -0.14103 | 0.97881 | -0.1502 | 3.456
4 | -0.022134 | -0.0055202 | 0.022172 | 0.0055285 | 3.7206e-05 | 8.2799e-06 | 0.033557 | 0.033555 | 0.033557 | 0.98122 | -0.13284 | 0.98292 | -0.12059 | 4.1429
5 | 0.015687 | 0.0039088 | -0.015657 | -0.0039068 | 3.0052e-05 | 1.9928e-06 | 0.02384 | 0.023843 | 0.023843 | 0.97881 | -0.1502 | 0.97688 | -0.16419 | 2.9436
6 | -0.023244 | -0.0057964 | 0.023252 | 0.0057984 | 8.0826e-06 | 1.9142e-06 | 0.035178 | 0.035178 | 0.035178 | 0.98292 | -0.12059 | 0.98327 | -0.11805 | 4.343
7 | 0.0010724 | 0.00026794 | -0.0010723 | -0.00026875 | 1.0968e-07 | -8.0312e-07 | 0.0016232 | 0.0016235 | 0.0016235 | 0.98292 | -0.12059 | 0.98282 | -0.12133 | 0.6013
8 | 0.0053567 | 0.0013422 | -0.0053559 | -0.0013421 | 8.0301e-07 | 6.0496e-08 | 0.0081064 | 0.0081065 | 0.0081065 | 0.98327 | -0.11805 | 0.98312 | -0.11914 | 3.0024
9 | -0.028609 | -0.0071406 | 0.028611 | 0.0071412 | 2.1237e-06 | 6.0941e-07 | 0.043284 | 0.043284 | 0.043284 | 0.98327 | -0.11805 | 0.98335 | -0.11751 | 5.3437
10 | -0.00030179 | -7.5637e-05 | 0.0003018 | 7.5451e-05 | 1.8891e-09 | -1.8578e-07 | 0.00045525 | 0.00045518 | 0.00045525 | 0.98644 | -0.095396 | 0.98645 | -0.09535 | 0.16861
11 | -0.0003018 | -7.5451e-05 | 0.0003018 | 7.5391e-05 | 6.1242e-10 | -6.0238e-08 | 0.00045518 | 0.00045516 | 0.00045518 | 0.98645 | -0.09535 | 0.98645 | -0.095336 | 0.16859
12 | 0.015431 | 0.0038502 | -0.01538 | -0.0038471 | 5.167e-05 | 3.0399e-06 | 0.023499 | 0.023505 | 0.023505 | 0.97688 | -0.16419 | 0.9735 | -0.18857 | 2.9019
13 | 0.012933 | 0.0032339 | -0.012932 | -0.003234 | 1.1033e-06 | -8.2045e-08 | 0.019765 | 0.019766 | 0.019766 | 0.9735 | -0.18857 | 0.97342 | -0.18919 | 2.4402
14 | 0.003323 | 0.00083265 | -0.0033227 | -0.00083276 | 2.5575e-07 | -1.0706e-07 | 0.0050295 | 0.0050296 | 0.0050296 | 0.98312 | -0.11914 | 0.98304 | -0.11969 | 1.8628
15 | -0.031264 | -0.0078061 | 0.031269 | 0.0078076 | 4.7146e-06 | 1.4277e-06 | 0.047299 | 0.047299 | 0.047299 | 0.98335 | -0.11751 | 0.9835 | -0.11642 | 5.8394
16 | -0.040898 | -0.010227 | 0.040912 | 0.010232 | 1.3961e-05 | 4.6949e-06 | 0.061707 | 0.061707 | 0.061707 | 0.9861 | -0.097812 | 0.98645 | -0.095336 | 7.6181
17 | 0.040898 | 0.010227 | -0.040871 | -0.010218 | 2.7105e-05 | 9.116e-06 | 0.061707 | 0.061707 | 0.061707 | 0.9861 | -0.097812 | 0.98543 | -0.10262 | 7.6182
18 | -0.041214 | -0.010307 | 0.04125 | 0.01032 | 3.6392e-05 | 1.2261e-05 | 0.062162 | 0.062161 | 0.062162 | 0.98645 | -0.095336 | 0.98735 | -0.088935 | 7.6743
19 | 0.040736 | 0.010184 | -0.040736 | -0.010184 | 1.8282e-07 | 6.1433e-08 | 0.061504 | 0.061504 | 0.061504 | 0.98543 | -0.10262 | 0.98542 | -0.10266 | 7.593
20 | -0.031922 | -0.0079711 | 0.031928 | 0.007973 | 5.9989e-06 | 1.8363e-06 | 0.048286 | 0.048286 | 0.048286 | 0.9835 | -0.11642 | 0.98369 | -0.11505 | 5.9613
21 | -0.041909 | -0.010485 | 0.041946 | 0.010497 | 3.736e-05 | 1.264e-05 | 0.063153 | 0.063153 | 0.063153 | 0.98735 | -0.088935 | 0.98826 | -0.082478 | 7.7967
22 | 0.040601 | 0.010151 | -0.040593 | -0.010148 | 8.3697e-06 | 2.8099e-06 | 0.0613 | 0.0613 | 0.0613 | 0.98542 | -0.10266 | 0.98521 | -0.10415 | 7.5679
23 | 0.010179 | 0.0025457 | -0.010177 | -0.0025465 | 2.2913e-06 | -8.135e-07 | 0.015563 | 0.015563 | 0.015563 | 0.97313 | -0.19124 | 0.97291 | -0.19287 | 1.9214
24 | -0.010535 | -0.0026351 | 0.010538 | 0.0026341 | 2.9835e-06 | -9.1371e-07 | 0.016108 | 0.016107 | 0.016108 | 0.97313 | -0.19124 | 0.97342 | -0.18919 | 1.9886
25 | 0.0098566 | 0.0024663 | -0.009855 | -0.0024669 | 1.5074e-06 | -6.0823e-07 | 0.015074 | 0.015074 | 0.015074 | 0.97291 | -0.19287 | 0.97275 | -0.19398 | 1.861
26 | 0.009855 | 0.0024669 | -0.009844 | -0.0024665 | 1.1076e-05 | 3.8594e-07 | 0.015074 | 0.015076 | 0.015076 | 0.97275 | -0.19398 | 0.97163 | -0.20212 | 2.7918
27 | 0.0037512 | 0.00093991 | -0.0037507 | -0.00094001 | 4.7877e-07 | -1.0376e-07 | 0.0057447 | 0.0057448 | 0.0057448 | 0.97163 | -0.20212 | 0.9715 | -0.20304 | 2.1277
28 | 0.0060928 | 0.0015266 | -0.006089 | -0.001526 | 3.8342e-06 | 6.0118e-07 | 0.0093308 | 0.0093311 | 0.0093311 | 0.97163 | -0.20212 | 0.971 | -0.20667 | 3.456
29 | -0.033413 | -0.0083453 | 0.033416 | 0.0083461 | 2.6268e-06 | 8.2194e-07 | 0.050533 | 0.050533 | 0.050533 | 0.98369 | -0.11505 | 0.98377 | -0.11448 | 6.2387
30 | -0.0342 | -0.0085428 | 0.03421 | 0.0085457 | 9.4645e-06 | 2.9921e-06 | 0.05172 | 0.05172 | 0.05172 | 0.98377 | -0.11448 | 0.98405 | -0.11247 | 6.3852
31 | -0.035412 | -0.0088471 | 0.035413 | 0.0088473 | 5.114e-07 | 1.64e-07 | 0.053538 | 0.053538 | 0.053538 | 0.98405 | -0.11247 | 0.98407 | -0.11236 | 6.6096
32 | -0.036449 | -0.009107 | 0.03646 | 0.0091106 | 1.1219e-05 | 3.6378e-06 | 0.055105 | 0.055105 | 0.055105 | 0.98407 | -0.11236 | 0.98438 | -0.11012 | 6.8031
33 | -0.037545 | -0.0093825 | 0.037557 | 0.0093864 | 1.2036e-05 | 3.9437e-06 | 0.056744 | 0.056744 | 0.056744 | 0.98438 | -0.11012 | 0.9847 | -0.1078 | 7.0055
34 | 0.004663 | 0.0011679 | -0.0046629 | -0.0011679 | 8.6356e-08 | -2.2083e-09 | 0.007048 | 0.007048 | 0.007048 | 0.98446 | -0.10931 | 0.98444 | -0.10944 | 2.6104
35 | -0.0058736 | -0.0014713 | 0.0058742 | 0.0014714 | 6.6061e-07 | 8.327e-08 | 0.0088777 | 0.0088776 | 0.0088777 | 0.98446 | -0.10931 | 0.98457 | -0.10849 | 3.288
36 | 0.0039082 | 0.00097876 | -0.0039078 | -0.00097885 | 4.2952e-07 | -8.5567e-08 | 0.0059072 | 0.0059072 | 0.0059072 | 0.98444 | -0.10944 | 0.98433 | -0.11024 | 2.1879
37 | -0.0090428 | -0.0022653 | 0.0090456 | 0.002266 | 2.733e-06 | 7.5282e-07 | 0.013666 | 0.013666 | 0.013666 | 0.98457 | -0.10849 | 0.98488 | -0.10631 | 5.0616
38 | 0.0031686 | 0.00079389 | -0.0031683 | -0.00079405 | 3.018e-07 | -1.5212e-07 | 0.0047887 | 0.0047888 | 0.0047888 | 0.98457 | -0.10849 | 0.98447 | -0.10918 | 1.7736
39 | 0.0031198 | 0.00078137 | -0.0031196 | -0.00078151 | 2.6263e-07 | -1.395e-07 | 0.0047161 | 0.0047162 | 0.0047162 | 0.98433 | -0.11024 | 0.98424 | -0.11085 | 1.7467
40 | -0.0095017 | -0.0023804 | 0.009503 | 0.0023807 | 1.2904e-06 | 3.686e-07 | 0.014355 | 0.014355 | 0.014355 | 0.98488 | -0.10631 | 0.98502 | -0.10533 | 5.3168
41 | 0.0024129 | 0.00060473 | -0.0024129 | -0.00060474 | 2.0247e-09 | -2.323e-09 | 0.0036471 | 0.0036471 | 0.0036471 | 0.98447 | -0.10918 | 0.98447 | -0.10919 | 1.3508
42 | 0.0023566 | 0.00059029 | -0.0023565 | -0.00059046 | 1.3857e-07 | -1.6904e-07 | 0.0035627 | 0.0035628 | 0.0035628 | 0.98424 | -0.11085 | 0.98418 | -0.11127 | 1.3195
43 | -0.009503 | -0.0023807 | 0.0095059 | 0.0023816 | 2.9234e-06 | 8.3492e-07 | 0.014355 | 0.014355 | 0.014355 | 0.98502 | -0.10533 | 0.98533 | -0.1031 | 5.3168
44 | 0.0015785 | 0.00039549 | -0.0015785 | -0.0003956 | 3.5863e-08 | -1.1443e-07 | 0.0023866 | 0.0023866 | 0.0023866 | 0.98418 | -0.11127 | 0.98416 | -0.11143 | 0.88393
45 | -0.011554 | -0.0028949 | 0.011558 | 0.0028961 | 3.9941e-06 | 1.2683e-06 | 0.017448 | 0.017448 | 0.017448 | 0.98533 | -0.1031 | 0.98568 | -0.10061 | 6.4623
46 | 0.042187 | 0.010559 | -0.042169 | -0.010553 | 1.751e-05 | 5.9316e-06 | 0.063488 | 0.063489 | 0.063489 | 0.98868 | -0.079471 | 0.98826 | -0.082478 | 7.8381
47 | -0.042522 | -0.010643 | 0.042565 | 0.010658 | 4.2884e-05 | 1.4555e-05 | 0.063993 | 0.063992 | 0.063993 | 0.98868 | -0.079471 | 0.98971 | -0.072174 | 7.9004
48 | -0.043846 | -0.010979 | 0.04389 | 0.010994 | 4.3056e-05 | 1.4722e-05 | 0.065919 | 0.065918 | 0.065919 | 0.98971 | -0.072174 | 0.99071 | -0.065074 | 8.1382
49 | -0.045305 | -0.011348 | 0.045309 | 0.01135 | 4.3654e-06 | 1.5039e-06 | 0.068045 | 0.068045 | 0.068045 | 0.99071 | -0.065074 | 0.99081 | -0.064377 | 8.4006
50 | -0.046043 | -0.011534 | 0.046046 | 0.011535 | 2.6397e-06 | 9.1272e-07 | 0.069147 | 0.069147 | 0.069147 | 0.99081 | -0.064377 | 0.99087 | -0.063962 | 8.5366
51 | -0.049245 | -0.012336 | 0.049257 | 0.012341 | 1.2445e-05 | 4.3636e-06 | 0.07395 | 0.07395 | 0.07395 | 0.99087 | -0.063962 | 0.99113 | -0.062136 | 9.1297
52 | -0.011558 | -0.0028961 | 0.011561 | 0.0028972 | 3.2792e-06 | 1.0411e-06 | 0.017448 | 0.017448 | 0.017448 | 0.98568 | -0.10061 | 0.98597 | -0.098557 | 6.4623
53 | -0.012596 | -0.0031565 | 0.012605 | 0.0031594 | 8.8873e-06 | 2.9152e-06 | 0.01901 | 0.01901 | 0.01901 | 0.98597 | -0.098557 | 0.98669 | -0.093462 | 7.0407
54 | 0.0018281 | 0.00045745 | -0.001828 | -0.00045769 | 1.0442e-07 | -2.3928e-07 | 0.0027611 | 0.0027612 | 0.0027612 | 0.98514 | -0.10472 | 0.98508 | -0.10513 | 1.0227
55 | -0.0020161 | -0.00050457 | 0.0020163 | 0.00050428 | 1.582e-07 | -2.8732e-07 | 0.0030451 | 0.0030449 | 0.0030451 | 0.98514 | -0.10472 | 0.98521 | -0.10415 | 1.1278
56 | 0.0016729 | 0.00041881 | -0.0016729 | -0.00041885 | 1.5557e-08 | -4.3726e-08 | 0.0025268 | 0.0025268 | 0.0025268 | 0.98508 | -0.10513 | 0.98507 | -0.1052 | 0.93586
57 | 0.038577 | 0.0096435 | -0.038557 | -0.0096371 | 1.9354e-05 | 6.397e-06 | 0.058255 | 0.058256 | 0.058256 | 0.98521 | -0.10415 | 0.9847 | -0.1078 | 7.1921
58 | 0.00081554 | 0.00020398 | -0.00081553 | -0.00020418 | 1.5264e-08 | -1.9934e-07 | 0.0012318 | 0.0012319 | 0.0012319 | 0.98507 | -0.1052 | 0.98505 | -0.10534 | 0.45625
59 | 0.00070871 | 0.00017741 | -0.0007087 | -0.00017762 | 1.1682e-08 | -2.0345e-07 | 0.0010705 | 0.0010706 | 0.0010706 | 0.98505 | -0.10534 | 0.98503 | -0.10546 | 0.39651
60 | 0.043633 | 0.010961 | -0.043631 | -0.01096 | 2.7281e-06 | 1.0361e-06 | 0.065425 | 0.065425 | 0.065425 | 0.99253 | -0.052226 | 0.99246 | -0.052676 | 24.2315
61 | -0.051336 | -0.012891 | 0.051405 | 0.012918 | 6.8663e-05 | 2.6168e-05 | 0.076974 | 0.076973 | 0.076974 | 0.99253 | -0.052226 | 0.9939 | -0.042616 | 28.5087
62 | 0.042104 | 0.010577 | -0.042015 | -0.010544 | 8.8467e-05 | 3.3567e-05 | 0.063136 | 0.063136 | 0.063136 | 0.99246 | -0.052676 | 0.99031 | -0.067815 | 23.3837
63 | 0.053523 | 0.013425 | -0.053424 | -0.01339 | 9.8523e-05 | 3.5031e-05 | 0.080136 | 0.080137 | 0.080137 | 0.9939 | -0.042616 | 0.99201 | -0.055914 | 9.8934
64 | -0.10493 | -0.026342 | 0.105 | 0.02637 | 7.2744e-05 | 2.7427e-05 | 0.15711 | 0.15711 | 0.15711 | 0.9939 | -0.042616 | 0.99461 | -0.037628 | 19.3962
65 | 0.036862 | 0.009252 | -0.036831 | -0.0092402 | 3.1236e-05 | 1.1804e-05 | 0.055393 | 0.055393 | 0.055393 | 0.99031 | -0.067815 | 0.98945 | -0.073923 | 20.5159
66 | 0.050397 | 0.012631 | -0.050354 | -0.012616 | 4.3377e-05 | 1.5271e-05 | 0.075596 | 0.075597 | 0.075597 | 0.99201 | -0.055914 | 0.99113 | -0.062136 | 9.333
67 | -0.10656 | -0.026759 | 0.10675 | 0.026833 | 0.00019631 | 7.4054e-05 | 0.15944 | 0.15944 | 0.15944 | 0.99461 | -0.037628 | 0.9965 | -0.024399 | 19.6835
68 | 0.035861 | 0.008997 | -0.035837 | -0.0089883 | 2.3057e-05 | 8.7049e-06 | 0.053934 | 0.053934 | 0.053934 | 0.98945 | -0.073923 | 0.98879 | -0.07856 | 19.9755
69 | -0.10781 | -0.027098 | 0.10795 | 0.027151 | 0.00014108 | 5.3236e-05 | 0.16101 | 0.16101 | 0.16101 | 0.9965 | -0.024399 | 0.99784 | -0.015013 | 19.8776
70 | 0.034625 | 0.0086843 | -0.034603 | -0.0086761 | 2.1917e-05 | 8.2639e-06 | 0.052109 | 0.052109 | 0.052109 | 0.98879 | -0.07856 | 0.98814 | -0.083129 | 19.2995
71 | -0.11035 | -0.027752 | 0.11058 | 0.02784 | 0.00023143 | 8.74e-05 | 0.16459 | 0.16459 | 0.16459 | 0.99784 | -0.015013 | 1 | 0 | 20.3195
72 | -0.015303 | -0.0038356 | 0.015306 | 0.0038367 | 3.1364e-06 | 1.0858e-06 | 0.023079 | 0.023079 | 0.023079 | 0.98669 | -0.093462 | 0.98689 | -0.091982 | 8.5476
73 | -0.016614 | -0.0041646 | 0.016622 | 0.0041672 | 7.3978e-06 | 2.6038e-06 | 0.025051 | 0.025051 | 0.025051 | 0.98689 | -0.091982 | 0.98735 | -0.088768 | 9.2782
74 | -0.023795 | -0.0059649 | 0.023804 | 0.0059685 | 9.5115e-06 | 3.5066e-06 | 0.035861 | 0.035861 | 0.035861 | 0.98735 | -0.088768 | 0.98775 | -0.085883 | 13.282
75 | -0.026118 | -0.0065482 | 0.026124 | 0.0065507 | 6.705e-06 | 2.49e-06 | 0.039346 | 0.039346 | 0.039346 | 0.98775 | -0.085883 | 0.98802 | -0.084031 | 14.5727
76 | -0.032353 | -0.0081118 | 0.032357 | 0.0081133 | 4.0436e-06 | 1.5203e-06 | 0.048727 | 0.048727 | 0.048727 | 0.98802 | -0.084031 | 0.98814 | -0.083129 | 18.0472
77 | 0.001892 | 0.00047415 | -0.001892 | -0.00047418 | 1.3715e-08 | -2.7561e-08 | 0.0028884 | 0.0028884 | 0.0028884 | 0.9747 | -0.17713 | 0.9747 | -0.17718 | 1.0698
78 | -0.004489 | -0.001125 | 0.0044894 | 0.001125 | 3.6083e-07 | -1.4695e-08 | 0.0068531 | 0.006853 | 0.0068531 | 0.9747 | -0.17713 | 0.97478 | -0.17655 | 2.5382
79 | 0.04402 | 0.011049 | -0.043947 | -0.011021 | 7.2921e-05 | 2.7725e-05 | 0.067203 | 0.067203 | 0.067203 | 0.97478 | -0.17655 | 0.97312 | -0.1885 | 24.8899
80 | -0.048509 | -0.012174 | 0.048561 | 0.012193 | 5.1591e-05 | 1.9655e-05 | 0.074056 | 0.074056 | 0.074056 | 0.97478 | -0.17655 | 0.97585 | -0.16889 | 27.428
81 | 0.015002 | 0.0037607 | -0.014999 | -0.0037596 | 3.1332e-06 | 1.0866e-06 | 0.022941 | 0.022941 | 0.022941 | 0.97312 | -0.1885 | 0.97291 | -0.19001 | 8.4965
82 | 0.028945 | 0.0072601 | -0.028925 | -0.0072526 | 2.0034e-05 | 7.5019e-06 | 0.044262 | 0.044262 | 0.044262 | 0.97312 | -0.1885 | 0.97242 | -0.1935 | 16.3934
83 | -0.050115 | -0.012583 | 0.050241 | 0.012631 | 0.00012605 | 4.8046e-05 | 0.076425 | 0.076425 | 0.076425 | 0.97585 | -0.16889 | 0.97838 | -0.15084 | 28.3057
84 | 0.013 | 0.0032585 | -0.012995 | -0.0032568 | 5.0535e-06 | 1.6894e-06 | 0.019882 | 0.019882 | 0.019882 | 0.97291 | -0.19001 | 0.97252 | -0.19282 | 7.3639
85 | 0.026341 | 0.006605 | -0.026322 | -0.006598 | 1.8895e-05 | 7.0364e-06 | 0.040308 | 0.040308 | 0.040308 | 0.97242 | -0.1935 | 0.9717 | -0.19868 | 14.929
86 | -0.05849 | -0.014698 | 0.058494 | 0.014699 | 3.6207e-06 | 1.3834e-06 | 0.088971 | 0.088971 | 0.088971 | 0.97838 | -0.15084 | 0.97845 | -0.15039 | 32.9523
87 | 0.0082492 | 0.002067 | -0.008248 | -0.0020667 | 1.2281e-06 | 3.1533e-07 | 0.012546 | 0.012546 | 0.012546 | 0.97838 | -0.15084 | 0.97823 | -0.15191 | 4.6467
88 | 0.011089 | 0.0027793 | -0.011085 | -0.0027781 | 3.8673e-06 | 1.2204e-06 | 0.016967 | 0.016967 | 0.016967 | 0.97252 | -0.19282 | 0.97217 | -0.19534 | 6.2842
89 | 0.012118 | 0.003038 | -0.012109 | -0.003035 | 9.3653e-06 | 3.0626e-06 | 0.018558 | 0.018558 | 0.018558 | 0.9717 | -0.19868 | 0.97093 | -0.20426 | 6.8733
90 | 0.014204 | 0.0035599 | -0.014198 | -0.0035581 | 5.2548e-06 | 1.8006e-06 | 0.021751 | 0.021751 | 0.021751 | 0.9717 | -0.19868 | 0.97133 | -0.20135 | 8.0558
91 | -0.062556 | -0.015717 | 0.062655 | 0.015755 | 9.9337e-05 | 3.7985e-05 | 0.095149 | 0.095149 | 0.095149 | 0.97845 | -0.15039 | 0.98005 | -0.139 | 35.2403
92 | 0.0039759 | 0.00099605 | -0.0039749 | -0.00099622 | 9.7637e-07 | -1.614e-07 | 0.0060477 | 0.0060479 | 0.0060479 | 0.97823 | -0.15191 | 0.97799 | -0.15369 | 2.24
93 | 0.0091619 | 0.0022956 | -0.0091597 | -0.002295 | 2.1447e-06 | 6.0931e-07 | 0.014041 | 0.014041 | 0.014041 | 0.97094 | -0.20416 | 0.97071 | -0.20585 | 5.2003
94 | -0.010688 | -0.0026781 | 0.010692 | 0.0026794 | 4.1573e-06 | 1.2917e-06 | 0.01638 | 0.016379 | 0.01638 | 0.97094 | -0.20416 | 0.97133 | -0.20135 | 6.0665
95 | 0.0063183 | 0.0015829 | -0.0063169 | -0.0015827 | 1.3926e-06 | 2.4157e-07 | 0.0096852 | 0.0096853 | 0.0096853 | 0.97071 | -0.20585 | 0.97049 | -0.20744 | 3.5872
96 | 0.0040284 | 0.0010091 | -0.0040278 | -0.0010092 | 6.486e-07 | -8.7144e-08 | 0.0061765 | 0.0061766 | 0.0061766 | 0.97049 | -0.20744 | 0.97033 | -0.20861 | 2.2876
97 | 0.0016382 | 0.00041032 | -0.0016381 | -0.00041055 | 8.3564e-08 | -2.2996e-07 | 0.0025121 | 0.0025122 | 0.0025122 | 0.97033 | -0.20861 | 0.97028 | -0.20898 | 0.93044
98 | 0.012109 | 0.003035 | -0.012107 | -0.0030342 | 2.2468e-06 | 7.3487e-07 | 0.018558 | 0.018558 | 0.018558 | 0.97093 | -0.20426 | 0.97074 | -0.2056 | 6.8733
99 | 0.010835 | 0.0027155 | -0.010831 | -0.0027143 | 3.6578e-06 | 1.1442e-06 | 0.016608 | 0.016608 | 0.016608 | 0.97074 | -0.2056 | 0.9704 | -0.20804 | 6.1512
100 | -0.066675 | -0.016763 | 0.066776 | 0.016801 | 0.00010083 | 3.8584e-05 | 0.10125 | 0.10125 | 0.10125 | 0.98005 | -0.139 | 0.98158 | -0.12816 | 37.5008
101 | -0.0033801 | -0.00084713 | 0.0033804 | 0.00084704 | 2.7679e-07 | -9.7332e-08 | 0.0051844 | 0.0051844 | 0.0051844 | 0.97014 | -0.20993 | 0.97022 | -0.20934 | 1.9202
102 | -0.0068536 | -0.0017175 | 0.0068549 | 0.0017178 | 1.2357e-06 | 2.5389e-07 | 0.010511 | 0.010511 | 0.010511 | 0.97022 | -0.20934 | 0.9704 | -0.20804 | 3.8931
103 | 0.0091378 | 0.00229 | -0.0091353 | -0.0022892 | 2.5622e-06 | 7.2528e-07 | 0.013986 | 0.013987 | 0.013987 | 0.97217 | -0.19534 | 0.97189 | -0.19736 | 5.1802
104 | 0.0071103 | 0.0017817 | -0.0071086 | -0.0017814 | 1.6916e-06 | 3.6721e-07 | 0.010886 | 0.010886 | 0.010886 | 0.97189 | -0.19736 | 0.97165 | -0.19908 | 4.0319
105 | 0.0051626 | 0.0012937 | -0.0051616 | -0.0012936 | 1.0242e-06 | 6.875e-08 | 0.0079061 | 0.0079062 | 0.0079062 | 0.97165 | -0.19908 | 0.97145 | -0.20051 | 2.9282
106 | 0.003929 | 0.00098468 | -0.003929 | -0.00098469 | 4.6037e-08 | -7.5124e-09 | 0.0060182 | 0.0060183 | 0.0060183 | 0.97145 | -0.20051 | 0.97144 | -0.2006 | 2.229
107 | 0.0038856 | 0.00097302 | -0.0038851 | -0.00097314 | 5.7146e-07 | -1.1382e-07 | 0.0058901 | 0.0058902 | 0.0058902 | 0.98158 | -0.12816 | 0.98143 | -0.12922 | 2.1816
108 | -0.074478 | -0.018731 | 0.07486 | 0.018877 | 0.00038223 | 0.0001464 | 0.11293 | 0.11293 | 0.11293 | 0.98158 | -0.12816 | 0.98678 | -0.091536 | 41.8247
109 | 0.079472 | 0.020168 | -0.078453 | -0.019778 | 0.0010193 | 0.00039053 | 0.11834 | 0.11834 | 0.11834 | 1 | 0 | 0.98678 | -0.091536 | 43.8314
110 | 0.0030828 | 0.00077207 | -0.0030827 | -0.00077214 | 1.2053e-07 | -6.537e-08 | 0.0046739 | 0.0046739 | 0.0046739 | 0.98143 | -0.12922 | 0.98139 | -0.12951 | 1.7311
111 | 0.0022952 | 0.00057478 | -0.002295 | -0.00057499 | 1.6443e-07 | -2.1168e-07 | 0.0034799 | 0.00348 | 0.00348 | 0.98139 | -0.12951 | 0.98132 | -0.13002 | 1.2889
112 | 0.0012917 | 0.00032354 | -0.0012917 | -0.00032373 | 3.9592e-08 | -1.9371e-07 | 0.0019586 | 0.0019587 | 0.0019587 | 0.98132 | -0.13002 | 0.98129 | -0.13025 | 0.72545

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.19085 | 0.048008

## res_load
| p_mw | q_mvar
0 | 0.00012788 | 3.205e-05
1 | 0.0034578 | 0.00086661
2 | 7.9078e-05 | 1.9819e-05
3 | 0.0027322 | 0.00068474
4 | 0.0010723 | 0.00026875
5 | 0.00030179 | 7.5637e-05
6 | 0.00022581 | 5.6594e-05
7 | 0.0024468 | 0.00061323
8 | 0.0020329 | 0.0005095
9 | 0.0026533 | 0.00066497
10 | 0.00013483 | 3.3792e-05
11 | 0.0033227 | 0.00083276
12 | 0.00065257 | 0.00016355
13 | 0.00065834 | 0.00016499
14 | 0.00013477 | 3.3777e-05
15 | 0.00035646 | 8.9338e-05
16 | 0.00032005 | 8.0211e-05
17 | 0.0023934 | 0.00059984
18 | 0.006089 | 0.001526
19 | 0.0037507 | 0.00094001
20 | 0.0014857 | 0.00037234
21 | 0.00078455 | 0.00019663
22 | 0.0012024 | 0.00030135
23 | 0.0010362 | 0.0002597
24 | 0.0010848 | 0.00027188
25 | 0.0012105 | 0.00030339
26 | 0.00075474 | 0.00018916
27 | 0.00078794 | 0.00019748
28 | 0.00045614 | 0.00011432
29 | 0.00075537 | 0.00018931
30 | 0.00076298 | 0.00019122
31 | 0.0024129 | 0.00060474
32 | 0.00077795 | 0.00019497
33 | 0.0020482 | 0.00051331
34 | 0.00033536 | 8.4049e-05
35 | 0.00022316 | 5.5929e-05
36 | 0.0012815 | 0.00032117
37 | 0.0014155 | 0.00035477
38 | 0.00073385 | 0.00018392
39 | 0.0031988 | 0.00080169
40 | 0.0010348 | 0.00025935
41 | 0.000188 | 4.7118e-05
42 | 0.00015515 | 3.8885e-05
43 | 0.00085732 | 0.00021486
44 | 0.0010003 | 0.0002507
45 | 0.00010682 | 2.6771e-05
46 | 0.0007087 | 0.00017762
47 | 0.007703 | 0.0019306
48 | 0.0015268 | 0.00038266
49 | 0.0051531 | 0.0012915
50 | 0.0030267 | 0.00075857
51 | 0.0015556 | 0.00038988
52 | 0.0009704 | 0.00024321
53 | 0.0010969 | 0.0002749
54 | 0.0010535 | 0.00026404
55 | 0.0012128 | 0.00030397
56 | 0.0024006 | 0.00060165
57 | 0.002698 | 0.00067618
58 | 0.0013083 | 0.00032788
59 | 0.0071731 | 0.0017977
60 | 0.0023133 | 0.00057977
61 | 0.0062289 | 0.0015611
62 | 0.0022454 | 0.00056275
63 | 0.002597 | 0.00065087
64 | 0.001892 | 0.00047418
65 | 0.0015541 | 0.00038948
66 | 0.0019995 | 0.00050113
67 | 0.002584 | 0.0006476
68 | 0.0019053 | 0.00047751
69 | 0.0040622 | 0.0010181
70 | 0.0042721 | 0.0010707
71 | 0.0015261 | 0.00038247
72 | 0.0028414 | 0.00071212
73 | 0.0035062 | 0.00087874
74 | 0.0022885 | 0.00057355
75 | 0.0023896 | 0.00059889
76 | 0.0016381 | 0.00041055
77 | 0.0012719 | 0.00031877
78 | 0.0039749 | 0.00099622
79 | 0.00402 | 0.0010075
80 | 0.0033801 | 0.00084713
81 | 0.0034733 | 0.00087048
82 | 0.0019475 | 0.0004881
83 | 0.002025 | 0.00050751
84 | 0.001946 | 0.00048771
85 | 0.0012326 | 0.00030891
86 | 0.0039762 | 0.00099654
87 | 0.0038158 | 0.00095633
88 | 0.003929 | 0.00098469
89 | 0.003593 | 0.0009005
90 | 0.00080227 | 0.00020107
91 | 0.00078747 | 0.00019736
92 | 0.0010033 | 0.00025145
93 | 0.0012917 | 0.00032373
94 | 0.0015785 | 0.0003956

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1