## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1094-11_1_2_node_24 | 0.4 | n |  | TRUE
1 | bus_LV_1094-11_1_2_node_27 | 0.4 | n |  | TRUE
2 | bus_LV_1094-11_1_2_node_22 | 0.4 | n |  | TRUE
3 | bus_LV_1094-11_1_2_node_31 | 0.4 | n |  | TRUE
4 | bus_LV_1094-11_1_2_node_30 | 0.4 | n |  | TRUE
5 | bus_LV_1094-11_1_2_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_1094-11_1_2_node_28 | 0.4 | n |  | TRUE
7 | bus_LV_1094-11_1_2_node_40 | 0.4 | n |  | TRUE
8 | bus_LV_1094-11_1_2_node_14 | 0.4 | n |  | TRUE
9 | bus_LV_1094-11_1_2_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_1094-11_1_2_node_39 | 0.4 | n |  | TRUE
11 | bus_LV_1094-11_1_2_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_1094-11_1_2_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_1094-11_1_2_node_42 | 0.4 | n |  | TRUE
14 | bus_LV_1094-11_1_2_node_38 | 0.4 | n |  | TRUE
15 | bus_LV_1094-11_1_2_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_1094-11_1_2_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_1094-11_1_2_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_1094-11_1_2_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_1094-11_1_2_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_1094-11_1_2_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_1094-11_1_2_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_1094-11_1_2_node_44 | 0.4 | n |  | TRUE
23 | bus_LV_1094-11_1_2_node_43 | 0.4 | n |  | TRUE
24 | bus_LV_1094-11_1_2_node_45 | 0.4 | n |  | TRUE
25 | bus_LV_1094-11_1_2_node_41 | 0.4 | n |  | TRUE
26 | bus_LV_1094-11_1_2_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_1094-11_1_2_node_35 | 0.4 | n |  | TRUE
28 | bus_LV_1094-11_1_2_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_1094-11_1_2_node_34 | 0.4 | n |  | TRUE
30 | bus_LV_1094-11_1_2_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_1094-11_1_2_node_37 | 0.4 | n |  | TRUE
32 | bus_MV_2_1_node_223 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1094-11_1_2_load_27 | 1 | 0.0022666 | 0.00056805 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1094-11_1_2_load_22 | 2 | 0.0031434 | 0.00078782 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1094-11_1_2_load_31 | 3 | 0.01006 | 0.0025212 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1094-11_1_2_load_30 | 4 | 0.0029755 | 0.00074574 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1094-11_1_2_load_40 | 7 | 0.0029384 | 0.00073642 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1094-11_1_2_load_39 | 10 | 0.0023559 | 0.00059044 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1094-11_1_2_load_19 | 11 | 0.0027714 | 0.00069459 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1094-11_1_2_load_16 | 12 | 0.004655 | 0.0011666 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1094-11_1_2_load_42 | 13 | 0.0028824 | 0.0007224 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1094-11_1_2_load_38 | 14 | 0.0022398 | 0.00056134 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1094-11_1_2_load_20 | 15 | 0.0049003 | 0.0012281 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1094-11_1_2_load_17 | 16 | 0.0049911 | 0.0012509 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1094-11_1_2_load_18 | 17 | 0.0060298 | 0.0015112 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1094-11_1_2_load_21 | 18 | 0.0066459 | 0.0016656 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1094-11_1_2_load_25 | 20 | 0.0014583 | 0.00036549 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1094-11_1_2_load_26 | 21 | 0.0034565 | 0.00086629 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1094-11_1_2_load_44 | 22 | 0.0014584 | 0.00036551 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1094-11_1_2_load_43 | 23 | 0.0031015 | 0.0007773 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1094-11_1_2_load_45 | 24 | 0.0024422 | 0.00061206 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1094-11_1_2_load_41 | 25 | 0.0023248 | 0.00058266 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1094-11_1_2_load_32 | 26 | 0.013059 | 0.0032728 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1094-11_1_2_load_35 | 27 | 0.0067259 | 0.0016857 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1094-11_1_2_load_33 | 28 | 0.0023109 | 0.00057916 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1094-11_1_2_load_34 | 29 | 0.0017766 | 0.00044525 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1094-11_1_2_load_36 | 30 | 0.0019498 | 0.00048867 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1094-11_1_2_load_37 | 31 | 0.0020508 | 0.00051398 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1094-11_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.010285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1094-11_1_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.020436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1094-11_1_2_line_2 | NAYY 4x150 SE | 2 | 19 | 0.015017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1094-11_1_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.0098907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1094-11_1_2_line_4 | NAYY 4x150 SE | 4 | 26 | 0.016565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1094-11_1_2_line_5 | NAYY 4x150 SE | 5 | 6 | 0.094823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1094-11_1_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.065921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1094-11_1_2_line_7 | NAYY 4x150 SE | 6 | 13 | 0.060531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1094-11_1_2_line_8 | NAYY 4x150 SE | 7 | 8 | 0.0024229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1094-11_1_2_line_9 | NAYY 4x150 SE | 8 | 9 | 0.031436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1094-11_1_2_line_10 | NAYY 4x150 SE | 8 | 10 | 0.011855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1094-11_1_2_line_11 | NAYY 4x150 SE | 9 | 11 | 0.017983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1094-11_1_2_line_12 | NAYY 4x150 SE | 9 | 12 | 0.048133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1094-11_1_2_line_13 | NAYY 4x150 SE | 10 | 14 | 0.019251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1094-11_1_2_line_14 | NAYY 4x150 SE | 11 | 15 | 0.025904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1094-11_1_2_line_15 | NAYY 4x150 SE | 12 | 16 | 0.027594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1094-11_1_2_line_16 | NAYY 4x150 SE | 13 | 25 | 0.021504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1094-11_1_2_line_17 | NAYY 4x150 SE | 14 | 31 | 0.0070939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1094-11_1_2_line_18 | NAYY 4x150 SE | 15 | 18 | 0.027268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1094-11_1_2_line_19 | NAYY 4x150 SE | 16 | 17 | 0.020762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1094-11_1_2_line_20 | NAYY 4x150 SE | 19 | 20 | 0.0098192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1094-11_1_2_line_21 | NAYY 4x150 SE | 19 | 21 | 0.010751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1094-11_1_2_line_22 | NAYY 4x150 SE | 20 | 22 | 0.007968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1094-11_1_2_line_23 | NAYY 4x150 SE | 21 | 23 | 0.024188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1094-11_1_2_line_24 | NAYY 4x150 SE | 22 | 24 | 0.019814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1094-11_1_2_line_25 | NAYY 4x150 SE | 23 | 25 | 0.00074479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1094-11_1_2_line_26 | NAYY 4x150 SE | 26 | 27 | 0.037479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1094-11_1_2_line_27 | NAYY 4x150 SE | 27 | 28 | 0.0098837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1094-11_1_2_line_28 | NAYY 4x150 SE | 28 | 29 | 0.017265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1094-11_1_2_line_29 | NAYY 4x150 SE | 29 | 30 | 0.0072891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1094-11_1_2_line_30 | NAYY 4x150 SE | 30 | 31 | 0.018072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1094-11_1_2_trafo_33 | 0.25 MVA 20/0.4 kV | 32 | 28 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2652436.7894 | 1220836.7913 | 2652445.6117 | 1220831.5051
1 | 2652436.7894 | 1220836.7913 | 2652444.2514 | 1220843.1831 | 2652446.3716 | 1220845.3698 | 2652451.7665 | 1220850.6731
2 | 2652462.789 | 1220860.8683 | 2652454.9536 | 1220853.8061 | 2652451.7665 | 1220850.6731
3 | 2652472.2076 | 1220948.339 | 2652478.4687 | 1220955.9957
4 | 2652461.7218 | 1220935.5157 | 2652472.2076 | 1220948.339
5 | 2652536.0385 | 1220771.3031 | 2652586.8882 | 1220764.8698 | 2652587.9727 | 1220772.6508 | 2652589.7357 | 1220779.1926 | 2652592.6772 | 1220785.4557 | 2652606.2712 | 1220802.7752
6 | 2652606.2712 | 1220802.7752 | 2652563.3571 | 1220835.8947 | 2652554.9745 | 1220844.0749
7 | 2652536.0385 | 1220771.3031 | 2652536.1763 | 1220776.3185 | 2652535.4725 | 1220780.4259 | 2652533.675 | 1220783.801 | 2652501.5037 | 1220818.7776
8 | 2652553.2405 | 1220845.767 | 2652554.9745 | 1220844.0749
9 | 2652553.2405 | 1220845.767 | 2652565.3888 | 1220861.8507 | 2652572.1904 | 1220870.8496
10 | 2652553.2405 | 1220845.767 | 2652544.7252 | 1220854.0149
11 | 2652572.1904 | 1220870.8496 | 2652558.2095 | 1220882.1591
12 | 2652572.1904 | 1220870.8496 | 2652591.2004 | 1220896.8443 | 2652578.4576 | 1220906.4012
13 | 2652530.8973 | 1220867.4082 | 2652544.7252 | 1220854.0149
14 | 2652538.0695 | 1220898.4508 | 2652558.2095 | 1220882.1591
15 | 2652578.4576 | 1220906.4012 | 2652556.382 | 1220922.9576
16 | 2652486.9459 | 1220834.6049 | 2652501.5037 | 1220818.7776
17 | 2652525.8018 | 1220872.3437 | 2652530.8973 | 1220867.4082
18 | 2652516.8691 | 1220915.6004 | 2652538.0695 | 1220898.4508
19 | 2652539.7725 | 1220935.4144 | 2652556.382 | 1220922.9576
20 | 2652462.789 | 1220860.8683 | 2652455.8377 | 1220867.8034
21 | 2652462.789 | 1220860.8683 | 2652470.0672 | 1220852.9554
22 | 2652455.8377 | 1220867.8034 | 2652450.1969 | 1220873.4311
23 | 2652486.4417 | 1220835.1531 | 2652470.0672 | 1220852.9554
24 | 2652435.8249 | 1220887.0481 | 2652440.4093 | 1220883.1961 | 2652450.1969 | 1220873.4311
25 | 2652486.9459 | 1220834.6049 | 2652486.4417 | 1220835.1531
26 | 2652488.0844 | 1220908.876 | 2652461.7218 | 1220935.5157
27 | 2652488.0844 | 1220908.876 | 2652495.1839 | 1220901.9996
28 | 2652495.1839 | 1220901.9996 | 2652507.5851 | 1220889.988
29 | 2652507.5851 | 1220889.988 | 2652512.8209 | 1220884.9167
30 | 2652512.8209 | 1220884.9167 | 2652525.8018 | 1220872.3437

## bus_geodata
| x | y | coords
0 | 2652436.7894 | 1220836.7913
1 | 2652445.6117 | 1220831.5051
2 | 2652451.7665 | 1220850.6731
3 | 2652478.4687 | 1220955.9957
4 | 2652472.2076 | 1220948.339
5 | 2652606.2712 | 1220802.7752
6 | 2652536.0385 | 1220771.3031
7 | 2652554.9745 | 1220844.0749
8 | 2652553.2405 | 1220845.7671
9 | 2652572.1904 | 1220870.8496
10 | 2652544.7252 | 1220854.0149
11 | 2652558.2095 | 1220882.1591
12 | 2652578.4576 | 1220906.4012
13 | 2652501.5037 | 1220818.7776
14 | 2652530.8973 | 1220867.4082
15 | 2652538.0695 | 1220898.4508
16 | 2652556.382 | 1220922.9576
17 | 2652539.7725 | 1220935.4144
18 | 2652516.8691 | 1220915.6004
19 | 2652462.789 | 1220860.8683
20 | 2652455.8377 | 1220867.8034
21 | 2652470.0672 | 1220852.9554
22 | 2652450.1969 | 1220873.4311
23 | 2652486.4417 | 1220835.1531
24 | 2652435.8249 | 1220887.0481
25 | 2652486.9459 | 1220834.6049
26 | 2652461.7218 | 1220935.5157
27 | 2652488.0844 | 1220908.876
28 | 2652495.1839 | 1220901.9996
29 | 2652507.5851 | 1220889.988
30 | 2652512.8209 | 1220884.9167
31 | 2652525.8018 | 1220872.3437
32 | 2652488.0844 | 1220908.876

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98411 | -0.1116 | 0 | 0
1 | 0.98408 | -0.11184 | 0.0022666 | 0.00056805
2 | 0.98418 | -0.11112 | 0.0031434 | 0.00078782
3 | 0.99769 | -0.016186 | 0.01006 | 0.0025212
4 | 0.99783 | -0.015188 | 0.0029755 | 0.00074574
5 | 0.99066 | -0.06525 | 0 | 0
6 | 0.98757 | -0.08707 | 0 | 0
7 | 0.99281 | -0.050155 | 0.0029384 | 0.00073642
8 | 0.9929 | -0.04953 | 0 | 0
9 | 0.99155 | -0.059093 | 0 | 0
10 | 0.99385 | -0.042873 | 0.0023559 | 0.00059044
11 | 0.99118 | -0.061709 | 0.0027714 | 0.00069459
12 | 0.99046 | -0.066765 | 0.004655 | 0.0011666
13 | 0.9856 | -0.10107 | 0.0028824 | 0.0007224
14 | 0.99546 | -0.031633 | 0.0022398 | 0.00056134
15 | 0.99075 | -0.06475 | 0.0049003 | 0.0012281
16 | 0.99002 | -0.069861 | 0.0049911 | 0.0012509
17 | 0.98984 | -0.071136 | 0.0060298 | 0.0015112
18 | 0.99048 | -0.066593 | 0.0066459 | 0.0016656
19 | 0.9843 | -0.11028 | 0 | 0
20 | 0.98422 | -0.11083 | 0.0014583 | 0.00036549
21 | 0.98447 | -0.10909 | 0.0034565 | 0.00086629
22 | 0.98418 | -0.11115 | 0.0014584 | 0.00036551
23 | 0.98497 | -0.10555 | 0.0031015 | 0.0007773
24 | 0.98411 | -0.11164 | 0.0024422 | 0.00061206
25 | 0.98498 | -0.10541 | 0.0023248 | 0.00058266
26 | 0.99814 | -0.013024 | 0.013059 | 0.0032728
27 | 0.99954 | -0.0032396 | 0.0067259 | 0.0016857
28 | 1 | 0 | -0.1002 | -0.025001
29 | 0.99836 | -0.011374 | 0.0017766 | 0.00044525
30 | 0.99769 | -0.016057 | 0.0019498 | 0.00048867
31 | 0.99607 | -0.02734 | 0.0020508 | 0.00051398
32 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0022666 | 0.00056795 | -0.0022666 | -0.00056805 | 7.5381e-08 | -1.0168e-07 | 0.0034272 | 0.0034272 | 0.0034272 | 0.98411 | -0.1116 | 0.98408 | -0.11184 | 1.2693
1 | -0.0022666 | -0.00056795 | 0.0022668 | 0.00056775 | 1.4978e-07 | -2.0207e-07 | 0.0034272 | 0.0034271 | 0.0034272 | 0.98411 | -0.1116 | 0.98418 | -0.11112 | 1.2693
2 | -0.0054102 | -0.0013556 | 0.0054109 | 0.0013556 | 6.2699e-07 | 5.0292e-08 | 0.0081798 | 0.0081797 | 0.0081798 | 0.98418 | -0.11112 | 0.9843 | -0.11028 | 3.0295
3 | -0.01006 | -0.0025212 | 0.010061 | 0.0025216 | 1.3893e-06 | 4.0516e-07 | 0.015003 | 0.015003 | 0.015003 | 0.99769 | -0.016186 | 0.99783 | -0.015188 | 5.5568
4 | -0.013036 | -0.0032673 | 0.01304 | 0.0032686 | 3.9065e-06 | 1.2861e-06 | 0.019441 | 0.019441 | 0.019441 | 0.99783 | -0.015188 | 0.99814 | -0.013024 | 7.2002
5 | 0.022669 | 0.0056957 | -0.0226 | -0.0056705 | 6.8622e-05 | 2.5176e-05 | 0.034055 | 0.034055 | 0.034055 | 0.99066 | -0.06525 | 0.98757 | -0.08707 | 12.6131
6 | -0.022669 | -0.0056957 | 0.022717 | 0.0057132 | 4.7705e-05 | 1.7497e-05 | 0.034055 | 0.034055 | 0.034055 | 0.99066 | -0.06525 | 0.99281 | -0.050155 | 12.6129
7 | 0.0226 | 0.0056705 | -0.022557 | -0.0056544 | 4.3806e-05 | 1.6075e-05 | 0.034055 | 0.034056 | 0.034056 | 0.98757 | -0.08707 | 0.9856 | -0.10107 | 12.6132
8 | -0.025655 | -0.0064496 | 0.025657 | 0.0064505 | 2.2361e-06 | 8.2872e-07 | 0.038459 | 0.038459 | 0.038459 | 0.99281 | -0.050155 | 0.9929 | -0.04953 | 14.2439
9 | 0.030068 | 0.007543 | -0.030028 | -0.0075281 | 3.9835e-05 | 1.4915e-05 | 0.045063 | 0.045063 | 0.045063 | 0.9929 | -0.04953 | 0.99155 | -0.059093 | 16.6902
10 | -0.055725 | -0.013993 | 0.055776 | 0.014013 | 5.1604e-05 | 1.9694e-05 | 0.083522 | 0.083522 | 0.083522 | 0.9929 | -0.04953 | 0.99385 | -0.042873 | 30.934
11 | 0.014329 | 0.0035919 | -0.014324 | -0.0035902 | 5.1891e-06 | 1.7639e-06 | 0.021504 | 0.021504 | 0.021504 | 0.99155 | -0.059093 | 0.99118 | -0.061709 | 7.9646
12 | 0.015698 | 0.0039361 | -0.015682 | -0.0039303 | 1.667e-05 | 5.7916e-06 | 0.023559 | 0.023559 | 0.023559 | 0.99155 | -0.059093 | 0.99046 | -0.066765 | 8.7257
13 | -0.058132 | -0.014604 | 0.058223 | 0.014638 | 9.1025e-05 | 3.476e-05 | 0.087049 | 0.087049 | 0.087049 | 0.99385 | -0.042873 | 0.99546 | -0.031633 | 32.2404
14 | 0.011553 | 0.0028956 | -0.011548 | -0.002894 | 4.8624e-06 | 1.5364e-06 | 0.017344 | 0.017344 | 0.017344 | 0.99118 | -0.061709 | 0.99075 | -0.06475 | 6.4237
15 | 0.011027 | 0.0027637 | -0.011022 | -0.0027622 | 4.7254e-06 | 1.4625e-06 | 0.016566 | 0.016566 | 0.016566 | 0.99046 | -0.066765 | 0.99002 | -0.069861 | 6.1356
16 | 0.019674 | 0.0049321 | -0.019662 | -0.0049278 | 1.184e-05 | 4.2798e-06 | 0.029704 | 0.029704 | 0.029704 | 0.9856 | -0.10107 | 0.98498 | -0.10541 | 11.0015
17 | -0.060463 | -0.0152 | 0.060499 | 0.015213 | 3.6172e-05 | 1.382e-05 | 0.090397 | 0.090397 | 0.090397 | 0.99546 | -0.031633 | 0.99607 | -0.02734 | 33.4804
18 | 0.0066476 | 0.0016659 | -0.0066459 | -0.0016656 | 1.6962e-06 | 3.0131e-07 | 0.0099841 | 0.0099842 | 0.0099842 | 0.99075 | -0.06475 | 0.99048 | -0.066593 | 3.6979
19 | 0.0060309 | 0.0015114 | -0.0060298 | -0.0015112 | 1.0645e-06 | 1.4249e-07 | 0.0090644 | 0.0090645 | 0.0090645 | 0.99002 | -0.069861 | 0.98984 | -0.071136 | 3.3572
20 | 0.0053596 | 0.0013429 | -0.0053592 | -0.0013428 | 4.0223e-07 | 2.9906e-08 | 0.0081023 | 0.0081023 | 0.0081023 | 0.9843 | -0.11028 | 0.98422 | -0.11083 | 3.0009
21 | -0.01077 | -0.0026985 | 0.010772 | 0.002699 | 1.7785e-06 | 5.4735e-07 | 0.016282 | 0.016282 | 0.016282 | 0.9843 | -0.11028 | 0.98447 | -0.10909 | 6.0304
22 | 0.0039009 | 0.00097735 | -0.0039007 | -0.00097738 | 1.7293e-07 | -3.4745e-08 | 0.0058975 | 0.0058975 | 0.0058975 | 0.98422 | -0.11083 | 0.98418 | -0.11115 | 2.1843
23 | -0.014229 | -0.0035653 | 0.014236 | 0.0035677 | 6.9809e-06 | 2.3773e-06 | 0.021506 | 0.021506 | 0.021506 | 0.98447 | -0.10909 | 0.98497 | -0.10555 | 7.9653
24 | 0.0024423 | 0.00061187 | -0.0024422 | -0.00061206 | 1.6858e-07 | -1.8692e-07 | 0.0036926 | 0.0036927 | 0.0036927 | 0.98418 | -0.11115 | 0.98411 | -0.11164 | 1.3676
25 | -0.017337 | -0.004345 | 0.017338 | 0.0043451 | 3.1882e-07 | 1.1314e-07 | 0.026192 | 0.026192 | 0.026192 | 0.98497 | -0.10555 | 0.98498 | -0.10541 | 9.7007
26 | -0.026099 | -0.0065414 | 0.026134 | 0.0065545 | 3.5404e-05 | 1.3126e-05 | 0.038908 | 0.038908 | 0.038908 | 0.99814 | -0.013024 | 0.99954 | -0.0032396 | 14.4104
27 | -0.03286 | -0.0082402 | 0.032875 | 0.0082457 | 1.476e-05 | 5.5474e-06 | 0.048921 | 0.048921 | 0.048921 | 0.99954 | -0.0032396 | 1 | 0 | 18.1188
28 | 0.066523 | 0.016756 | -0.066417 | -0.016715 | 0.00010562 | 4.0398e-05 | 0.099016 | 0.099016 | 0.099016 | 1 | 0 | 0.99836 | -0.011374 | 36.6728
29 | 0.064641 | 0.01627 | -0.064598 | -0.016254 | 4.224e-05 | 1.6151e-05 | 0.096369 | 0.096369 | 0.096369 | 0.99836 | -0.011374 | 0.99769 | -0.016057 | 35.6921
30 | 0.062649 | 0.015765 | -0.06255 | -0.015727 | 9.8501e-05 | 3.7649e-05 | 0.093461 | 0.093461 | 0.093461 | 0.99769 | -0.016057 | 0.99607 | -0.02734 | 34.615

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.10251 | 0.025581

## res_load
| p_mw | q_mvar
0 | 0.0022666 | 0.00056805
1 | 0.0031434 | 0.00078782
2 | 0.01006 | 0.0025212
3 | 0.0029755 | 0.00074574
4 | 0.0029384 | 0.00073642
5 | 0.0023559 | 0.00059044
6 | 0.0027714 | 0.00069459
7 | 0.004655 | 0.0011666
8 | 0.0028824 | 0.0007224
9 | 0.0022398 | 0.00056134
10 | 0.0049003 | 0.0012281
11 | 0.0049911 | 0.0012509
12 | 0.0060298 | 0.0015112
13 | 0.0066459 | 0.0016656
14 | 0.0014583 | 0.00036549
15 | 0.0034565 | 0.00086629
16 | 0.0014584 | 0.00036551
17 | 0.0031015 | 0.0007773
18 | 0.0024422 | 0.00061206
19 | 0.0023248 | 0.00058266
20 | 0.013059 | 0.0032728
21 | 0.0067259 | 0.0016857
22 | 0.0023109 | 0.00057916
23 | 0.0017766 | 0.00044525
24 | 0.0019498 | 0.00048867
25 | 0.0020508 | 0.00051398

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1