## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1094-3_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1094-3_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1094-3_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1094-3_0_2_node_11 | 0.4 | n |  | TRUE
4 | bus_LV_1094-3_0_2_node_18 | 0.4 | n |  | TRUE
5 | bus_LV_1094-3_0_2_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1094-3_0_2_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1094-3_0_2_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1094-3_0_2_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1094-3_0_2_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1094-3_0_2_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1094-3_0_2_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1094-3_0_2_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1094-3_0_2_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_1094-3_0_2_node_48 | 0.4 | n |  | TRUE
15 | bus_LV_1094-3_0_2_node_50 | 0.4 | n |  | TRUE
16 | bus_LV_1094-3_0_2_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1094-3_0_2_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1094-3_0_2_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1094-3_0_2_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1094-3_0_2_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1094-3_0_2_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1094-3_0_2_node_53 | 0.4 | n |  | TRUE
23 | bus_LV_1094-3_0_2_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1094-3_0_2_node_55 | 0.4 | n |  | TRUE
25 | bus_LV_1094-3_0_2_node_51 | 0.4 | n |  | TRUE
26 | bus_LV_1094-3_0_2_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_1094-3_0_2_node_49 | 0.4 | n |  | TRUE
28 | bus_LV_1094-3_0_2_node_109 | 0.4 | n |  | TRUE
29 | bus_LV_1094-3_0_2_node_67 | 0.4 | n |  | TRUE
30 | bus_LV_1094-3_0_2_node_52 | 0.4 | n |  | TRUE
31 | bus_LV_1094-3_0_2_node_54 | 0.4 | n |  | TRUE
32 | bus_LV_1094-3_0_2_node_56 | 0.4 | n |  | TRUE
33 | bus_LV_1094-3_0_2_node_57 | 0.4 | n |  | TRUE
34 | bus_LV_1094-3_0_2_node_58 | 0.4 | n |  | TRUE
35 | bus_LV_1094-3_0_2_node_59 | 0.4 | n |  | TRUE
36 | bus_LV_1094-3_0_2_node_68 | 0.4 | n |  | TRUE
37 | bus_LV_1094-3_0_2_node_75 | 0.4 | n |  | TRUE
38 | bus_LV_1094-3_0_2_node_69 | 0.4 | n |  | TRUE
39 | bus_LV_1094-3_0_2_node_70 | 0.4 | n |  | TRUE
40 | bus_LV_1094-3_0_2_node_71 | 0.4 | n |  | TRUE
41 | bus_LV_1094-3_0_2_node_72 | 0.4 | n |  | TRUE
42 | bus_LV_1094-3_0_2_node_73 | 0.4 | n |  | TRUE
43 | bus_LV_1094-3_0_2_node_74 | 0.4 | n |  | TRUE
44 | bus_MV_2_1_node_239 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1094-3_0_2_load_0 | 0 | 0.00035959 | 9.0123e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1094-3_0_2_load_1 | 1 | 0.002164 | 0.00054236 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1094-3_0_2_load_3 | 5 | 0.0022959 | 0.0005754 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1094-3_0_2_load_4 | 6 | 0.0022912 | 0.00057424 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1094-3_0_2_load_5 | 7 | 0.0026358 | 0.00066059 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1094-3_0_2_load_6 | 9 | 0.0035246 | 0.00088336 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1094-3_0_2_load_9 | 11 | 0.0046342 | 0.0011614 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1094-3_0_2_load_10 | 12 | 0.0082953 | 0.002079 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1094-3_0_2_load_21 | 13 | 0.0027047 | 0.00067786 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1094-3_0_2_load_48 | 14 | 0.0068862 | 0.0017258 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1094-3_0_2_load_50 | 15 | 0.0081961 | 0.0020541 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1094-3_0_2_load_12 | 16 | 0.00035252 | 8.8351e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1094-3_0_2_load_13 | 17 | 0.00042147 | 0.00010563 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1094-3_0_2_load_15 | 19 | 0.00039199 | 9.8241e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1094-3_0_2_load_16 | 20 | 0.00379 | 0.00094987 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1094-3_0_2_load_17 | 21 | 0.00013358 | 3.3478e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1094-3_0_2_load_55 | 24 | 0.0018637 | 0.00046708 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1094-3_0_2_load_51 | 25 | 0.0025726 | 0.00064476 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1094-3_0_2_load_20 | 26 | 0.0027797 | 0.00069667 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1094-3_0_2_load_49 | 27 | 0.0050779 | 0.0012726 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1094-3_0_2_load_52 | 30 | 0.0037772 | 0.00094666 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1094-3_0_2_load_54 | 31 | 0.0019993 | 0.00050108 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1094-3_0_2_load_56 | 32 | 0.0028387 | 0.00071145 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1094-3_0_2_load_57 | 33 | 0.0018364 | 0.00046025 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1094-3_0_2_load_58 | 34 | 0.0026961 | 0.0006757 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1094-3_0_2_load_59 | 35 | 0.0018362 | 0.00046019 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1094-3_0_2_load_68 | 36 | 0.0096047 | 0.0024072 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1094-3_0_2_load_75 | 37 | 0.023365 | 0.0058558 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1094-3_0_2_load_69 | 38 | 0.010129 | 0.0025386 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1094-3_0_2_load_70 | 39 | 0.0013287 | 0.000333 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1094-3_0_2_load_72 | 41 | 0.0011993 | 0.00030058 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1094-3_0_2_load_73 | 42 | 0.0016684 | 0.00041813 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1094-3_0_2_load_74 | 43 | 0.023121 | 0.0057946 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1094-3_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.031156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1094-3_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.037143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1094-3_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.03493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1094-3_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.017813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1094-3_0_2_line_4 | NAYY 4x150 SE | 3 | 15 | 0.023862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1094-3_0_2_line_5 | NAYY 4x150 SE | 3 | 8 | 0.024394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1094-3_0_2_line_6 | NAYY 4x150 SE | 4 | 23 | 0.030933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1094-3_0_2_line_7 | NAYY 4x150 SE | 4 | 20 | 0.04834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1094-3_0_2_line_8 | NAYY 4x150 SE | 5 | 6 | 0.018704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1094-3_0_2_line_9 | NAYY 4x150 SE | 6 | 7 | 0.001743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1094-3_0_2_line_10 | NAYY 4x150 SE | 7 | 8 | 0.01553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1094-3_0_2_line_11 | NAYY 4x150 SE | 8 | 9 | 0.037975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1094-3_0_2_line_12 | NAYY 4x150 SE | 9 | 10 | 0.012517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1094-3_0_2_line_13 | NAYY 4x150 SE | 10 | 11 | 0.013693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1094-3_0_2_line_14 | NAYY 4x150 SE | 10 | 12 | 0.059404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1094-3_0_2_line_15 | NAYY 4x150 SE | 11 | 13 | 0.026433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1094-3_0_2_line_16 | NAYY 4x150 SE | 12 | 14 | 0.064837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1094-3_0_2_line_17 | NAYY 4x150 SE | 13 | 26 | 0.00013731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1094-3_0_2_line_18 | NAYY 4x150 SE | 14 | 27 | 0.03142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1094-3_0_2_line_19 | NAYY 4x150 SE | 14 | 28 | 0.023518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1094-3_0_2_line_20 | NAYY 4x150 SE | 16 | 17 | 0.025591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1094-3_0_2_line_21 | NAYY 4x150 SE | 16 | 18 | 0.014223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1094-3_0_2_line_22 | NAYY 4x150 SE | 17 | 19 | 0.025769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1094-3_0_2_line_23 | NAYY 4x150 SE | 18 | 20 | 0.015841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1094-3_0_2_line_24 | NAYY 4x150 SE | 18 | 21 | 0.029967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1094-3_0_2_line_25 | NAYY 4x150 SE | 21 | 22 | 0.013787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1094-3_0_2_line_26 | NAYY 4x150 SE | 22 | 30 | 0.018552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1094-3_0_2_line_27 | NAYY 4x150 SE | 23 | 24 | 0.0054593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1094-3_0_2_line_28 | NAYY 4x150 SE | 23 | 25 | 0.017499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1094-3_0_2_line_29 | NAYY 4x150 SE | 24 | 32 | 0.01551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1094-3_0_2_line_30 | NAYY 4x150 SE | 27 | 29 | 0.034301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1094-3_0_2_line_31 | NAYY 4x150 SE | 28 | 41 | 0.019184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1094-3_0_2_line_32 | NAYY 4x150 SE | 29 | 36 | 0.0051475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1094-3_0_2_line_33 | NAYY 4x150 SE | 29 | 37 | 0.032529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1094-3_0_2_line_34 | NAYY 4x150 SE | 30 | 31 | 0.0052868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1094-3_0_2_line_35 | NAYY 4x150 SE | 32 | 33 | 0.0075233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1094-3_0_2_line_36 | NAYY 4x150 SE | 33 | 34 | 0.011521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1094-3_0_2_line_37 | NAYY 4x150 SE | 34 | 35 | 0.0069358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1094-3_0_2_line_38 | NAYY 4x150 SE | 36 | 38 | 0.032918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1094-3_0_2_line_39 | NAYY 4x150 SE | 37 | 43 | 0.030942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1094-3_0_2_line_40 | NAYY 4x150 SE | 39 | 40 | 0.012072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1094-3_0_2_line_41 | NAYY 4x150 SE | 40 | 41 | 0.038985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1094-3_0_2_line_42 | NAYY 4x150 SE | 40 | 42 | 0.0016323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1094-3_0_2_trafo_49 | 0.25 MVA 20/0.4 kV | 44 | 27 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2653104.9963 | 1220103.38 | 2653097.5873 | 1220133.6418
1 | 2653086.6561 | 1220168.8797 | 2653090.6715 | 1220161.889 | 2653097.5873 | 1220133.6418
2 | 2653082.3815 | 1220203.2627 | 2653087.1517 | 1220182.2368 | 2653086.6561 | 1220168.8797
3 | 2653080.1646 | 1220152.3229 | 2653082.7809 | 1220157.5939 | 2653086.6561 | 1220168.8797
4 | 2653082.3815 | 1220203.2627 | 2653059.073 | 1220198.1518
5 | 2653076.9873 | 1220227.0515 | 2653082.3815 | 1220203.2627
6 | 2653080.1646 | 1220152.3229 | 2653071.5094 | 1220158.0493 | 2653066.2286 | 1220158.8917 | 2653057.8933 | 1220163.6204 | 2653052.3577 | 1220164.9608
7 | 2653080.1646 | 1220152.3229 | 2653079.1435 | 1220150.257 | 2653049.5354 | 1220115.0066
8 | 2653041.8066 | 1220219.5237 | 2653051.8914 | 1220221.5691 | 2653060.1118 | 1220223.3649
9 | 2653060.1118 | 1220223.3649 | 2653061.8146 | 1220223.7369
10 | 2653076.9873 | 1220227.0515 | 2653061.8146 | 1220223.7369
11 | 2653076.9873 | 1220227.0515 | 2653068.5884 | 1220264.086
12 | 2653065.82 | 1220276.2933 | 2653068.5884 | 1220264.086
13 | 2653065.82 | 1220276.2933 | 2653063.041 | 1220275.6682 | 2653060.6407 | 1220286.2436
14 | 2653065.82 | 1220276.2933 | 2653069.4773 | 1220277.1153 | 2653068.4192 | 1220281.7643 | 2653067.8218 | 1220284.9498 | 2653067.7231 | 1220290.0631 | 2653068.5476 | 1220295.4627 | 2653069.8845 | 1220298.6877 | 2653072.4621 | 1220303.18 | 2653076.3092 | 1220307.4058 | 2653083.4062 | 1220313.8952 | 2653092.8761 | 1220322.9014
15 | 2653060.6407 | 1220286.2436 | 2653060.1348 | 1220288.4724 | 2653054.8057 | 1220312.0246
16 | 2653092.8761 | 1220322.9014 | 2653109.144 | 1220338.3728 | 2653118.2663 | 1220326.1911 | 2653130.8815 | 1220308.6039 | 2653134.1942 | 1220304.1826
17 | 2653054.8057 | 1220312.0246 | 2653054.7753 | 1220312.1585
18 | 2653134.1942 | 1220304.1826 | 2653153.034 | 1220279.0379
19 | 2653134.1942 | 1220304.1826 | 2653122.4539 | 1220324.5607
20 | 2653069.5223 | 1220080.3639 | 2653048.2558 | 1220094.5987
21 | 2653038.0722 | 1220104.2632 | 2653040.4629 | 1220100.7823 | 2653043.1508 | 1220098.0157 | 2653048.2558 | 1220094.5987
22 | 2653069.5223 | 1220080.3639 | 2653090.9369 | 1220066.03
23 | 2653038.0722 | 1220104.2632 | 2653041.3249 | 1220106.2378 | 2653045.1403 | 1220109.7739 | 2653049.5354 | 1220115.0066
24 | 2653038.0722 | 1220104.2632 | 2653032.9656 | 1220101.7273 | 2653027.3711 | 1220100.2989 | 2653022.0784 | 1220099.9182 | 2653016.574 | 1220100.3028 | 2653009.1002 | 1220102.0152
25 | 2652995.9963 | 1220106.3013 | 2653009.1002 | 1220102.0152
26 | 2652995.9963 | 1220106.3013 | 2653005.7345 | 1220122.0917
27 | 2653052.3577 | 1220164.9608 | 2653046.9984 | 1220163.9206
28 | 2653052.3577 | 1220164.9608 | 2653050.6409 | 1220168.5922 | 2653040.3056 | 1220177.25
29 | 2653034.2396 | 1220156.1316 | 2653038.3505 | 1220160.7781 | 2653042.6322 | 1220163.0731 | 2653046.9984 | 1220163.9206
30 | 2653173.1011 | 1220251.223 | 2653159.769 | 1220270.0489 | 2653153.034 | 1220279.0379
31 | 2653122.4539 | 1220324.5607 | 2653128.0289 | 1220328.146 | 2653132.722 | 1220330.2335 | 2653140.038 | 1220331.7219
32 | 2653173.1011 | 1220251.223 | 2653173.185 | 1220246.0761
33 | 2653173.1011 | 1220251.223 | 2653190.9298 | 1220278.431
34 | 2653008.5097 | 1220126.5916 | 2653005.7345 | 1220122.0917
35 | 2653034.2396 | 1220156.1316 | 2653029.2544 | 1220150.497
36 | 2653021.62 | 1220141.8681 | 2653029.2544 | 1220150.497
37 | 2653017.0242 | 1220136.6735 | 2653021.62 | 1220141.8681
38 | 2653173.185 | 1220246.0761 | 2653173.185 | 1220246.0761 | 2653178.3466 | 1220239.0401 | 2653178.8173 | 1220236.4538 | 2653177.3413 | 1220235.2066 | 2653187.536 | 1220221.9227 | 2653189.1821 | 1220219.5526
39 | 2653212.6986 | 1220256.4462 | 2653210.5684 | 1220258.7731 | 2653190.9298 | 1220278.431
40 | 2653179.0937 | 1220330.425 | 2653175.1527 | 1220341.8359
41 | 2653179.0937 | 1220330.425 | 2653147.9719 | 1220331.9928 | 2653140.038 | 1220331.7219
42 | 2653179.0937 | 1220330.425 | 2653180.6948 | 1220330.1077

## bus_geodata
| x | y | coords
0 | 2653104.9963 | 1220103.38
1 | 2653097.5873 | 1220133.6418
2 | 2653086.6561 | 1220168.8797
3 | 2653082.3815 | 1220203.2627
4 | 2653080.1646 | 1220152.3229
5 | 2653041.8066 | 1220219.5237
6 | 2653060.1118 | 1220223.3649
7 | 2653061.8146 | 1220223.7369
8 | 2653076.9873 | 1220227.0515
9 | 2653068.5884 | 1220264.086
10 | 2653065.82 | 1220276.2933
11 | 2653060.6407 | 1220286.2436
12 | 2653092.8761 | 1220322.9014
13 | 2653054.8057 | 1220312.0246
14 | 2653134.1942 | 1220304.1826
15 | 2653059.073 | 1220198.1518
16 | 2653048.2558 | 1220094.5987
17 | 2653069.5223 | 1220080.3639
18 | 2653038.0722 | 1220104.2632
19 | 2653090.9369 | 1220066.03
20 | 2653049.5354 | 1220115.0066
21 | 2653009.1002 | 1220102.0152
22 | 2652995.9963 | 1220106.3013
23 | 2653052.3577 | 1220164.9608
24 | 2653046.9984 | 1220163.9206
25 | 2653040.3056 | 1220177.25
26 | 2653054.7753 | 1220312.1585
27 | 2653153.034 | 1220279.0379
28 | 2653122.4539 | 1220324.5607
29 | 2653173.1011 | 1220251.223
30 | 2653005.7345 | 1220122.0917
31 | 2653008.5097 | 1220126.5916
32 | 2653034.2396 | 1220156.1316
33 | 2653029.2544 | 1220150.497
34 | 2653021.62 | 1220141.8681
35 | 2653017.0242 | 1220136.6736
36 | 2653173.185 | 1220246.0761
37 | 2653190.9298 | 1220278.431
38 | 2653189.1821 | 1220219.5526
39 | 2653175.1527 | 1220341.8359
40 | 2653179.0937 | 1220330.425
41 | 2653140.038 | 1220331.7219
42 | 2653180.6948 | 1220330.1077
43 | 2653212.6986 | 1220256.4462
44 | 2653173.1011 | 1220251.223

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9797 | -0.14251 | 0.00035959 | 9.0123e-05
1 | 0.97972 | -0.1424 | 0.002164 | 0.00054236
2 | 0.97985 | -0.14142 | 0 | 0
3 | 0.98123 | -0.13161 | 0 | 0
4 | 0.97922 | -0.14597 | 0 | 0
5 | 0.98224 | -0.12439 | 0.0022959 | 0.0005754
6 | 0.98231 | -0.12394 | 0.0022912 | 0.00057424
7 | 0.98232 | -0.12386 | 0.0026358 | 0.00066059
8 | 0.98248 | -0.1227 | 0 | 0
9 | 0.98483 | -0.10605 | 0.0035246 | 0.00088336
10 | 0.98566 | -0.10013 | 0 | 0
11 | 0.98546 | -0.10155 | 0.0046342 | 0.0011614
12 | 0.99051 | -0.066027 | 0.0082953 | 0.002079
13 | 0.98525 | -0.10304 | 0.0027047 | 0.00067786
14 | 0.99657 | -0.023773 | 0.0068862 | 0.0017258
15 | 0.98094 | -0.13363 | 0.0081961 | 0.0020541
16 | 0.97826 | -0.15279 | 0.00035252 | 8.8351e-05
17 | 0.97823 | -0.15301 | 0.00042147 | 0.00010563
18 | 0.97829 | -0.15262 | 0 | 0
19 | 0.97822 | -0.15312 | 0.00039199 | 9.8241e-05
20 | 0.97845 | -0.15145 | 0.00379 | 0.00094987
21 | 0.97803 | -0.15447 | 0.00013358 | 3.3478e-05
22 | 0.97791 | -0.1553 | 0 | 0
23 | 0.9786 | -0.15037 | 0 | 0
24 | 0.97851 | -0.151 | 0.0018637 | 0.00046708
25 | 0.97854 | -0.15084 | 0.0025726 | 0.00064476
26 | 0.98525 | -0.10305 | 0.0027797 | 0.00069667
27 | 1 | 0 | -0.14401 | -0.036081
28 | 0.99642 | -0.024767 | 0 | 0
29 | 0.99675 | -0.022747 | 0 | 0
30 | 0.97776 | -0.15642 | 0.0037772 | 0.00094666
31 | 0.97774 | -0.15653 | 0.0019993 | 0.00050108
32 | 0.97831 | -0.15249 | 0.0028387 | 0.00071145
33 | 0.97824 | -0.15299 | 0.0018364 | 0.00046025
34 | 0.97816 | -0.15353 | 0.0026961 | 0.0006757
35 | 0.97814 | -0.15366 | 0.0018362 | 0.00046019
36 | 0.9966 | -0.023768 | 0.0096047 | 0.0024072
37 | 0.99458 | -0.037972 | 0.023365 | 0.0058558
38 | 0.99612 | -0.02712 | 0.010129 | 0.0025386
39 | 0.99612 | -0.026915 | 0.0013287 | 0.000333
40 | 0.99614 | -0.026753 | 0 | 0
41 | 0.99631 | -0.025577 | 0.0011993 | 0.00030058
42 | 0.99614 | -0.026781 | 0.0016684 | 0.00041813
43 | 0.99355 | -0.045198 | 0.023121 | 0.0057946
44 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00035959 | -9.0123e-05 | 0.0003596 | 8.9733e-05 | 5.7978e-09 | -3.9009e-07 | 0.00054617 | 0.00054603 | 0.00054617 | 0.9797 | -0.14251 | 0.97972 | -0.1424 | 0.20229
1 | -0.0025236 | -0.00063209 | 0.002524 | 0.00063175 | 3.4047e-07 | -3.3684e-07 | 0.0038328 | 0.0038326 | 0.0038328 | 0.97972 | -0.1424 | 0.97985 | -0.14142 | 1.4196
2 | -0.027074 | -0.006786 | 0.027111 | 0.0067998 | 3.6845e-05 | 1.3731e-05 | 0.041115 | 0.041115 | 0.041115 | 0.97985 | -0.14142 | 0.98123 | -0.13161 | 15.2278
3 | 0.02455 | 0.0061543 | -0.024535 | -0.0061486 | 1.545e-05 | 5.7181e-06 | 0.037282 | 0.037283 | 0.037283 | 0.97985 | -0.14142 | 0.97922 | -0.14597 | 13.8083
4 | 0.0081984 | 0.0020547 | -0.0081961 | -0.0020541 | 2.3016e-06 | 5.839e-07 | 0.012433 | 0.012433 | 0.012433 | 0.98123 | -0.13161 | 0.98094 | -0.13363 | 4.6047
5 | -0.035309 | -0.0088545 | 0.035353 | 0.008871 | 4.3646e-05 | 1.6478e-05 | 0.053548 | 0.053547 | 0.053548 | 0.98123 | -0.13161 | 0.98248 | -0.1227 | 19.8324
6 | 0.013656 | 0.0034229 | -0.013648 | -0.0034201 | 8.3121e-06 | 2.8081e-06 | 0.020752 | 0.020752 | 0.020752 | 0.97922 | -0.14597 | 0.9786 | -0.15037 | 7.6858
7 | 0.010879 | 0.0027257 | -0.01087 | -0.0027231 | 8.243e-06 | 2.5628e-06 | 0.016531 | 0.016531 | 0.016531 | 0.97922 | -0.14597 | 0.97845 | -0.15145 | 6.1226
8 | -0.0022959 | -0.0005754 | 0.002296 | 0.00057521 | 1.4118e-07 | -1.8247e-07 | 0.003478 | 0.0034779 | 0.003478 | 0.98224 | -0.12439 | 0.98231 | -0.12394 | 1.2882
9 | -0.0045873 | -0.0011495 | 0.0045873 | 0.0011495 | 5.2516e-08 | -1.8663e-09 | 0.0069488 | 0.0069488 | 0.0069488 | 0.98231 | -0.12394 | 0.98232 | -0.12386 | 2.5736
10 | -0.0072231 | -0.00181 | 0.0072243 | 0.0018103 | 1.1602e-06 | 2.4958e-07 | 0.010941 | 0.010941 | 0.010941 | 0.98232 | -0.12386 | 0.98248 | -0.1227 | 4.0524
11 | -0.042577 | -0.010681 | 0.042676 | 0.010719 | 9.8549e-05 | 3.7421e-05 | 0.064489 | 0.064489 | 0.064489 | 0.98248 | -0.1227 | 0.98483 | -0.10605 | 23.8848
12 | -0.0462 | -0.011602 | 0.046238 | 0.011617 | 3.807e-05 | 1.4483e-05 | 0.069814 | 0.069814 | 0.069814 | 0.98483 | -0.10605 | 0.98566 | -0.10013 | 25.8571
13 | 0.010122 | 0.0025367 | -0.01012 | -0.0025361 | 1.995e-06 | 5.9283e-07 | 0.01528 | 0.01528 | 0.01528 | 0.98566 | -0.10013 | 0.98546 | -0.10155 | 5.6594
14 | -0.05636 | -0.014153 | 0.056629 | 0.014256 | 0.00026841 | 0.00010248 | 0.085095 | 0.085094 | 0.085095 | 0.98566 | -0.10013 | 0.99051 | -0.066027 | 31.5165
15 | 0.0054856 | 0.0013746 | -0.0054844 | -0.0013745 | 1.1316e-06 | 9.8547e-08 | 0.008283 | 0.0082831 | 0.0082831 | 0.98546 | -0.10155 | 0.98525 | -0.10304 | 3.0678
16 | -0.064924 | -0.016335 | 0.065309 | 0.016482 | 0.00038505 | 0.00014726 | 0.097556 | 0.097556 | 0.097556 | 0.99051 | -0.066027 | 0.99657 | -0.023773 | 36.1319
17 | 0.0027797 | 0.00069667 | -0.0027797 | -0.00069667 | 1.5106e-09 | -1.1676e-09 | 0.0041982 | 0.0041982 | 0.0041982 | 0.98525 | -0.10304 | 0.98525 | -0.10305 | 1.5549
18 | -0.076393 | -0.019259 | 0.076648 | 0.019357 | 0.00025527 | 9.777e-05 | 0.11411 | 0.11411 | 0.11411 | 0.99657 | -0.023773 | 1 | 0 | 42.2614
19 | 0.0041979 | 0.0010511 | -0.0041974 | -0.0010512 | 5.7653e-07 | -8.464e-08 | 0.0062678 | 0.0062679 | 0.0062679 | 0.99657 | -0.023773 | 0.99642 | -0.024767 | 2.3214
20 | 0.00081349 | 0.00020324 | -0.00081347 | -0.00020355 | 2.4443e-08 | -3.1189e-07 | 0.0012372 | 0.0012373 | 0.0012373 | 0.97826 | -0.15279 | 0.97823 | -0.15301 | 0.45825
21 | -0.001166 | -0.00029159 | 0.001166 | 0.00029142 | 2.791e-08 | -1.6784e-07 | 0.0017734 | 0.0017733 | 0.0017734 | 0.97826 | -0.15279 | 0.97829 | -0.15262 | 0.6568
22 | 0.00039199 | 9.792e-05 | -0.00039199 | -9.8241e-05 | 5.7159e-09 | -3.2131e-07 | 0.00059616 | 0.00059627 | 0.00059627 | 0.97823 | -0.15301 | 0.97822 | -0.15312 | 0.22084
23 | -0.0070793 | -0.001773 | 0.0070804 | 0.0017732 | 1.146e-06 | 2.4184e-07 | 0.010767 | 0.010767 | 0.010767 | 0.97829 | -0.15262 | 0.97845 | -0.15145 | 3.9879
24 | 0.0059132 | 0.0014816 | -0.0059117 | -0.0014814 | 1.5127e-06 | 2.0565e-07 | 0.0089941 | 0.0089942 | 0.0089942 | 0.97829 | -0.15262 | 0.97803 | -0.15447 | 3.3312
25 | 0.0057781 | 0.0014479 | -0.0057775 | -0.0014478 | 6.6487e-07 | 8.2723e-08 | 0.008791 | 0.0087911 | 0.0087911 | 0.97803 | -0.15447 | 0.97791 | -0.1553 | 3.2559
26 | 0.0057775 | 0.0014478 | -0.0057766 | -0.0014477 | 8.9466e-07 | 1.1138e-07 | 0.0087911 | 0.0087911 | 0.0087911 | 0.97791 | -0.1553 | 0.97776 | -0.15642 | 3.256
27 | 0.011075 | 0.0027755 | -0.011074 | -0.0027752 | 9.6603e-07 | 3.0297e-07 | 0.01684 | 0.01684 | 0.01684 | 0.9786 | -0.15037 | 0.97851 | -0.151 | 6.237
28 | 0.0025728 | 0.0006446 | -0.0025726 | -0.00064476 | 1.6711e-07 | -1.5557e-07 | 0.003912 | 0.003912 | 0.003912 | 0.9786 | -0.15037 | 0.97854 | -0.15084 | 1.4489
29 | 0.0092101 | 0.0023081 | -0.0092082 | -0.0023076 | 1.8985e-06 | 5.3539e-07 | 0.014006 | 0.014006 | 0.014006 | 0.97851 | -0.151 | 0.97831 | -0.15249 | 5.1873
30 | 0.066558 | 0.016725 | -0.066348 | -0.016644 | 0.00021001 | 8.0325e-05 | 0.099055 | 0.099055 | 0.099055 | 1 | 0 | 0.99675 | -0.022747 | 36.687
31 | 0.0041974 | 0.0010512 | -0.0041969 | -0.0010512 | 4.703e-07 | -6.8972e-08 | 0.0062679 | 0.006268 | 0.006268 | 0.99642 | -0.024767 | 0.99631 | -0.025577 | 2.3215
32 | 0.019741 | 0.0049481 | -0.019738 | -0.0049471 | 2.7899e-06 | 1.0059e-06 | 0.029471 | 0.029471 | 0.029471 | 0.99675 | -0.022747 | 0.9966 | -0.023768 | 10.9153
33 | 0.046607 | 0.011696 | -0.046509 | -0.011659 | 9.8282e-05 | 3.7378e-05 | 0.069584 | 0.069584 | 0.069584 | 0.99675 | -0.022747 | 0.99458 | -0.037972 | 25.7718
34 | 0.0019994 | 0.00050102 | -0.0019993 | -0.00050108 | 3.0543e-08 | -5.456e-08 | 0.0030427 | 0.0030428 | 0.0030428 | 0.97776 | -0.15642 | 0.97774 | -0.15653 | 1.1269
35 | 0.0063695 | 0.0015961 | -0.0063691 | -0.0015961 | 4.4062e-07 | 7.5012e-08 | 0.009688 | 0.0096881 | 0.0096881 | 0.97831 | -0.15249 | 0.97824 | -0.15299 | 3.5882
36 | 0.0045326 | 0.0011358 | -0.0045323 | -0.0011358 | 3.4175e-07 | -1.319e-08 | 0.0068946 | 0.0068947 | 0.0068947 | 0.97824 | -0.15299 | 0.97816 | -0.15353 | 2.5536
37 | 0.0018362 | 0.00046012 | -0.0018362 | -0.00046019 | 3.3769e-08 | -7.4072e-08 | 0.0027933 | 0.0027933 | 0.0027933 | 0.97816 | -0.15353 | 0.97814 | -0.15366 | 1.0346
38 | 0.010134 | 0.0025399 | -0.010129 | -0.0025386 | 4.7026e-06 | 1.3799e-06 | 0.015131 | 0.015131 | 0.015131 | 0.9966 | -0.023768 | 0.99612 | -0.02712 | 5.604
39 | 0.023144 | 0.0058031 | -0.023121 | -0.0057946 | 2.3151e-05 | 8.5029e-06 | 0.034627 | 0.034627 | 0.034627 | 0.99458 | -0.037972 | 0.99355 | -0.045198 | 12.8249
40 | -0.0013287 | -0.000333 | 0.0013287 | 0.00033285 | 2.9675e-08 | -1.4574e-07 | 0.0019848 | 0.0019848 | 0.0019848 | 0.99612 | -0.026915 | 0.99614 | -0.026753 | 0.73511
41 | -0.0029971 | -0.00075097 | 0.0029976 | 0.00075065 | 4.8755e-07 | -3.2008e-07 | 0.0044769 | 0.0044767 | 0.0044769 | 0.99614 | -0.026753 | 0.99631 | -0.025577 | 1.6581
42 | 0.0016684 | 0.00041811 | -0.0016684 | -0.00041813 | 6.3261e-09 | -1.8816e-08 | 0.0024922 | 0.0024922 | 0.0024922 | 0.99614 | -0.026753 | 0.99614 | -0.026781 | 0.92303

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.14908 | 0.037354

## res_load
| p_mw | q_mvar
0 | 0.00035959 | 9.0123e-05
1 | 0.002164 | 0.00054236
2 | 0.0022959 | 0.0005754
3 | 0.0022912 | 0.00057424
4 | 0.0026358 | 0.00066059
5 | 0.0035246 | 0.00088336
6 | 0.0046342 | 0.0011614
7 | 0.0082953 | 0.002079
8 | 0.0027047 | 0.00067786
9 | 0.0068862 | 0.0017258
10 | 0.0081961 | 0.0020541
11 | 0.00035252 | 8.8351e-05
12 | 0.00042147 | 0.00010563
13 | 0.00039199 | 9.8241e-05
14 | 0.00379 | 0.00094987
15 | 0.00013358 | 3.3478e-05
16 | 0.0018637 | 0.00046708
17 | 0.0025726 | 0.00064476
18 | 0.0027797 | 0.00069667
19 | 0.0050779 | 0.0012726
20 | 0.0037772 | 0.00094666
21 | 0.0019993 | 0.00050108
22 | 0.0028387 | 0.00071145
23 | 0.0018364 | 0.00046025
24 | 0.0026961 | 0.0006757
25 | 0.0018362 | 0.00046019
26 | 0.0096047 | 0.0024072
27 | 0.023365 | 0.0058558
28 | 0.010129 | 0.0025386
29 | 0.0013287 | 0.000333
30 | 0.0011993 | 0.00030058
31 | 0.0016684 | 0.00041813
32 | 0.023121 | 0.0057946

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1