## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1094-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1094-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1094-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1094-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1094-4_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1094-4_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1094-4_0_4_node_126 | 0.4 | n |  | TRUE
7 | bus_LV_1094-4_0_4_node_74 | 0.4 | n |  | TRUE
8 | bus_LV_1094-4_0_4_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_1094-4_0_4_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_1094-4_0_4_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_1094-4_0_4_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_1094-4_0_4_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_1094-4_0_4_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_1094-4_0_4_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_1094-4_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1094-4_0_4_node_6 | 0.4 | n |  | TRUE
17 | bus_LV_1094-4_0_4_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_1094-4_0_4_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_1094-4_0_4_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_1094-4_0_4_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_1094-4_0_4_node_66 | 0.4 | n |  | TRUE
22 | bus_LV_1094-4_0_4_node_67 | 0.4 | n |  | TRUE
23 | bus_LV_1094-4_0_4_node_65 | 0.4 | n |  | TRUE
24 | bus_LV_1094-4_0_4_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_1094-4_0_4_node_59 | 0.4 | n |  | TRUE
26 | bus_LV_1094-4_0_4_node_61 | 0.4 | n |  | TRUE
27 | bus_LV_1094-4_0_4_node_58 | 0.4 | n |  | TRUE
28 | bus_LV_1094-4_0_4_node_12 | 0.4 | n |  | TRUE
29 | bus_LV_1094-4_0_4_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_1094-4_0_4_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_1094-4_0_4_node_64 | 0.4 | n |  | TRUE
32 | bus_LV_1094-4_0_4_node_77 | 0.4 | n |  | TRUE
33 | bus_LV_1094-4_0_4_node_51 | 0.4 | n |  | TRUE
34 | bus_LV_1094-4_0_4_node_68 | 0.4 | n |  | TRUE
35 | bus_LV_1094-4_0_4_node_69 | 0.4 | n |  | TRUE
36 | bus_LV_1094-4_0_4_node_70 | 0.4 | n |  | TRUE
37 | bus_LV_1094-4_0_4_node_71 | 0.4 | n |  | TRUE
38 | bus_LV_1094-4_0_4_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_1094-4_0_4_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_1094-4_0_4_node_48 | 0.4 | n |  | TRUE
41 | bus_LV_1094-4_0_4_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_1094-4_0_4_node_125 | 0.4 | n |  | TRUE
43 | bus_LV_1094-4_0_4_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_1094-4_0_4_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_1094-4_0_4_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_1094-4_0_4_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_1094-4_0_4_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_1094-4_0_4_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_1094-4_0_4_node_31 | 0.4 | n |  | TRUE
50 | bus_LV_1094-4_0_4_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_1094-4_0_4_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_1094-4_0_4_node_34 | 0.4 | n |  | TRUE
53 | bus_LV_1094-4_0_4_node_35 | 0.4 | n |  | TRUE
54 | bus_LV_1094-4_0_4_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_1094-4_0_4_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_1094-4_0_4_node_50 | 0.4 | n |  | TRUE
57 | bus_LV_1094-4_0_4_node_57 | 0.4 | n |  | TRUE
58 | bus_LV_1094-4_0_4_node_60 | 0.4 | n |  | TRUE
59 | bus_LV_1094-4_0_4_node_127 | 0.4 | n |  | TRUE
60 | bus_LV_1094-4_0_4_node_56 | 0.4 | n |  | TRUE
61 | bus_LV_1094-4_0_4_node_39 | 0.4 | n |  | TRUE
62 | bus_LV_1094-4_0_4_node_40 | 0.4 | n |  | TRUE
63 | bus_LV_1094-4_0_4_node_41 | 0.4 | n |  | TRUE
64 | bus_LV_1094-4_0_4_node_42 | 0.4 | n |  | TRUE
65 | bus_LV_1094-4_0_4_node_43 | 0.4 | n |  | TRUE
66 | bus_LV_1094-4_0_4_node_45 | 0.4 | n |  | TRUE
67 | bus_LV_1094-4_0_4_node_44 | 0.4 | n |  | TRUE
68 | bus_LV_1094-4_0_4_node_46 | 0.4 | n |  | TRUE
69 | bus_LV_1094-4_0_4_node_124 | 0.4 | n |  | TRUE
70 | bus_LV_1094-4_0_4_node_123 | 0.4 | n |  | TRUE
71 | bus_LV_1094-4_0_4_node_47 | 0.4 | n |  | TRUE
72 | bus_LV_1094-4_0_4_node_49 | 0.4 | n |  | TRUE
73 | bus_LV_1094-4_0_4_node_52 | 0.4 | n |  | TRUE
74 | bus_LV_1094-4_0_4_node_53 | 0.4 | n |  | TRUE
75 | bus_LV_1094-4_0_4_node_54 | 0.4 | n |  | TRUE
76 | bus_LV_1094-4_0_4_node_55 | 0.4 | n |  | TRUE
77 | bus_LV_1094-4_0_4_node_62 | 0.4 | n |  | TRUE
78 | bus_LV_1094-4_0_4_node_63 | 0.4 | n |  | TRUE
79 | bus_LV_1094-4_0_4_node_109 | 0.4 | n |  | TRUE
80 | bus_LV_1094-4_0_4_node_106 | 0.4 | n |  | TRUE
81 | bus_LV_1094-4_0_4_node_110 | 0.4 | n |  | TRUE
82 | bus_LV_1094-4_0_4_node_107 | 0.4 | n |  | TRUE
83 | bus_LV_1094-4_0_4_node_78 | 0.4 | n |  | TRUE
84 | bus_LV_1094-4_0_4_node_72 | 0.4 | n |  | TRUE
85 | bus_LV_1094-4_0_4_node_73 | 0.4 | n |  | TRUE
86 | bus_LV_1094-4_0_4_node_75 | 0.4 | n |  | TRUE
87 | bus_LV_1094-4_0_4_node_103 | 0.4 | n |  | TRUE
88 | bus_LV_1094-4_0_4_node_76 | 0.4 | n |  | TRUE
89 | bus_LV_1094-4_0_4_node_114 | 0.4 | n |  | TRUE
90 | bus_LV_1094-4_0_4_node_113 | 0.4 | n |  | TRUE
91 | bus_LV_1094-4_0_4_node_79 | 0.4 | n |  | TRUE
92 | bus_LV_1094-4_0_4_node_80 | 0.4 | n |  | TRUE
93 | bus_LV_1094-4_0_4_node_81 | 0.4 | n |  | TRUE
94 | bus_LV_1094-4_0_4_node_82 | 0.4 | n |  | TRUE
95 | bus_LV_1094-4_0_4_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_1094-4_0_4_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_1094-4_0_4_node_85 | 0.4 | n |  | TRUE
98 | bus_LV_1094-4_0_4_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_1094-4_0_4_node_87 | 0.4 | n |  | TRUE
100 | bus_LV_1094-4_0_4_node_88 | 0.4 | n |  | TRUE
101 | bus_LV_1094-4_0_4_node_89 | 0.4 | n |  | TRUE
102 | bus_LV_1094-4_0_4_node_90 | 0.4 | n |  | TRUE
103 | bus_LV_1094-4_0_4_node_91 | 0.4 | n |  | TRUE
104 | bus_LV_1094-4_0_4_node_92 | 0.4 | n |  | TRUE
105 | bus_LV_1094-4_0_4_node_93 | 0.4 | n |  | TRUE
106 | bus_LV_1094-4_0_4_node_94 | 0.4 | n |  | TRUE
107 | bus_LV_1094-4_0_4_node_95 | 0.4 | n |  | TRUE
108 | bus_LV_1094-4_0_4_node_96 | 0.4 | n |  | TRUE
109 | bus_LV_1094-4_0_4_node_97 | 0.4 | n |  | TRUE
110 | bus_LV_1094-4_0_4_node_105 | 0.4 | n |  | TRUE
111 | bus_LV_1094-4_0_4_node_98 | 0.4 | n |  | TRUE
112 | bus_LV_1094-4_0_4_node_108 | 0.4 | n |  | TRUE
113 | bus_LV_1094-4_0_4_node_104 | 0.4 | n |  | TRUE
114 | bus_LV_1094-4_0_4_node_112 | 0.4 | n |  | TRUE
115 | bus_LV_1094-4_0_4_node_111 | 0.4 | n |  | TRUE
116 | bus_LV_1094-4_0_4_node_101 | 0.4 | n |  | TRUE
117 | bus_LV_1094-4_0_4_node_102 | 0.4 | n |  | TRUE
118 | bus_LV_1094-4_0_4_node_100 | 0.4 | n |  | TRUE
119 | bus_LV_1094-4_0_4_node_99 | 0.4 | n |  | TRUE
120 | bus_LV_1094-4_0_4_node_120 | 0.4 | n |  | TRUE
121 | bus_LV_1094-4_0_4_node_121 | 0.4 | n |  | TRUE
122 | bus_LV_1094-4_0_4_node_118 | 0.4 | n |  | TRUE
123 | bus_LV_1094-4_0_4_node_115 | 0.4 | n |  | TRUE
124 | bus_LV_1094-4_0_4_node_116 | 0.4 | n |  | TRUE
125 | bus_LV_1094-4_0_4_node_117 | 0.4 | n |  | TRUE
126 | bus_LV_1094-4_0_4_node_119 | 0.4 | n |  | TRUE
127 | bus_LV_1094-4_0_4_node_122 | 0.4 | n |  | TRUE
128 | bus_MV_2_1_node_244 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1094-4_0_4_load_0 | 0 | 0.0017983 | 0.0004507 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1094-4_0_4_load_1 | 1 | 0.00040758 | 0.00010215 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1094-4_0_4_load_4 | 4 | 0.0031011 | 0.00077721 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1094-4_0_4_load_5 | 5 | 0.0010913 | 0.00027349 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1094-4_0_4_load_126 | 6 | 0.0025891 | 0.00064889 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1094-4_0_4_load_74 | 7 | 0.0025752 | 0.00064541 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1094-4_0_4_load_18 | 8 | 0.0014688 | 0.00036812 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1094-4_0_4_load_19 | 9 | 0.0025602 | 0.00064165 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1094-4_0_4_load_14 | 11 | 0.0038292 | 0.00095968 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1094-4_0_4_load_15 | 14 | 0.00070299 | 0.00017619 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1094-4_0_4_load_13 | 15 | 0.0015686 | 0.00039314 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1094-4_0_4_load_6 | 16 | 0.0071158 | 0.0017834 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1094-4_0_4_load_7 | 17 | 0.0007049 | 0.00017666 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1094-4_0_4_load_8 | 18 | 0.00032633 | 8.1786e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1094-4_0_4_load_9 | 19 | 0.00015859 | 3.9747e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1094-4_0_4_load_10 | 20 | 0.00033938 | 8.5058e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1094-4_0_4_load_66 | 21 | 0.0035864 | 0.00089883 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1094-4_0_4_load_67 | 22 | 0.0033458 | 0.00083853 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1094-4_0_4_load_65 | 23 | 0.0022706 | 0.00056906 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1094-4_0_4_load_59 | 25 | 0.0024161 | 0.00060552 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1094-4_0_4_load_58 | 27 | 0.0031292 | 0.00078426 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1094-4_0_4_load_21 | 29 | 0.00013761 | 3.4488e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1094-4_0_4_load_20 | 30 | 0.00065602 | 0.00016441 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1094-4_0_4_load_77 | 32 | 0.0043552 | 0.0010915 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1094-4_0_4_load_68 | 34 | 0.003044 | 0.00076291 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1094-4_0_4_load_69 | 35 | 0.0037425 | 0.00093795 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1094-4_0_4_load_70 | 36 | 0.0021819 | 0.00054682 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1094-4_0_4_load_71 | 37 | 0.0014663 | 0.0003675 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1094-4_0_4_load_22 | 41 | 0.0018084 | 0.00045323 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1094-4_0_4_load_125 | 42 | 0.00091848 | 0.00023019 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1094-4_0_4_load_26 | 44 | 0.00025611 | 6.4187e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1094-4_0_4_load_27 | 45 | 0.00025893 | 6.4893e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1094-4_0_4_load_29 | 46 | 0.0011114 | 0.00027854 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1094-4_0_4_load_32 | 47 | 0.0011154 | 0.00027955 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1094-4_0_4_load_33 | 50 | 0.00074281 | 0.00018617 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1094-4_0_4_load_36 | 51 | 0.00025088 | 6.2877e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1094-4_0_4_load_34 | 52 | 0.00087339 | 0.00021889 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1094-4_0_4_load_37 | 54 | 0.00032673 | 8.1886e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1094-4_0_4_load_57 | 57 | 0.00066783 | 0.00016737 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1094-4_0_4_load_60 | 58 | 0.0031335 | 0.00078533 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1094-4_0_4_load_127 | 59 | 0.00035693 | 8.9455e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1094-4_0_4_load_56 | 60 | 0.00045066 | 0.00011295 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1094-4_0_4_load_39 | 61 | 0.0020465 | 0.00051289 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1094-4_0_4_load_42 | 64 | 0.0012799 | 0.00032078 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1094-4_0_4_load_43 | 65 | 0.00019018 | 4.7664e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1094-4_0_4_load_45 | 66 | 0.00051185 | 0.00012828 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1094-4_0_4_load_44 | 67 | 0.0028536 | 0.00071518 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1094-4_0_4_load_123 | 70 | 0.0021174 | 0.00053067 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1094-4_0_4_load_47 | 71 | 0.0086377 | 0.0021648 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1094-4_0_4_load_49 | 72 | 0.0010045 | 0.00025175 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1094-4_0_4_load_52 | 73 | 0.0012138 | 0.0003042 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1094-4_0_4_load_53 | 74 | 0.0024051 | 0.00060278 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1094-4_0_4_load_55 | 76 | 0.0004945 | 0.00012393 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1094-4_0_4_load_62 | 77 | 0.0034069 | 0.00085386 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1094-4_0_4_load_109 | 79 | 0.0079834 | 0.0020008 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1094-4_0_4_load_106 | 80 | 0.0068423 | 0.0017148 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1094-4_0_4_load_110 | 81 | 0.004471 | 0.0011205 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1094-4_0_4_load_107 | 82 | 0.0069472 | 0.0017411 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1094-4_0_4_load_73 | 85 | 0.0020851 | 0.00052258 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1094-4_0_4_load_75 | 86 | 0.0015288 | 0.00038314 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1094-4_0_4_load_76 | 88 | 0.0025435 | 0.00063747 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1094-4_0_4_load_113 | 90 | 0.003201 | 0.00080224 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1094-4_0_4_load_79 | 91 | 0.0034075 | 0.00085401 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1094-4_0_4_load_80 | 92 | 0.0085121 | 0.0021333 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1094-4_0_4_load_81 | 93 | 0.0025027 | 0.00062723 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1094-4_0_4_load_82 | 94 | 0.0032386 | 0.00081167 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1094-4_0_4_load_83 | 95 | 0.0057215 | 0.0014339 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1094-4_0_4_load_84 | 96 | 0.0082798 | 0.0020751 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1094-4_0_4_load_85 | 97 | 0.0015281 | 0.00038298 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1094-4_0_4_load_86 | 98 | 0.0023172 | 0.00058076 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1094-4_0_4_load_87 | 99 | 0.0028466 | 0.00071341 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1094-4_0_4_load_88 | 100 | 0.0051299 | 0.0012857 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1094-4_0_4_load_89 | 101 | 0.0056255 | 0.0014099 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1094-4_0_4_load_90 | 102 | 0.0031603 | 0.00079206 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1094-4_0_4_load_91 | 103 | 0.0014051 | 0.00035215 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1094-4_0_4_load_92 | 104 | 0.0019696 | 0.00049362 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1094-4_0_4_load_93 | 105 | 0.0026543 | 0.00066524 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1094-4_0_4_load_94 | 106 | 0.0028643 | 0.00071787 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1094-4_0_4_load_95 | 107 | 0.0014852 | 0.00037223 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1094-4_0_4_load_97 | 109 | 0.0021513 | 0.00053915 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1094-4_0_4_load_98 | 111 | 0.0010811 | 0.00027094 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1094-4_0_4_load_108 | 112 | 0.0067049 | 0.0016804 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1094-4_0_4_load_112 | 114 | 0.0049838 | 0.001249 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1094-4_0_4_load_111 | 115 | 0.0054726 | 0.0013716 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1094-4_0_4_load_102 | 117 | 0.0021465 | 0.00053795 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1094-4_0_4_load_100 | 118 | 0.0027782 | 0.00069629 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1094-4_0_4_load_99 | 119 | 0.0032113 | 0.00080482 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1094-4_0_4_load_120 | 120 | 0.0017156 | 0.00042997 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1094-4_0_4_load_121 | 121 | 0.0016198 | 0.00040595 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1094-4_0_4_load_118 | 122 | 0.0029573 | 0.00074118 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1094-4_0_4_load_115 | 123 | 0.001794 | 0.00044962 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1094-4_0_4_load_116 | 124 | 0.00072178 | 0.0001809 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1094-4_0_4_load_117 | 125 | 0.0013632 | 0.00034166 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1094-4_0_4_load_119 | 126 | 0.0014885 | 0.00037306 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1094-4_0_4_load_122 | 127 | 0.0017883 | 0.00044819 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 34 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1094-4_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.022791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1094-4_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.019155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1094-4_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.020625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1094-4_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.030342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1094-4_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.016545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1094-4_0_4_line_5 | NAYY 4x150 SE | 3 | 8 | 0.029241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1094-4_0_4_line_6 | NAYY 4x150 SE | 3 | 9 | 0.14657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1094-4_0_4_line_7 | NAYY 4x150 SE | 4 | 10 | 0.023662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1094-4_0_4_line_8 | NAYY 4x150 SE | 5 | 11 | 0.0073581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1094-4_0_4_line_9 | NAYY 4x150 SE | 6 | 7 | 0.018216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1094-4_0_4_line_10 | NAYY 4x150 SE | 7 | 87 | 0.054899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1094-4_0_4_line_11 | NAYY 4x150 SE | 9 | 12 | 0.067777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1094-4_0_4_line_12 | NAYY 4x150 SE | 10 | 13 | 0.04953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1094-4_0_4_line_13 | NAYY 4x150 SE | 11 | 15 | 0.064925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1094-4_0_4_line_14 | NAYY 4x150 SE | 12 | 38 | 0.18237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1094-4_0_4_line_15 | NAYY 4x150 SE | 12 | 39 | 0.012825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1094-4_0_4_line_16 | NAYY 4x150 SE | 13 | 14 | 0.020075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1094-4_0_4_line_17 | NAYY 4x150 SE | 14 | 19 | 0.016741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1094-4_0_4_line_18 | NAYY 4x150 SE | 16 | 17 | 0.0076372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1094-4_0_4_line_19 | NAYY 4x150 SE | 16 | 18 | 0.12022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1094-4_0_4_line_20 | NAYY 4x150 SE | 17 | 19 | 0.0101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1094-4_0_4_line_21 | NAYY 4x150 SE | 18 | 20 | 0.022308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_1094-4_0_4_line_22 | NAYY 4x150 SE | 20 | 24 | 0.13713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1094-4_0_4_line_23 | NAYY 4x150 SE | 20 | 25 | 0.14159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_1094-4_0_4_line_24 | NAYY 4x150 SE | 21 | 22 | 0.018359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_1094-4_0_4_line_25 | NAYY 4x150 SE | 21 | 23 | 0.0030944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_1094-4_0_4_line_26 | NAYY 4x150 SE | 22 | 34 | 0.0035054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_1094-4_0_4_line_27 | NAYY 4x150 SE | 23 | 77 | 0.019228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_1094-4_0_4_line_28 | NAYY 4x150 SE | 24 | 28 | 0.081998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1094-4_0_4_line_29 | NAYY 4x150 SE | 25 | 26 | 0.0866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_1094-4_0_4_line_30 | NAYY 4x150 SE | 25 | 27 | 0.0013403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_1094-4_0_4_line_31 | NAYY 4x150 SE | 26 | 78 | 0.045236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_1094-4_0_4_line_32 | NAYY 4x150 SE | 26 | 31 | 0.02479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_1094-4_0_4_line_33 | NAYY 4x150 SE | 27 | 58 | 0.021508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_1094-4_0_4_line_34 | NAYY 4x150 SE | 28 | 29 | 0.036018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1094-4_0_4_line_35 | NAYY 4x150 SE | 28 | 30 | 0.064204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1094-4_0_4_line_36 | NAYY 4x150 SE | 29 | 33 | 0.0077361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1094-4_0_4_line_37 | NAYY 4x150 SE | 31 | 32 | 0.087633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_1094-4_0_4_line_38 | NAYY 4x150 SE | 32 | 83 | 0.0187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_1094-4_0_4_line_39 | NAYY 4x150 SE | 33 | 40 | 0.12494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1094-4_0_4_line_40 | NAYY 4x150 SE | 34 | 35 | 0.017865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1094-4_0_4_line_41 | NAYY 4x150 SE | 35 | 36 | 0.0046009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1094-4_0_4_line_42 | NAYY 4x150 SE | 36 | 37 | 0.016221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1094-4_0_4_line_43 | NAYY 4x150 SE | 37 | 84 | 0.019322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1094-4_0_4_line_44 | NAYY 4x150 SE | 38 | 42 | 0.055524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1094-4_0_4_line_45 | NAYY 4x150 SE | 38 | 43 | 0.026155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1094-4_0_4_line_46 | NAYY 4x150 SE | 39 | 41 | 0.078088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1094-4_0_4_line_47 | NAYY 4x150 SE | 40 | 56 | 0.09301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1094-4_0_4_line_48 | NAYY 4x150 SE | 40 | 71 | 0.023675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1094-4_0_4_line_49 | NAYY 4x150 SE | 43 | 44 | 0.025423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1094-4_0_4_line_50 | NAYY 4x150 SE | 44 | 45 | 0.0060024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1094-4_0_4_line_51 | NAYY 4x150 SE | 45 | 46 | 0.018424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1094-4_0_4_line_52 | NAYY 4x150 SE | 46 | 47 | 0.0014232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1094-4_0_4_line_53 | NAYY 4x150 SE | 47 | 49 | 0.022906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1094-4_0_4_line_54 | NAYY 4x150 SE | 48 | 49 | 0.11593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1094-4_0_4_line_55 | NAYY 4x150 SE | 48 | 50 | 0.041084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1094-4_0_4_line_56 | NAYY 4x150 SE | 49 | 51 | 0.0193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1094-4_0_4_line_57 | NAYY 4x150 SE | 50 | 52 | 0.027152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1094-4_0_4_line_58 | NAYY 4x150 SE | 52 | 53 | 0.044735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1094-4_0_4_line_59 | NAYY 4x150 SE | 53 | 54 | 0.033688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1094-4_0_4_line_60 | NAYY 4x150 SE | 55 | 56 | 0.080602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1094-4_0_4_line_61 | NAYY 4x150 SE | 55 | 57 | 0.019846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1094-4_0_4_line_62 | NAYY 4x150 SE | 56 | 59 | 0.027543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1094-4_0_4_line_63 | NAYY 4x150 SE | 57 | 60 | 0.0018601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1094-4_0_4_line_64 | NAYY 4x150 SE | 58 | 77 | 0.0017184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
65 | LV_1094-4_0_4_line_65 | NAYY 4x150 SE | 60 | 76 | 0.034554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1094-4_0_4_line_66 | NAYY 4x150 SE | 61 | 62 | 0.075937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1094-4_0_4_line_67 | NAYY 4x150 SE | 62 | 63 | 0.17206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1094-4_0_4_line_68 | NAYY 4x150 SE | 63 | 64 | 0.020521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1094-4_0_4_line_69 | NAYY 4x150 SE | 64 | 65 | 0.0068916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1094-4_0_4_line_70 | NAYY 4x150 SE | 65 | 66 | 0.21352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1094-4_0_4_line_71 | NAYY 4x150 SE | 66 | 68 | 0.083486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1094-4_0_4_line_72 | NAYY 4x150 SE | 66 | 67 | 0.018516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1094-4_0_4_line_73 | NAYY 4x150 SE | 68 | 69 | 0.2272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1094-4_0_4_line_74 | NAYY 4x150 SE | 69 | 70 | 0.16393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1094-4_0_4_line_75 | NAYY 4x150 SE | 70 | 104 | 0.023593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1094-4_0_4_line_76 | NAYY 4x150 SE | 71 | 72 | 0.020624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1094-4_0_4_line_77 | NAYY 4x150 SE | 73 | 74 | 0.0021217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1094-4_0_4_line_78 | NAYY 4x150 SE | 73 | 75 | 0.043275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1094-4_0_4_line_79 | NAYY 4x150 SE | 75 | 76 | 0.019599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1094-4_0_4_line_80 | NAYY 4x150 SE | 78 | 79 | 0.023209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1094-4_0_4_line_81 | NAYY 4x150 SE | 78 | 80 | 0.0036802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1094-4_0_4_line_82 | NAYY 4x150 SE | 79 | 81 | 0.029106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1094-4_0_4_line_83 | NAYY 4x150 SE | 80 | 82 | 0.029435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1094-4_0_4_line_84 | NAYY 4x150 SE | 81 | 115 | 0.02547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1094-4_0_4_line_85 | NAYY 4x150 SE | 83 | 91 | 0.012046 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1094-4_0_4_line_86 | NAYY 4x150 SE | 83 | 92 | 0.013647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
87 | LV_1094-4_0_4_line_87 | NAYY 4x150 SE | 84 | 85 | 0.016374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1094-4_0_4_line_88 | NAYY 4x150 SE | 85 | 86 | 0.016535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1094-4_0_4_line_89 | NAYY 4x150 SE | 86 | 88 | 0.0010575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1094-4_0_4_line_90 | NAYY 4x150 SE | 87 | 89 | 0.026751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1094-4_0_4_line_91 | NAYY 4x150 SE | 87 | 90 | 0.020663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1094-4_0_4_line_92 | NAYY 4x150 SE | 89 | 122 | 0.005058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1094-4_0_4_line_93 | NAYY 4x150 SE | 89 | 123 | 0.036249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1094-4_0_4_line_94 | NAYY 4x150 SE | 90 | 114 | 0.049179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1094-4_0_4_line_95 | NAYY 4x150 SE | 91 | 93 | 0.014092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1094-4_0_4_line_96 | NAYY 4x150 SE | 92 | 94 | 0.018439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_1094-4_0_4_line_97 | NAYY 4x150 SE | 94 | 95 | 0.018939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
98 | LV_1094-4_0_4_line_98 | NAYY 4x150 SE | 95 | 96 | 0.00522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
99 | LV_1094-4_0_4_line_99 | NAYY 4x150 SE | 96 | 97 | 0.015099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_1094-4_0_4_line_100 | NAYY 4x150 SE | 97 | 98 | 0.0048361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
101 | LV_1094-4_0_4_line_101 | NAYY 4x150 SE | 98 | 99 | 0.028178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
102 | LV_1094-4_0_4_line_102 | NAYY 4x150 SE | 99 | 100 | 0.020843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
103 | LV_1094-4_0_4_line_103 | NAYY 4x150 SE | 100 | 101 | 0.028926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1094-4_0_4_line_104 | NAYY 4x150 SE | 101 | 102 | 0.031784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1094-4_0_4_line_105 | NAYY 4x150 SE | 102 | 103 | 0.02898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1094-4_0_4_line_106 | NAYY 4x150 SE | 103 | 104 | 0.031359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1094-4_0_4_line_107 | NAYY 4x150 SE | 105 | 106 | 0.0060942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1094-4_0_4_line_108 | NAYY 4x150 SE | 105 | 107 | 0.016175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1094-4_0_4_line_109 | NAYY 4x150 SE | 106 | 108 | 0.040591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1094-4_0_4_line_110 | NAYY 4x150 SE | 107 | 109 | 0.004725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1094-4_0_4_line_111 | NAYY 4x150 SE | 108 | 110 | 0.005222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1094-4_0_4_line_112 | NAYY 4x150 SE | 109 | 111 | 0.019116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1094-4_0_4_line_113 | NAYY 4x150 SE | 110 | 112 | 0.02205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1094-4_0_4_line_114 | NAYY 4x150 SE | 110 | 113 | 0.003712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1094-4_0_4_line_115 | NAYY 4x150 SE | 111 | 119 | 0.0037364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1094-4_0_4_line_116 | NAYY 4x150 SE | 113 | 114 | 0.019679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1094-4_0_4_line_117 | NAYY 4x150 SE | 113 | 115 | 0.014021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1094-4_0_4_line_118 | NAYY 4x150 SE | 116 | 117 | 0.016078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1094-4_0_4_line_119 | NAYY 4x150 SE | 116 | 118 | 0.032397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1094-4_0_4_line_120 | NAYY 4x150 SE | 117 | 120 | 0.025007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1094-4_0_4_line_121 | NAYY 4x150 SE | 118 | 119 | 0.019886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_1094-4_0_4_line_122 | NAYY 4x150 SE | 120 | 121 | 0.029305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_1094-4_0_4_line_123 | NAYY 4x150 SE | 121 | 127 | 0.0022918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_1094-4_0_4_line_124 | NAYY 4x150 SE | 123 | 124 | 0.017143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_1094-4_0_4_line_125 | NAYY 4x150 SE | 124 | 125 | 0.022079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_1094-4_0_4_line_126 | NAYY 4x150 SE | 125 | 126 | 0.039374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1094-4_0_4_trafo_68 | 0.25 MVA 20/0.4 kV | 128 | 34 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2653122.5375 | 1219736.6349 | 2653122.5375 | 1219736.6349 | 2653103.1139 | 1219744.0997 | 2653101.1767 | 1219744.5201
1 | 2653135.1061 | 1219749.0767 | 2653132.8362 | 1219743.2418 | 2653128.7985 | 1219738.2361 | 2653122.5375 | 1219736.6349
2 | 2653081.3087 | 1219742.0931 | 2653088.25 | 1219744.8344 | 2653094.7965 | 1219745.9045 | 2653101.1767 | 1219744.5201
3 | 2653135.1061 | 1219749.0767 | 2653134.1984 | 1219753.8605 | 2653129.2465 | 1219760.3203 | 2653122.8654 | 1219776.437
4 | 2653135.1061 | 1219749.0767 | 2653138.5939 | 1219751.9318 | 2653149.81 | 1219756.3031
5 | 2653081.3087 | 1219742.0931 | 2653085.0966 | 1219758.1033 | 2653090.3685 | 1219769.7549
6 | 2653081.3087 | 1219742.0931 | 2653074.3274 | 1219734.4596 | 2653070.7443 | 1219726.1115 | 2653068.1609 | 1219717.9835 | 2653064.9852 | 1219686.9029 | 2653063.2299 | 1219676.959 | 2653063.1163 | 1219668.4194 | 2653065.0207 | 1219659.9201 | 2653068.7448 | 1219652.4487 | 2653074.7423 | 1219642.7517 | 2653082.8036 | 1219628.8261 | 2653085.2937 | 1219623.5784 | 2653090.0794 | 1219610.2351 | 2653091.1393 | 1219606.1734
7 | 2653117.706 | 1219799.3746 | 2653118.6142 | 1219789.4322 | 2653121.965 | 1219778.7111 | 2653122.8654 | 1219776.437
8 | 2653156.6658 | 1219758.9751 | 2653149.81 | 1219756.3031
9 | 2653391.0144 | 1219928.2732 | 2653377.5962 | 1219915.9121
10 | 2653421.4787 | 1219971.506 | 2653412.8316 | 1219962.712 | 2653396.0631 | 1219947.4302 | 2653394.072 | 1219941.8534 | 2653393.3662 | 1219935.0985 | 2653391.0144 | 1219928.2732
11 | 2653073.2093 | 1219544.8226 | 2653078.4101 | 1219550.4724 | 2653092.6341 | 1219574.7584 | 2653094.2062 | 1219582.2658 | 2653094.5473 | 1219589.9736 | 2653092.8292 | 1219599.6976 | 2653091.1393 | 1219606.1734
12 | 2653117.706 | 1219799.3746 | 2653121.4847 | 1219808.7474 | 2653129.5142 | 1219822.1938 | 2653133.509 | 1219831.1572 | 2653133.4375 | 1219845.1206
13 | 2653156.6658 | 1219758.9751 | 2653182.4744 | 1219769.0336 | 2653189.3471 | 1219770.1178 | 2653195.2369 | 1219768.247 | 2653215.8131 | 1219755.7236
14 | 2652964.0825 | 1219676.2434 | 2652965.5166 | 1219675.4001 | 2652973.9855 | 1219666.8034 | 2652999.3696 | 1219635.0319 | 2653017.9621 | 1219610.1376 | 2653022.7969 | 1219606.6006 | 2653029.1068 | 1219606.1454 | 2653040.0461 | 1219609.8783 | 2653053.9119 | 1219581.5066 | 2653073.2093 | 1219544.8226
15 | 2653079.0781 | 1219533.4124 | 2653073.2093 | 1219544.8226
16 | 2653133.4375 | 1219845.1206 | 2653132.7315 | 1219849.417 | 2653132.2045 | 1219863.4097 | 2653132.4222 | 1219865.114
17 | 2653132.4222 | 1219865.114 | 2653133.3464 | 1219872.3476 | 2653135.7081 | 1219881.4965
18 | 2653143.4887 | 1219897.4275 | 2653139.9177 | 1219890.6767
19 | 2653143.4887 | 1219897.4275 | 2653145.092 | 1219900.4584 | 2653146.2452 | 1219908.985 | 2653146.0402 | 1219931.1078 | 2653143.6844 | 1219944.2726 | 2653137.6245 | 1219962.6743 | 2653131.2109 | 1219989.2668 | 2653125.7735 | 1220014.6546
20 | 2653139.9177 | 1219890.6767 | 2653139.697 | 1219890.2596 | 2653135.7081 | 1219881.4965 | 2653135.7081 | 1219881.4965
21 | 2653121.1018 | 1220036.4677 | 2653125.7735 | 1220014.6546
22 | 2653086.6561 | 1220168.8797 | 2653090.6715 | 1220161.889 | 2653119.1686 | 1220045.4939 | 2653121.1018 | 1220036.4677
23 | 2653260.6705 | 1220060.3109 | 2653121.1018 | 1220036.4677
24 | 2653290.7465 | 1220024.338 | 2653297.4661 | 1220016.301 | 2653302.795 | 1220010.4918
25 | 2653288.7617 | 1220026.712 | 2653290.7465 | 1220024.338
26 | 2653302.795 | 1220010.4918 | 2653305.1646 | 1220007.9085
27 | 2653288.7617 | 1220026.712 | 2653276.4285 | 1220041.4633
28 | 2653038.0722 | 1220104.2632 | 2653041.3249 | 1220106.2378 | 2653045.1403 | 1220109.7739 | 2653079.1435 | 1220150.257 | 2653080.1646 | 1220152.3229 | 2653082.7809 | 1220157.5939 | 2653086.6561 | 1220168.8797
29 | 2653269.2734 | 1220130.4967 | 2653249.473 | 1220114.0208 | 2653244.7373 | 1220108.2082 | 2653242.7809 | 1220102.1315 | 2653242.4134 | 1220094.8571 | 2653244.5495 | 1220086.7712 | 2653248.1356 | 1220076.8972 | 2653255.2368 | 1220066.81 | 2653260.6705 | 1220060.3109
30 | 2653261.5302 | 1220059.2826 | 2653260.6705 | 1220060.3109
31 | 2653269.2734 | 1220130.4967 | 2653271.6157 | 1220132.441 | 2653301.0451 | 1220102.2078
32 | 2653257.567 | 1220149.0368 | 2653264.4706 | 1220140.66 | 2653271.6157 | 1220132.441 | 2653269.2734 | 1220130.4967
33 | 2653261.5302 | 1220059.2826 | 2653275.3263 | 1220042.7816
34 | 2653038.0722 | 1220104.2632 | 2653032.9656 | 1220101.7273 | 2653027.3711 | 1220100.2989 | 2653022.0784 | 1220099.9182 | 2653016.574 | 1220100.3028 | 2653009.1002 | 1220102.0152 | 2653003.3491 | 1220103.8963
35 | 2653038.0722 | 1220104.2632 | 2653040.4629 | 1220100.7823 | 2653043.1508 | 1220098.0157 | 2653089.7911 | 1220066.797
36 | 2652995.9963 | 1220106.3013 | 2653003.3491 | 1220103.8963
37 | 2653257.567 | 1220149.0368 | 2653264.7567 | 1220154.4821 | 2653297.1322 | 1220165.5561 | 2653300.3558 | 1220166.5189 | 2653317.2537 | 1220171.5397 | 2653323.6131 | 1220171.4188 | 2653330.0405 | 1220169.6308 | 2653335.4033 | 1220165.5651 | 2653337.911 | 1220162.9231
38 | 2653350.7842 | 1220149.3595 | 2653337.911 | 1220162.9231
39 | 2652903.7816 | 1220092.985 | 2652903.5871 | 1220094.3842 | 2652902.3448 | 1220106.1136 | 2652904.0773 | 1220115.2235 | 2652908.6267 | 1220123.2577 | 2652915.7669 | 1220128.3464 | 2652924.0277 | 1220130.2876 | 2652935.9386 | 1220127.8919 | 2652995.9963 | 1220106.3013
40 | 2653305.1646 | 1220007.9085 | 2653317.2412 | 1219994.7433
41 | 2653320.3514 | 1219991.3528 | 2653317.2412 | 1219994.7433
42 | 2653320.3514 | 1219991.3528 | 2653331.3164 | 1219979.3994
43 | 2653344.2102 | 1219965.01 | 2653337.3416 | 1219972.8311 | 2653331.3164 | 1219979.3994
44 | 2652964.0825 | 1219676.2434 | 2652963.8098 | 1219683.0229 | 2652952.2715 | 1219687.79 | 2652931.332 | 1219695.9201 | 2652919.5653 | 1219703.3313
45 | 2652938.9879 | 1219678.8888 | 2652950.6954 | 1219680.705 | 2652958.3084 | 1219679.6164 | 2652964.0825 | 1219676.2434
46 | 2653079.0781 | 1219533.4124 | 2653101.1522 | 1219535.9883 | 2653146.7435 | 1219544.3998 | 2653156.2231 | 1219545.0771
47 | 2652912.2634 | 1220000.8595 | 2652913.5414 | 1220006.4632 | 2652914.1549 | 1220017.6977 | 2652903.7816 | 1220092.985
48 | 2652903.7816 | 1220092.985 | 2652918.8444 | 1220093.6747 | 2652927.436 | 1220093.3875
49 | 2652938.9879 | 1219678.8888 | 2652937.4689 | 1219675.6289 | 2652921.8524 | 1219661.1369 | 2652921.4253 | 1219660.8369
50 | 2652921.4253 | 1219660.8369 | 2652916.5133 | 1219657.3872
51 | 2652916.5133 | 1219657.3872 | 2652916.5133 | 1219657.3872 | 2652909.68 | 1219655.2697 | 2652898.6887 | 1219652.7764
52 | 2652898.6887 | 1219652.7764 | 2652897.3007 | 1219652.4615
53 | 2652874.8274 | 1219648.4674 | 2652880.3503 | 1219648.6165 | 2652897.3007 | 1219652.4615
54 | 2652770.4993 | 1219684.3203 | 2652791.65 | 1219677.1699 | 2652829.5878 | 1219662.0634 | 2652842.1633 | 1219658.4171 | 2652848.5722 | 1219657.907 | 2652853.2139 | 1219658.1594 | 2652859.9938 | 1219662.0219 | 2652864.6365 | 1219657.0267 | 2652869.651 | 1219650.3226 | 2652871.4678 | 1219649.1046 | 2652874.8274 | 1219648.4674
55 | 2652770.4993 | 1219684.3203 | 2652772.6696 | 1219692.0109 | 2652789.0706 | 1219720.7536
56 | 2652874.8274 | 1219648.4674 | 2652875.888 | 1219637.559 | 2652874.73 | 1219629.2995
57 | 2652789.0706 | 1219720.7536 | 2652796.4531 | 1219733.6914 | 2652799.4385 | 1219736.7419 | 2652804.6166 | 1219738.9669 | 2652806.9465 | 1219739.2874
58 | 2652850.4286 | 1219748.8679 | 2652848.3167 | 1219747.4372 | 2652815.5906 | 1219740.4762 | 2652806.9465 | 1219739.2874
59 | 2652850.4286 | 1219748.8679 | 2652856.5093 | 1219743.4407 | 2652867.3594 | 1219735.8323 | 2652877.2977 | 1219728.6096
60 | 2652876.5945 | 1219928.9656 | 2652881.0731 | 1219941.5798 | 2652886.7174 | 1219952.8034 | 2652907.0957 | 1219986.3937 | 2652911.3435 | 1219996.7933 | 2652912.2634 | 1220000.8595
61 | 2652876.5945 | 1219928.9656 | 2652858.6057 | 1219937.3476
62 | 2652912.2634 | 1220000.8595 | 2652923.4223 | 1219990.8969 | 2652929.4166 | 1219979.7989
63 | 2652856.9197 | 1219938.1332 | 2652858.6057 | 1219937.3476
64 | 2653275.3263 | 1220042.7816 | 2653276.4285 | 1220041.4633
65 | 2652823.2545 | 1219941.5671 | 2652834.7361 | 1219938.8561 | 2652844.9295 | 1219940.2139 | 2652852.2433 | 1219940.3122 | 2652856.9197 | 1219938.1332
66 | 2653527.8097 | 1220300.3393 | 2653521.3173 | 1220293.3212 | 2653518.2838 | 1220291.4706 | 2653513.2252 | 1220291.2361 | 2653484.0432 | 1220296.4329 | 2653478.1537 | 1220295.7797 | 2653474.3027 | 1220293.7105 | 2653467.097 | 1220283.3173 | 2653463.672 | 1220279.4397
67 | 2653527.8097 | 1220300.3393 | 2653658.1361 | 1220187.5865
68 | 2653658.1361 | 1220187.5865 | 2653671.8806 | 1220202.8247
69 | 2653676.4964 | 1220207.9421 | 2653671.8806 | 1220202.8247
70 | 2653676.4964 | 1220207.9421 | 2653859.0291 | 1220097.1527
71 | 2653834.3442 | 1220035.1487 | 2653839.8909 | 1220040.1797 | 2653861.1365 | 1220052.746 | 2653863.9505 | 1220056.218 | 2653864.3161 | 1220061.091 | 2653863.0565 | 1220066.9721 | 2653861.1838 | 1220071.0132 | 2653854.1911 | 1220079.066 | 2653852.1154 | 1220082.8941 | 2653851.8848 | 1220085.7382 | 2653853.0751 | 1220089.1955 | 2653856.489 | 1220094.2961 | 2653859.0291 | 1220097.1527
72 | 2653871.3327 | 1220110.9893 | 2653859.0291 | 1220097.1527
73 | 2653670.7254 | 1219877.5098 | 2653834.3442 | 1220035.1487
74 | 2653670.7254 | 1219877.5098 | 2653666.7235 | 1219882.8993 | 2653660.0272 | 1219887.5307 | 2653648.1424 | 1219893.6831 | 2653578.23 | 1219920.4595 | 2653565.1853 | 1219926.5126 | 2653558.0467 | 1219930.5621 | 2653551.9104 | 1219934.5316 | 2653529.1882 | 1219955.5193
75 | 2653529.1882 | 1219955.5193 | 2653522.7284 | 1219961.486 | 2653512.2128 | 1219971.8999
76 | 2652944.977 | 1220084.1676 | 2652933.2954 | 1220093.1916 | 2652927.436 | 1220093.3875
77 | 2652809.3344 | 1219993.232 | 2652810.46 | 1219995.0306
78 | 2652806.6662 | 1219952.0042 | 2652808.0699 | 1219957.142 | 2652803.5649 | 1219979.16 | 2652804.8766 | 1219986.1092 | 2652809.3344 | 1219993.232
79 | 2652806.6662 | 1219952.0042 | 2652823.2545 | 1219941.5671
80 | 2653301.0451 | 1220102.2078 | 2653317.4063 | 1220085.7464
81 | 2653301.0451 | 1220102.2078 | 2653303.6471 | 1220104.8105
82 | 2653317.4063 | 1220085.7464 | 2653337.9246 | 1220065.1023
83 | 2653303.6471 | 1220104.8105 | 2653310.8921 | 1220097.304 | 2653324.3643 | 1220083.902
84 | 2653337.9246 | 1220065.1023 | 2653344.7793 | 1220058.2055 | 2653355.7576 | 1220046.918
85 | 2653350.7842 | 1220149.3595 | 2653359.5649 | 1220157.6056
86 | 2653350.7842 | 1220149.3595 | 2653360.3171 | 1220139.5943
87 | 2653344.2102 | 1219965.01 | 2653355.0191 | 1219952.7103 | 2653355.0191 | 1219952.7103
88 | 2653367.6118 | 1219963.4264 | 2653355.0191 | 1219952.7103
89 | 2653367.6118 | 1219963.4264 | 2653368.4171 | 1219964.1118
90 | 2653439.3823 | 1219951.5876 | 2653421.4787 | 1219971.506
91 | 2653421.4787 | 1219971.506 | 2653407.4157 | 1219986.6451
92 | 2653435.6188 | 1219948.1963 | 2653439.3823 | 1219951.5876
93 | 2653439.3823 | 1219951.5876 | 2653454.9781 | 1219933.5053 | 2653462.3559 | 1219923.5762
94 | 2653373.945 | 1220022.6772 | 2653407.4157 | 1219986.6451
95 | 2653359.5649 | 1220157.6056 | 2653369.8376 | 1220167.2527
96 | 2653373.1974 | 1220126.4001 | 2653360.3171 | 1220139.5943
97 | 2653373.1974 | 1220126.4001 | 2653386.4273 | 1220112.8478
98 | 2653386.4273 | 1220112.8478 | 2653390.0737 | 1220109.1126
99 | 2653390.0737 | 1220109.1126 | 2653400.6213 | 1220098.3079 | 2653400.6213 | 1220098.3079
100 | 2653400.6213 | 1220098.3079 | 2653402.6863 | 1220093.9459 | 2653402.6864 | 1220093.9359
101 | 2653402.6864 | 1220093.9359 | 2653402.7028 | 1220090.4217 | 2653400.7039 | 1220080.6311 | 2653401.129 | 1220077.2329 | 2653403.8497 | 1220074.2109 | 2653409.1851 | 1220069.4053
102 | 2653424.6718 | 1220055.4561 | 2653409.1851 | 1220069.4053
103 | 2653424.6718 | 1220055.4561 | 2653446.1647 | 1220036.097
104 | 2653446.1647 | 1220036.097 | 2653459.6906 | 1220023.9141 | 2653469.3398 | 1220014.3582
105 | 2653469.3398 | 1220014.3582 | 2653489.931 | 1219993.9662
106 | 2653512.2128 | 1219971.8999 | 2653489.931 | 1219993.9662
107 | 2653406.6135 | 1220035.6888 | 2653402.1484 | 1220039.8364
108 | 2653406.6135 | 1220035.6888 | 2653418.4643 | 1220024.6806
109 | 2653371.7649 | 1220035.7444 | 2653385.2269 | 1220049.9737 | 2653388.0968 | 1220050.622 | 2653391.4505 | 1220049.7738 | 2653402.1484 | 1220039.8364
110 | 2653421.9261 | 1220021.4649 | 2653418.4643 | 1220024.6806
111 | 2653368.1422 | 1220039.5143 | 2653371.7649 | 1220035.7444
112 | 2653421.9261 | 1220021.4649 | 2653435.9315 | 1220008.4552
113 | 2653368.1422 | 1220039.5143 | 2653362.2293 | 1220045.6762 | 2653352.7405 | 1220055.2931
114 | 2653368.1422 | 1220039.5143 | 2653365.533 | 1220036.8671
115 | 2653438.6691 | 1220005.9123 | 2653435.9315 | 1220008.4552
116 | 2653365.533 | 1220036.8671 | 2653362.9231 | 1220034.2977 | 2653370.6973 | 1220026.1734 | 2653373.945 | 1220022.6772
117 | 2653365.533 | 1220036.8671 | 2653355.7576 | 1220046.918
118 | 2653474.977 | 1219968.4394 | 2653485.3261 | 1219956.1345
119 | 2653474.977 | 1219968.4394 | 2653461.4151 | 1219984.7833 | 2653453.239 | 1219992.3782
120 | 2653501.4223 | 1219936.9965 | 2653485.3261 | 1219956.1345
121 | 2653438.6691 | 1220005.9123 | 2653453.239 | 1219992.3782
122 | 2653501.4223 | 1219936.9965 | 2653520.2848 | 1219914.5694
123 | 2653521.76 | 1219912.8155 | 2653520.2848 | 1219914.5694
124 | 2653462.3559 | 1219923.5762 | 2653463.4881 | 1219922.0524 | 2653472.1021 | 1219909.4749
125 | 2653483.9588 | 1219890.8605 | 2653477.466 | 1219901.6431 | 2653472.1021 | 1219909.4749
126 | 2653483.9588 | 1219890.8605 | 2653485.1302 | 1219888.9151 | 2653493.7921 | 1219873.2388 | 2653501.9171 | 1219855.8507

## bus_geodata
| x | y | coords
0 | 2653122.5375 | 1219736.6349
1 | 2653101.1767 | 1219744.5201
2 | 2653135.1061 | 1219749.0767
3 | 2653081.3086 | 1219742.0931
4 | 2653122.8654 | 1219776.437
5 | 2653149.81 | 1219756.3031
6 | 2653377.5962 | 1219915.9121
7 | 2653391.0144 | 1219928.2732
8 | 2653090.3685 | 1219769.7549
9 | 2653091.1393 | 1219606.1734
10 | 2653117.706 | 1219799.3746
11 | 2653156.6658 | 1219758.9751
12 | 2653073.2093 | 1219544.8226
13 | 2653133.4375 | 1219845.1206
14 | 2653132.4222 | 1219865.114
15 | 2653215.8131 | 1219755.7236
16 | 2653143.4887 | 1219897.4275
17 | 2653139.9177 | 1219890.6767
18 | 2653125.7735 | 1220014.6546
19 | 2653135.7081 | 1219881.4965
20 | 2653121.1018 | 1220036.4677
21 | 2653290.7465 | 1220024.338
22 | 2653302.795 | 1220010.4918
23 | 2653288.7617 | 1220026.712
24 | 2653086.6561 | 1220168.8797
25 | 2653260.6705 | 1220060.3109
26 | 2653269.2734 | 1220130.4967
27 | 2653261.5302 | 1220059.2826
28 | 2653038.0722 | 1220104.2632
29 | 2653003.3491 | 1220103.8963
30 | 2653089.7911 | 1220066.797
31 | 2653257.567 | 1220149.0368
32 | 2653337.911 | 1220162.9231
33 | 2652995.9963 | 1220106.3013
34 | 2653305.1646 | 1220007.9085
35 | 2653317.2412 | 1219994.7433
36 | 2653320.3514 | 1219991.3528
37 | 2653331.3164 | 1219979.3994
38 | 2652964.0825 | 1219676.2434
39 | 2653079.0781 | 1219533.4124
40 | 2652903.7816 | 1220092.985
41 | 2653156.2231 | 1219545.0771
42 | 2652919.5653 | 1219703.3313
43 | 2652938.9879 | 1219678.8888
44 | 2652921.4253 | 1219660.8369
45 | 2652916.5133 | 1219657.3872
46 | 2652898.6887 | 1219652.7764
47 | 2652897.3007 | 1219652.4615
48 | 2652770.4993 | 1219684.3203
49 | 2652874.8274 | 1219648.4674
50 | 2652789.0706 | 1219720.7536
51 | 2652874.73 | 1219629.2995
52 | 2652806.9465 | 1219739.2874
53 | 2652850.4286 | 1219748.8679
54 | 2652877.2977 | 1219728.6096
55 | 2652876.5945 | 1219928.9656
56 | 2652912.2634 | 1220000.8595
57 | 2652858.6057 | 1219937.3476
58 | 2653275.3263 | 1220042.7816
59 | 2652929.4166 | 1219979.7989
60 | 2652856.9197 | 1219938.1332
61 | 2653463.672 | 1220279.4397
62 | 2653527.8097 | 1220300.3393
63 | 2653658.1361 | 1220187.5865
64 | 2653671.8806 | 1220202.8247
65 | 2653676.4964 | 1220207.9421
66 | 2653859.0291 | 1220097.1527
67 | 2653871.3327 | 1220110.9893
68 | 2653834.3442 | 1220035.1487
69 | 2653670.7254 | 1219877.5098
70 | 2653529.1882 | 1219955.5193
71 | 2652927.436 | 1220093.3875
72 | 2652944.977 | 1220084.1676
73 | 2652809.3344 | 1219993.232
74 | 2652810.46 | 1219995.0306
75 | 2652806.6662 | 1219952.0042
76 | 2652823.2545 | 1219941.5671
77 | 2653276.4285 | 1220041.4633
78 | 2653301.0451 | 1220102.2078
79 | 2653317.4063 | 1220085.7464
80 | 2653303.6471 | 1220104.8105
81 | 2653337.9246 | 1220065.1023
82 | 2653324.3643 | 1220083.902
83 | 2653350.7842 | 1220149.3595
84 | 2653344.2102 | 1219965.01
85 | 2653355.0191 | 1219952.7103
86 | 2653367.6118 | 1219963.4264
87 | 2653421.4787 | 1219971.506
88 | 2653368.4171 | 1219964.1118
89 | 2653439.3823 | 1219951.5876
90 | 2653407.4157 | 1219986.6451
91 | 2653359.5649 | 1220157.6056
92 | 2653360.3171 | 1220139.5943
93 | 2653369.8376 | 1220167.2527
94 | 2653373.1974 | 1220126.4001
95 | 2653386.4273 | 1220112.8478
96 | 2653390.0737 | 1220109.1126
97 | 2653400.6213 | 1220098.3079
98 | 2653402.6864 | 1220093.9359
99 | 2653409.1851 | 1220069.4053
100 | 2653424.6718 | 1220055.4561
101 | 2653446.1647 | 1220036.097
102 | 2653469.3398 | 1220014.3582
103 | 2653489.931 | 1219993.9662
104 | 2653512.2128 | 1219971.8999
105 | 2653406.6135 | 1220035.6888
106 | 2653402.1484 | 1220039.8364
107 | 2653418.4643 | 1220024.6806
108 | 2653371.7649 | 1220035.7444
109 | 2653421.9261 | 1220021.4648
110 | 2653368.1422 | 1220039.5143
111 | 2653435.9315 | 1220008.4552
112 | 2653352.7405 | 1220055.2931
113 | 2653365.533 | 1220036.8671
114 | 2653373.945 | 1220022.6772
115 | 2653355.7575 | 1220046.918
116 | 2653474.977 | 1219968.4394
117 | 2653485.3261 | 1219956.1345
118 | 2653453.239 | 1219992.3782
119 | 2653438.6691 | 1220005.9123
120 | 2653501.4223 | 1219936.9965
121 | 2653520.2848 | 1219914.5694
122 | 2653435.6188 | 1219948.1963
123 | 2653462.3559 | 1219923.5762
124 | 2653472.1021 | 1219909.4749
125 | 2653483.9588 | 1219890.8605
126 | 2653501.9171 | 1219855.8507
127 | 2653521.76 | 1219912.8155
128 | 2653344.2102 | 1219965.01

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97878 | -0.14908 | 0.0017983 | 0.0004507
1 | 0.97838 | -0.15197 | 0.00040758 | 0.00010215
2 | 0.97917 | -0.14629 | 0 | 0
3 | 0.97803 | -0.15451 | 0 | 0
4 | 0.98007 | -0.13982 | 0.0031011 | 0.00077721
5 | 0.97902 | -0.14741 | 0.0010913 | 0.00027349
6 | 0.97277 | -0.19162 | 0.0025891 | 0.00064889
7 | 0.97284 | -0.19112 | 0.0025752 | 0.00064541
8 | 0.97796 | -0.15496 | 0.0014688 | 0.00036812
9 | 0.97584 | -0.1703 | 0.0025602 | 0.00064165
10 | 0.98089 | -0.13402 | 0 | 0
11 | 0.97896 | -0.14782 | 0.0038292 | 0.00095968
12 | 0.97507 | -0.17579 | 0 | 0
13 | 0.98258 | -0.12192 | 0 | 0
14 | 0.98327 | -0.11703 | 0.00070299 | 0.00017619
15 | 0.97881 | -0.14888 | 0.0015686 | 0.00039314
16 | 0.9845 | -0.1083 | 0.0071158 | 0.0017834
17 | 0.98422 | -0.11028 | 0.0007049 | 0.00017666
18 | 0.98731 | -0.088366 | 0.00032633 | 8.1786e-05
19 | 0.98386 | -0.11283 | 0.00015859 | 3.9747e-05
20 | 0.98784 | -0.084641 | 0.00033938 | 8.5058e-05
21 | 0.99767 | -0.016074 | 0.0035864 | 0.00089883
22 | 0.99962 | -0.0026049 | 0.0033458 | 0.00083853
23 | 0.99734 | -0.018313 | 0.0022706 | 0.00056906
24 | 0.98464 | -0.10729 | 0 | 0
25 | 0.99288 | -0.049273 | 0.0024161 | 0.00060552
26 | 0.98646 | -0.094235 | 0 | 0
27 | 0.99301 | -0.048349 | 0.0031292 | 0.00078426
28 | 0.98273 | -0.12089 | 0 | 0
29 | 0.98192 | -0.12663 | 0.00013761 | 3.4488e-05
30 | 0.98267 | -0.12133 | 0.00065602 | 0.00016441
31 | 0.98563 | -0.1001 | 0 | 0
32 | 0.98269 | -0.12092 | 0.0043552 | 0.0010915
33 | 0.98175 | -0.12786 | 0 | 0
34 | 1 | 0 | -0.24158 | -0.060874
35 | 0.99965 | -0.0024179 | 0.0037425 | 0.00093795
36 | 0.99959 | -0.0028688 | 0.0021819 | 0.00054682
37 | 0.99941 | -0.0041052 | 0.0014663 | 0.0003675
38 | 0.97351 | -0.18711 | 0 | 0
39 | 0.97504 | -0.17604 | 0 | 0
40 | 0.97898 | -0.14767 | 0 | 0
41 | 0.97483 | -0.17752 | 0.0018084 | 0.00045323
42 | 0.97344 | -0.18765 | 0.00091848 | 0.00023019
43 | 0.97332 | -0.18848 | 0 | 0
44 | 0.97314 | -0.18981 | 0.00025611 | 6.4187e-05
45 | 0.9731 | -0.19011 | 0.00025893 | 6.4893e-05
46 | 0.97298 | -0.19097 | 0.0011114 | 0.00027854
47 | 0.97297 | -0.19102 | 0.0011154 | 0.00027955
48 | 0.97257 | -0.19396 | 0 | 0
49 | 0.9729 | -0.19156 | 0 | 0
50 | 0.97245 | -0.19481 | 0.00074281 | 0.00018617
51 | 0.97289 | -0.19161 | 0.00025088 | 6.2877e-05
52 | 0.9724 | -0.19515 | 0.00087339 | 0.00021889
53 | 0.97238 | -0.19531 | 0 | 0
54 | 0.97237 | -0.19543 | 0.00032673 | 8.1886e-05
55 | 0.9776 | -0.15753 | 0 | 0
56 | 0.97822 | -0.15311 | 0 | 0
57 | 0.97745 | -0.15861 | 0.00066783 | 0.00016737
58 | 0.99517 | -0.033322 | 0.0031335 | 0.00078533
59 | 0.9782 | -0.15322 | 0.00035693 | 8.9455e-05
60 | 0.97744 | -0.1587 | 0.00045066 | 0.00011295
61 | 0.97006 | -0.21194 | 0.0020465 | 0.00051289
62 | 0.97029 | -0.21029 | 0 | 0
63 | 0.97081 | -0.20654 | 0 | 0
64 | 0.97087 | -0.20609 | 0.0012799 | 0.00032078
65 | 0.9709 | -0.20584 | 0.00019018 | 4.7664e-05
66 | 0.972 | -0.19782 | 0.00051185 | 0.00012828
67 | 0.97193 | -0.19838 | 0.0028536 | 0.00071518
68 | 0.97285 | -0.19171 | 0 | 0
69 | 0.97514 | -0.17511 | 0 | 0
70 | 0.9768 | -0.16314 | 0.0021174 | 0.00053067
71 | 0.97864 | -0.15005 | 0.0086377 | 0.0021648
72 | 0.97861 | -0.15027 | 0.0010045 | 0.00025175
73 | 0.9769 | -0.16257 | 0.0012138 | 0.0003042
74 | 0.97689 | -0.16262 | 0.0024051 | 0.00060278
75 | 0.97713 | -0.16093 | 0 | 0
76 | 0.97723 | -0.16019 | 0.0004945 | 0.00012393
77 | 0.99535 | -0.032107 | 0.0034069 | 0.00085386
78 | 0.9837 | -0.1137 | 0 | 0
79 | 0.98133 | -0.13046 | 0.0079834 | 0.0020008
80 | 0.98362 | -0.11422 | 0.0068423 | 0.0017148
81 | 0.97869 | -0.14917 | 0.004471 | 0.0011205
82 | 0.98333 | -0.11633 | 0.0069472 | 0.0017411
83 | 0.98211 | -0.12509 | 0 | 0
84 | 0.99924 | -0.0052951 | 0 | 0
85 | 0.9991 | -0.0063034 | 0.0020851 | 0.00052258
86 | 0.999 | -0.0069768 | 0.0015288 | 0.00038314
87 | 0.97325 | -0.18813 | 0 | 0
88 | 0.999 | -0.0070037 | 0.0025435 | 0.00063747
89 | 0.97293 | -0.19048 | 0 | 0
90 | 0.97366 | -0.18519 | 0.003201 | 0.00080224
91 | 0.982 | -0.12583 | 0.0034075 | 0.00085401
92 | 0.98172 | -0.12787 | 0.0085121 | 0.0021333
93 | 0.98195 | -0.1262 | 0.0025027 | 0.00062723
94 | 0.98127 | -0.13107 | 0.0032386 | 0.00081167
95 | 0.98084 | -0.13416 | 0.0057215 | 0.0014339
96 | 0.98073 | -0.1349 | 0.0082798 | 0.0020751
97 | 0.98049 | -0.13663 | 0.0015281 | 0.00038298
98 | 0.98042 | -0.13716 | 0.0023172 | 0.00058076
99 | 0.98002 | -0.14002 | 0.0028466 | 0.00071341
100 | 0.97975 | -0.14192 | 0.0051299 | 0.0012857
101 | 0.97886 | -0.14832 | 0.0056255 | 0.0014099
102 | 0.97814 | -0.1535 | 0.0031603 | 0.00079206
103 | 0.97761 | -0.15728 | 0.0014051 | 0.00035215
104 | 0.97711 | -0.1609 | 0.0019696 | 0.00049362
105 | 0.97356 | -0.18589 | 0.0026543 | 0.00066524
106 | 0.97375 | -0.18457 | 0.0028643 | 0.00071787
107 | 0.97314 | -0.18896 | 0.0014852 | 0.00037223
108 | 0.97515 | -0.17453 | 0 | 0
109 | 0.97302 | -0.18978 | 0.0021513 | 0.00053915
110 | 0.97533 | -0.17324 | 0 | 0
111 | 0.97262 | -0.19267 | 0.0010811 | 0.00027094
112 | 0.97511 | -0.1748 | 0.0067049 | 0.0016804
113 | 0.97549 | -0.17207 | 0 | 0
114 | 0.97487 | -0.17655 | 0.0049838 | 0.001249
115 | 0.97656 | -0.16444 | 0.0054726 | 0.0013716
116 | 0.97191 | -0.1978 | 0 | 0
117 | 0.97174 | -0.19903 | 0.0021465 | 0.00053795
118 | 0.97226 | -0.19531 | 0.0027782 | 0.00069629
119 | 0.97255 | -0.19319 | 0.0032113 | 0.00080482
120 | 0.97155 | -0.20039 | 0.0017156 | 0.00042997
121 | 0.9714 | -0.20144 | 0.0016198 | 0.00040595
122 | 0.97291 | -0.19064 | 0.0029573 | 0.00074118
123 | 0.97264 | -0.19254 | 0.001794 | 0.00044962
124 | 0.97255 | -0.19319 | 0.00072178 | 0.0001809
125 | 0.97246 | -0.19385 | 0.0013632 | 0.00034166
126 | 0.97238 | -0.19447 | 0.0014885 | 0.00037306
127 | 0.9714 | -0.20149 | 0.0017883 | 0.00044819
128 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.01215 | 0.0030393 | -0.012145 | -0.0030377 | 4.8509e-06 | 1.5794e-06 | 0.018469 | 0.018469 | 0.018469 | 0.97878 | -0.14908 | 0.97838 | -0.15197 | 6.8403
1 | -0.013948 | -0.00349 | 0.013953 | 0.0034918 | 5.3732e-06 | 1.8258e-06 | 0.021203 | 0.021202 | 0.021203 | 0.97878 | -0.14908 | 0.97917 | -0.14629 | 7.8528
2 | 0.011737 | 0.0029356 | -0.011733 | -0.0029343 | 4.1002e-06 | 1.3181e-06 | 0.017849 | 0.017849 | 0.017849 | 0.97838 | -0.15197 | 0.97803 | -0.15451 | 6.6107
3 | -0.020444 | -0.0051176 | 0.020462 | 0.0051243 | 1.8272e-05 | 6.6458e-06 | 0.031066 | 0.031066 | 0.031066 | 0.97917 | -0.14629 | 0.98007 | -0.13982 | 11.5058
4 | 0.0064906 | 0.0016258 | -0.0064896 | -0.0016256 | 1.0044e-06 | 1.7822e-07 | 0.0098632 | 0.0098633 | 0.0098633 | 0.97917 | -0.14629 | 0.97902 | -0.14741 | 3.6531
5 | 0.0014689 | 0.00036779 | -0.0014688 | -0.00036812 | 9.1129e-08 | -3.3187e-07 | 0.0022347 | 0.0022349 | 0.0022349 | 0.97803 | -0.15451 | 0.97796 | -0.15496 | 0.82773
6 | 0.010264 | 0.0025665 | -0.010242 | -0.0025597 | 2.2299e-05 | 6.7414e-06 | 0.015614 | 0.015615 | 0.015615 | 0.97803 | -0.15451 | 0.97584 | -0.1703 | 5.7833
7 | -0.023563 | -0.0059015 | 0.023582 | 0.0059084 | 1.8896e-05 | 6.9693e-06 | 0.035774 | 0.035774 | 0.035774 | 0.98007 | -0.13982 | 0.98089 | -0.13402 | 13.2496
8 | 0.0053983 | 0.0013521 | -0.005398 | -0.0013521 | 3.0908e-07 | 2.636e-08 | 0.0082047 | 0.0082047 | 0.0082047 | 0.97902 | -0.14741 | 0.97896 | -0.14782 | 3.0388
9 | -0.0025891 | -0.00064889 | 0.0025893 | 0.00064873 | 1.7829e-07 | -1.5759e-07 | 0.0039605 | 0.0039604 | 0.0039605 | 0.97277 | -0.19162 | 0.97284 | -0.19112 | 1.4668
10 | -0.0051645 | -0.0012941 | 0.0051666 | 0.0012943 | 2.1375e-06 | 1.402e-07 | 0.0078993 | 0.0078991 | 0.0078993 | 0.97284 | -0.19112 | 0.97325 | -0.18813 | 2.9257
11 | 0.0076816 | 0.0019181 | -0.0076758 | -0.0019167 | 5.8004e-06 | 1.3849e-06 | 0.011711 | 0.011711 | 0.011711 | 0.97584 | -0.1703 | 0.97507 | -0.17579 | 4.3375
12 | -0.023582 | -0.0059084 | 0.023622 | 0.005923 | 3.9553e-05 | 1.4586e-05 | 0.035774 | 0.035774 | 0.035774 | 0.98089 | -0.13402 | 0.98258 | -0.12192 | 13.2495
13 | 0.0015689 | 0.00039241 | -0.0015686 | -0.00039314 | 2.3036e-07 | -7.2757e-07 | 0.0023844 | 0.0023847 | 0.0023847 | 0.97896 | -0.14782 | 0.97881 | -0.14888 | 0.88322
14 | 0.005867 | 0.0014644 | -0.0058579 | -0.0014632 | 9.119e-06 | 1.2361e-06 | 0.0089512 | 0.008952 | 0.008952 | 0.97507 | -0.17579 | 0.97351 | -0.18711 | 3.3156
15 | 0.0018088 | 0.00045226 | -0.0018088 | -0.0004524 | 6.0963e-08 | -1.3652e-07 | 0.00276 | 0.0027601 | 0.0027601 | 0.97507 | -0.17579 | 0.97504 | -0.17604 | 1.0222
16 | -0.023622 | -0.005923 | 0.023638 | 0.0059289 | 1.6031e-05 | 5.9113e-06 | 0.035774 | 0.035773 | 0.035774 | 0.98258 | -0.12192 | 0.98327 | -0.11703 | 13.2495
17 | -0.024341 | -0.0061051 | 0.024355 | 0.0061104 | 1.4176e-05 | 5.2397e-06 | 0.036837 | 0.036837 | 0.036837 | 0.98327 | -0.11703 | 0.98386 | -0.11283 | 13.6434
18 | 0.025234 | 0.0063325 | -0.025227 | -0.00633 | 6.9333e-06 | 2.5696e-06 | 0.038143 | 0.038143 | 0.038143 | 0.9845 | -0.1083 | 0.98422 | -0.11028 | 14.1269
19 | -0.03235 | -0.0081159 | 0.032439 | 0.0081474 | 8.9684e-05 | 3.1427e-05 | 0.048898 | 0.048897 | 0.048898 | 0.9845 | -0.1083 | 0.98731 | -0.088366 | 9.0552
20 | 0.024522 | 0.0061533 | -0.024513 | -0.0061501 | 8.6641e-06 | 3.204e-06 | 0.037077 | 0.037077 | 0.037077 | 0.98422 | -0.11028 | 0.98386 | -0.11283 | 13.7323
21 | -0.032766 | -0.0082291 | 0.032783 | 0.0082351 | 1.6977e-05 | 5.9588e-06 | 0.049389 | 0.049388 | 0.049389 | 0.98731 | -0.088366 | 0.98784 | -0.084641 | 9.146
22 | 0.016176 | 0.0040641 | -0.016125 | -0.0040463 | 5.082e-05 | 1.7796e-05 | 0.02437 | 0.024371 | 0.024371 | 0.98784 | -0.084641 | 0.98464 | -0.10729 | 9.0262
23 | -0.049298 | -0.012384 | 0.049542 | 0.012474 | 0.00024367 | 9.0076e-05 | 0.07427 | 0.074269 | 0.07427 | 0.98784 | -0.084641 | 0.99288 | -0.049273 | 13.7537
24 | -0.22337 | -0.056444 | 0.2238 | 0.056606 | 0.00042428 | 0.00016246 | 0.33332 | 0.33332 | 0.33332 | 0.99767 | -0.016074 | 0.99962 | -0.0026049 | 41.1511
25 | 0.21979 | 0.055545 | -0.21972 | -0.055519 | 6.9235e-05 | 2.6508e-05 | 0.32797 | 0.32797 | 0.32797 | 0.99767 | -0.016074 | 0.99734 | -0.018313 | 40.4907
26 | -0.22714 | -0.057445 | 0.22723 | 0.057477 | 8.3449e-05 | 3.1958e-05 | 0.3383 | 0.3383 | 0.3383 | 0.99962 | -0.0026049 | 1 | 0 | 41.7659
27 | 0.21745 | 0.054949 | -0.21703 | -0.054788 | 0.00042136 | 0.00016131 | 0.32459 | 0.32459 | 0.32459 | 0.99734 | -0.018313 | 0.99535 | -0.032107 | 40.0725
28 | 0.016125 | 0.0040463 | -0.016095 | -0.0040357 | 3.039e-05 | 1.0648e-05 | 0.024371 | 0.024371 | 0.024371 | 0.98464 | -0.10729 | 0.98273 | -0.12089 | 9.0264
29 | 0.15489 | 0.039091 | -0.15392 | -0.038721 | 0.00097145 | 0.0003703 | 0.23223 | 0.23223 | 0.23223 | 0.99288 | -0.049273 | 0.98646 | -0.094235 | 28.6706
30 | -0.20685 | -0.052171 | 0.20688 | 0.052181 | 2.6812e-05 | 1.026e-05 | 0.31012 | 0.31012 | 0.31012 | 0.99288 | -0.049273 | 0.99301 | -0.048349 | 38.2865
31 | 0.084445 | 0.021269 | -0.084215 | -0.021182 | 0.00022914 | 8.6978e-05 | 0.12742 | 0.12742 | 0.12742 | 0.98646 | -0.094235 | 0.9837 | -0.1137 | 23.5959
32 | 0.069476 | 0.017452 | -0.069419 | -0.017431 | 5.6647e-05 | 2.0839e-05 | 0.10481 | 0.10481 | 0.10481 | 0.98646 | -0.094235 | 0.98563 | -0.1001 | 12.9401
33 | -0.21001 | -0.052965 | 0.21045 | 0.053135 | 0.00044337 | 0.00016969 | 0.31481 | 0.31481 | 0.31481 | 0.99301 | -0.048349 | 0.99517 | -0.033322 | 38.8654
34 | 0.015439 | 0.003872 | -0.015427 | -0.0038678 | 1.2284e-05 | 4.2685e-06 | 0.023378 | 0.023378 | 0.023378 | 0.98273 | -0.12089 | 0.98192 | -0.12663 | 8.6586
35 | 0.00065606 | 0.00016362 | -0.00065602 | -0.00016441 | 3.9524e-08 | -7.9822e-07 | 0.0009931 | 0.00099339 | 0.00099339 | 0.98273 | -0.12089 | 0.98267 | -0.12133 | 0.36792
36 | 0.015289 | 0.0038333 | -0.015286 | -0.0038324 | 2.5915e-06 | 8.9889e-07 | 0.02317 | 0.02317 | 0.02317 | 0.98192 | -0.12663 | 0.98175 | -0.12786 | 8.5814
37 | 0.069419 | 0.017431 | -0.069219 | -0.017358 | 0.00020025 | 7.368e-05 | 0.10481 | 0.10482 | 0.10482 | 0.98563 | -0.1001 | 0.98269 | -0.12092 | 12.9403
38 | 0.064864 | 0.016266 | -0.064826 | -0.016252 | 3.7525e-05 | 1.3722e-05 | 0.098221 | 0.098222 | 0.098222 | 0.98269 | -0.12092 | 0.98211 | -0.12509 | 12.1261
39 | 0.015286 | 0.0038324 | -0.015245 | -0.0038179 | 4.1853e-05 | 1.4522e-05 | 0.02317 | 0.02317 | 0.02317 | 0.98175 | -0.12786 | 0.97898 | -0.14767 | 8.5816
40 | 0.013557 | 0.0033976 | -0.013552 | -0.0033961 | 4.5365e-06 | 1.5105e-06 | 0.020173 | 0.020173 | 0.020173 | 1 | 0 | 0.99965 | -0.0024179 | 7.4714
41 | 0.0098098 | 0.0024581 | -0.0098091 | -0.002458 | 6.1214e-07 | 1.7512e-07 | 0.014602 | 0.014602 | 0.014602 | 0.99965 | -0.0024179 | 0.99959 | -0.0028688 | 5.4081
42 | 0.0076273 | 0.0019111 | -0.007626 | -0.0019109 | 1.3049e-06 | 2.8927e-07 | 0.011354 | 0.011354 | 0.011354 | 0.99959 | -0.0028688 | 0.99941 | -0.0041052 | 4.2052
43 | 0.0061597 | 0.0015434 | -0.0061586 | -0.0015432 | 1.0141e-06 | 1.3687e-07 | 0.0091709 | 0.009171 | 0.009171 | 0.99941 | -0.0041052 | 0.99924 | -0.0052951 | 3.3967
44 | 0.00091854 | 0.00022953 | -0.00091848 | -0.00023019 | 6.8285e-08 | -6.6404e-07 | 0.0014038 | 0.001404 | 0.001404 | 0.97351 | -0.18711 | 0.97344 | -0.18765 | 0.52
45 | 0.0049393 | 0.0012337 | -0.0049384 | -0.0012336 | 9.2991e-07 | 3.2524e-08 | 0.0075483 | 0.0075484 | 0.0075484 | 0.97351 | -0.18711 | 0.97332 | -0.18848 | 2.7957
46 | 0.0018088 | 0.0004524 | -0.0018084 | -0.00045323 | 3.7125e-07 | -8.3097e-07 | 0.0027601 | 0.0027604 | 0.0027604 | 0.97504 | -0.17604 | 0.97483 | -0.17752 | 1.0224
47 | 0.0055991 | 0.0014006 | -0.0055949 | -0.0014002 | 4.2029e-06 | 4.4796e-07 | 0.0085096 | 0.00851 | 0.00851 | 0.97898 | -0.14767 | 0.97822 | -0.15311 | 3.1519
48 | 0.0096454 | 0.0024172 | -0.0096423 | -0.0024163 | 3.1753e-06 | 9.2371e-07 | 0.014661 | 0.014661 | 0.014661 | 0.97898 | -0.14767 | 0.97864 | -0.15005 | 5.4299
49 | 0.0049384 | 0.0012336 | -0.0049375 | -0.0012336 | 9.0392e-07 | 3.1746e-08 | 0.0075484 | 0.0075485 | 0.0075485 | 0.97332 | -0.18848 | 0.97314 | -0.18981 | 2.7957
50 | 0.0046814 | 0.0011694 | -0.0046812 | -0.0011694 | 1.9185e-07 | -7.8212e-10 | 0.0071569 | 0.0071569 | 0.0071569 | 0.97314 | -0.18981 | 0.9731 | -0.19011 | 2.6507
51 | 0.0044223 | 0.0011045 | -0.0044218 | -0.0011045 | 5.2554e-07 | -2.6727e-08 | 0.006761 | 0.0067611 | 0.0067611 | 0.9731 | -0.19011 | 0.97298 | -0.19097 | 2.5041
52 | 0.0033104 | 0.000826 | -0.0033103 | -0.00082601 | 2.2751e-08 | -8.926e-09 | 0.0050614 | 0.0050614 | 0.0050614 | 0.97298 | -0.19097 | 0.97297 | -0.19102 | 1.8746
53 | 0.0021949 | 0.00054646 | -0.0021948 | -0.00054668 | 1.6094e-07 | -2.2256e-07 | 0.0033555 | 0.0033556 | 0.0033556 | 0.97297 | -0.19102 | 0.9729 | -0.19156 | 1.2428
54 | -0.0019432 | -0.00048524 | 0.0019439 | 0.00048405 | 6.3908e-07 | -1.1934e-06 | 0.0029725 | 0.002972 | 0.0029725 | 0.97257 | -0.19396 | 0.9729 | -0.19156 | 1.1009
55 | 0.0019432 | 0.00048524 | -0.001943 | -0.00048566 | 2.2653e-07 | -4.2264e-07 | 0.0029725 | 0.0029727 | 0.0029727 | 0.97257 | -0.19396 | 0.97245 | -0.19481 | 1.101
56 | 0.00025088 | 6.2638e-05 | -0.00025088 | -6.2877e-05 | 1.7728e-09 | -2.3898e-07 | 0.00038363 | 0.00038372 | 0.00038372 | 0.9729 | -0.19156 | 0.97289 | -0.19161 | 0.14212
57 | 0.0012002 | 0.0002995 | -0.0012001 | -0.00029981 | 5.7118e-08 | -3.1487e-07 | 0.001836 | 0.0018361 | 0.0018361 | 0.97245 | -0.19481 | 0.9724 | -0.19515 | 0.68005
58 | 0.00032674 | 8.0918e-05 | -0.00032674 | -8.1471e-05 | 6.9716e-09 | -5.5225e-07 | 0.00049965 | 0.00049985 | 0.00049985 | 0.9724 | -0.19515 | 0.97238 | -0.19531 | 0.18513
59 | 0.00032674 | 8.1471e-05 | -0.00032673 | -8.1886e-05 | 5.2537e-09 | -4.1586e-07 | 0.00049985 | 0.0005 | 0.0005 | 0.97238 | -0.19531 | 0.97237 | -0.19543 | 0.18518
60 | -0.0052348 | -0.0013108 | 0.005238 | 0.0013111 | 3.1927e-06 | 2.1673e-07 | 0.0079675 | 0.0079672 | 0.0079675 | 0.9776 | -0.15753 | 0.97822 | -0.15311 | 2.9509
61 | 0.0052348 | 0.0013108 | -0.005234 | -0.0013108 | 7.8615e-07 | 5.3574e-08 | 0.0079675 | 0.0079676 | 0.0079676 | 0.9776 | -0.15753 | 0.97745 | -0.15861 | 2.951
62 | 0.00035693 | 8.9111e-05 | -0.00035693 | -8.9455e-05 | 5.0654e-09 | -3.4382e-07 | 0.00054283 | 0.00054295 | 0.00054295 | 0.97822 | -0.15311 | 0.9782 | -0.15322 | 0.20109
63 | 0.0045662 | 0.0011434 | -0.0045661 | -0.0011434 | 5.6079e-08 | -1.7453e-09 | 0.006951 | 0.006951 | 0.006951 | 0.97745 | -0.15861 | 0.97744 | -0.1587 | 2.5744
64 | -0.21358 | -0.05392 | 0.21362 | 0.053934 | 3.6485e-05 | 1.3966e-05 | 0.31949 | 0.31949 | 0.31949 | 0.99517 | -0.033322 | 0.99535 | -0.032107 | 39.4438
65 | 0.0041155 | 0.0010305 | -0.0041146 | -0.0010306 | 8.4631e-07 | -1.0751e-07 | 0.0062649 | 0.0062651 | 0.0062651 | 0.97744 | -0.1587 | 0.97723 | -0.16019 | 2.3204
66 | -0.0020465 | -0.00051289 | 0.0020469 | 0.00051214 | 4.6689e-07 | -7.5812e-07 | 0.0031392 | 0.0031388 | 0.0031392 | 0.97006 | -0.21194 | 0.97029 | -0.21029 | 1.1627
67 | -0.0020469 | -0.00051214 | 0.002048 | 0.00051042 | 1.0575e-06 | -1.7196e-06 | 0.0031388 | 0.0031381 | 0.0031388 | 0.97029 | -0.21029 | 0.97081 | -0.20654 | 1.1625
68 | -0.002048 | -0.00051042 | 0.0020481 | 0.00051021 | 1.2609e-07 | -2.0525e-07 | 0.0031381 | 0.003138 | 0.0031381 | 0.97081 | -0.20654 | 0.97087 | -0.20609 | 1.1622
69 | -0.003328 | -0.00083099 | 0.0033282 | 0.00083095 | 1.1184e-07 | -4.221e-08 | 0.0050997 | 0.0050996 | 0.0050997 | 0.97087 | -0.20609 | 0.9709 | -0.20584 | 1.8888
70 | -0.0035183 | -0.00087861 | 0.0035222 | 0.00087746 | 3.8718e-06 | -1.1545e-06 | 0.0053911 | 0.0053902 | 0.0053911 | 0.9709 | -0.20584 | 0.972 | -0.19782 | 1.9967
71 | -0.0068879 | -0.0017208 | 0.0068937 | 0.001722 | 5.7899e-06 | 1.1912e-06 | 0.010542 | 0.010542 | 0.010542 | 0.972 | -0.19782 | 0.97285 | -0.19171 | 3.9046
72 | 0.0028538 | 0.00071503 | -0.0028536 | -0.00071518 | 2.2052e-07 | -1.4467e-07 | 0.0043687 | 0.0043688 | 0.0043688 | 0.972 | -0.19782 | 0.97193 | -0.19838 | 1.6181
73 | -0.0068937 | -0.001722 | 0.0069094 | 0.0017252 | 1.5755e-05 | 3.2318e-06 | 0.010542 | 0.010541 | 0.010542 | 0.97285 | -0.19171 | 0.97514 | -0.17511 | 3.9045
74 | -0.0069094 | -0.0017252 | 0.0069208 | 0.0017275 | 1.1365e-05 | 2.3228e-06 | 0.010541 | 0.01054 | 0.010541 | 0.97514 | -0.17511 | 0.9768 | -0.16314 | 3.9041
75 | -0.0090382 | -0.0022582 | 0.009041 | 0.002259 | 2.7899e-06 | 7.776e-07 | 0.013766 | 0.013766 | 0.013766 | 0.9768 | -0.16314 | 0.97711 | -0.1609 | 5.0985
76 | 0.0010045 | 0.0002515 | -0.0010045 | -0.00025175 | 3.0021e-08 | -2.4758e-07 | 0.0015273 | 0.0015274 | 0.0015274 | 0.97864 | -0.15005 | 0.97861 | -0.15027 | 0.56569
77 | 0.0024052 | 0.00060276 | -0.0024051 | -0.00060278 | 1.7769e-08 | -1.973e-08 | 0.0036635 | 0.0036635 | 0.0036635 | 0.9769 | -0.16257 | 0.97689 | -0.16262 | 1.3569
78 | -0.0036189 | -0.00090697 | 0.0036198 | 0.00090674 | 8.2051e-07 | -2.2636e-07 | 0.0055124 | 0.0055122 | 0.0055124 | 0.9769 | -0.16257 | 0.97713 | -0.16093 | 2.0416
79 | -0.0036198 | -0.00090674 | 0.0036201 | 0.00090664 | 3.7158e-07 | -1.026e-07 | 0.0055122 | 0.0055121 | 0.0055122 | 0.97713 | -0.16093 | 0.97723 | -0.16019 | 2.0415
80 | 0.070423 | 0.017725 | -0.070259 | -0.017662 | 0.00016443 | 6.2949e-05 | 0.10655 | 0.10655 | 0.10655 | 0.9837 | -0.1137 | 0.98133 | -0.13046 | 39.4646
81 | 0.013793 | 0.0034567 | -0.013792 | -0.0034564 | 9.9964e-07 | 3.3776e-07 | 0.020864 | 0.020864 | 0.020864 | 0.9837 | -0.1137 | 0.98362 | -0.11422 | 7.7273
82 | 0.062275 | 0.015661 | -0.062113 | -0.015599 | 0.00016202 | 6.1948e-05 | 0.094449 | 0.094449 | 0.094449 | 0.98133 | -0.13046 | 0.97869 | -0.14917 | 34.9811
83 | 0.0069493 | 0.0017415 | -0.0069472 | -0.0017411 | 2.03e-06 | 4.0725e-07 | 0.010513 | 0.010513 | 0.010513 | 0.98362 | -0.11422 | 0.98333 | -0.11633 | 3.8937
84 | 0.057642 | 0.014479 | -0.05752 | -0.014432 | 0.0001221 | 4.6643e-05 | 0.087651 | 0.087651 | 0.087651 | 0.97869 | -0.14917 | 0.97656 | -0.16444 | 32.4635
85 | 0.0059109 | 0.0014812 | -0.0059103 | -0.0014811 | 6.0286e-07 | 7.946e-08 | 0.0089557 | 0.0089558 | 0.0089558 | 0.98211 | -0.12509 | 0.982 | -0.12583 | 3.3169
86 | 0.058915 | 0.014771 | -0.058893 | -0.014763 | 2.2619e-05 | 8.1817e-06 | 0.089266 | 0.089266 | 0.089266 | 0.98211 | -0.12509 | 0.98172 | -0.12787 | 11.0205
87 | 0.0061586 | 0.0015432 | -0.0061578 | -0.0015431 | 8.5937e-07 | 1.1606e-07 | 0.009171 | 0.0091711 | 0.0091711 | 0.99924 | -0.0052951 | 0.9991 | -0.0063034 | 3.3967
88 | 0.0040727 | 0.0010205 | -0.0040723 | -0.0010206 | 3.7962e-07 | -7.0512e-08 | 0.0060656 | 0.0060657 | 0.0060657 | 0.9991 | -0.0063034 | 0.999 | -0.0069768 | 2.2465
89 | 0.0025435 | 0.00063746 | -0.0025435 | -0.00063747 | 9.4717e-09 | -1.0203e-08 | 0.0037886 | 0.0037886 | 0.0037886 | 0.999 | -0.0069768 | 0.999 | -0.0070037 | 1.4032
90 | 0.0083299 | 0.0020865 | -0.0083272 | -0.0020858 | 2.7073e-06 | 7.0895e-07 | 0.012735 | 0.012735 | 0.012735 | 0.97325 | -0.18813 | 0.97293 | -0.19048 | 4.7168
91 | -0.013496 | -0.0033808 | 0.013502 | 0.0033826 | 5.4898e-06 | 1.8546e-06 | 0.020634 | 0.020634 | 0.020634 | 0.97325 | -0.18813 | 0.97366 | -0.18519 | 7.6423
92 | 0.0029574 | 0.00074114 | -0.0029573 | -0.00074118 | 6.4571e-08 | -3.7977e-08 | 0.0045231 | 0.0045231 | 0.0045231 | 0.97293 | -0.19048 | 0.97291 | -0.19064 | 1.6752
93 | 0.0053698 | 0.0013447 | -0.0053682 | -0.0013445 | 1.5255e-06 | 1.367e-07 | 0.0082122 | 0.0082124 | 0.0082124 | 0.97293 | -0.19048 | 0.97264 | -0.19254 | 3.0416
94 | -0.016703 | -0.0041849 | 0.016723 | 0.004192 | 1.9995e-05 | 7.0782e-06 | 0.025526 | 0.025526 | 0.025526 | 0.97366 | -0.18519 | 0.97487 | -0.17655 | 9.4541
95 | 0.0025028 | 0.0006271 | -0.0025027 | -0.00062723 | 1.2647e-07 | -1.2963e-07 | 0.0037924 | 0.0037925 | 0.0037925 | 0.982 | -0.12583 | 0.98195 | -0.1262 | 1.4046
96 | 0.050381 | 0.01263 | -0.050358 | -0.012622 | 2.2365e-05 | 7.903e-06 | 0.076364 | 0.076364 | 0.076364 | 0.98172 | -0.12787 | 0.98127 | -0.13107 | 9.4277
97 | 0.04712 | 0.01181 | -0.047099 | -0.011803 | 2.0113e-05 | 7.0182e-06 | 0.071453 | 0.071454 | 0.071454 | 0.98127 | -0.13107 | 0.98084 | -0.13416 | 8.8214
98 | 0.041378 | 0.010369 | -0.041374 | -0.010368 | 4.2785e-06 | 1.4479e-06 | 0.062774 | 0.062774 | 0.062774 | 0.98084 | -0.13416 | 0.98073 | -0.1349 | 7.7498
99 | 0.033094 | 0.0082925 | -0.033086 | -0.00829 | 7.9182e-06 | 2.474e-06 | 0.050211 | 0.050211 | 0.050211 | 0.98073 | -0.1349 | 0.98049 | -0.13663 | 6.1989
100 | 0.031558 | 0.0079071 | -0.031556 | -0.0079064 | 2.3072e-06 | 7.0443e-07 | 0.047892 | 0.047892 | 0.047892 | 0.98049 | -0.13663 | 0.98042 | -0.13716 | 5.9126
101 | 0.029238 | 0.0073256 | -0.029227 | -0.0073222 | 1.1542e-05 | 3.3735e-06 | 0.044375 | 0.044376 | 0.044376 | 0.98042 | -0.13716 | 0.98002 | -0.14002 | 5.4785
102 | 0.02638 | 0.0066088 | -0.026373 | -0.0066069 | 6.9551e-06 | 1.8874e-06 | 0.040054 | 0.040054 | 0.040054 | 0.98002 | -0.14002 | 0.97975 | -0.14192 | 4.9449
103 | 0.021243 | 0.0053213 | -0.021225 | -0.0053144 | 1.8788e-05 | 6.8622e-06 | 0.032263 | 0.032263 | 0.032263 | 0.97975 | -0.14192 | 0.97886 | -0.14832 | 11.9492
104 | 0.015599 | 0.0039045 | -0.015588 | -0.0039006 | 1.1151e-05 | 3.8895e-06 | 0.023711 | 0.023711 | 0.023711 | 0.97886 | -0.14832 | 0.97814 | -0.1535 | 8.782
105 | 0.012428 | 0.0031086 | -0.012421 | -0.0031064 | 6.4621e-06 | 2.1219e-06 | 0.018904 | 0.018904 | 0.018904 | 0.97814 | -0.1535 | 0.97761 | -0.15728 | 7.0014
106 | 0.011016 | 0.0027543 | -0.011011 | -0.0027526 | 5.5e-06 | 1.7224e-06 | 0.016765 | 0.016765 | 0.016765 | 0.97761 | -0.15728 | 0.97711 | -0.1609 | 6.2093
107 | -0.020656 | -0.005178 | 0.02066 | 0.0051794 | 3.7904e-06 | 1.3821e-06 | 0.031571 | 0.031571 | 0.031571 | 0.97356 | -0.18589 | 0.97375 | -0.18457 | 11.6931
108 | 0.018002 | 0.0045128 | -0.017994 | -0.0045101 | 7.6409e-06 | 2.7378e-06 | 0.027514 | 0.027514 | 0.027514 | 0.97356 | -0.18589 | 0.97314 | -0.18896 | 10.1905
109 | -0.023524 | -0.0058973 | 0.023557 | 0.0059094 | 3.2732e-05 | 1.2084e-05 | 0.035948 | 0.035948 | 0.035948 | 0.97375 | -0.18457 | 0.97515 | -0.17453 | 13.3142
110 | 0.016509 | 0.0041378 | -0.016507 | -0.0041372 | 1.8788e-06 | 6.6392e-07 | 0.025243 | 0.025243 | 0.025243 | 0.97314 | -0.18896 | 0.97302 | -0.18978 | 9.3494
111 | -0.023557 | -0.0059094 | 0.023561 | 0.0059109 | 4.2109e-06 | 1.5544e-06 | 0.035948 | 0.035948 | 0.035948 | 0.97515 | -0.17453 | 0.97533 | -0.17324 | 13.3142
112 | 0.014356 | 0.003598 | -0.01435 | -0.003596 | 5.7489e-06 | 1.9738e-06 | 0.021954 | 0.021954 | 0.021954 | 0.97302 | -0.18978 | 0.97262 | -0.19267 | 8.131
113 | 0.0067063 | 0.0016807 | -0.0067049 | -0.0016804 | 1.4404e-06 | 2.7887e-07 | 0.010232 | 0.010232 | 0.010232 | 0.97533 | -0.17324 | 0.97511 | -0.1748 | 3.7895
114 | -0.030267 | -0.0075916 | 0.030272 | 0.0075935 | 4.9396e-06 | 1.8535e-06 | 0.04618 | 0.04618 | 0.04618 | 0.97533 | -0.17324 | 0.97549 | -0.17207 | 17.1036
115 | 0.013269 | 0.0033251 | -0.013268 | -0.0033248 | 9.6076e-07 | 3.2316e-07 | 0.0203 | 0.0203 | 0.0203 | 0.97262 | -0.19267 | 0.97255 | -0.19319 | 7.5184
116 | 0.02172 | 0.005446 | -0.021707 | -0.005441 | 1.3481e-05 | 4.9393e-06 | 0.033133 | 0.033133 | 0.033133 | 0.97549 | -0.17207 | 0.97487 | -0.17655 | 12.2715
117 | -0.051992 | -0.013039 | 0.052047 | 0.01306 | 5.5035e-05 | 2.0992e-05 | 0.079313 | 0.079313 | 0.079313 | 0.97549 | -0.17207 | 0.97656 | -0.16444 | 29.375
118 | 0.0072728 | 0.0018222 | -0.0072716 | -0.0018219 | 1.2439e-06 | 2.792e-07 | 0.011135 | 0.011135 | 0.011135 | 0.97191 | -0.1978 | 0.97174 | -0.19903 | 4.124
119 | -0.0072728 | -0.0018222 | 0.0072753 | 0.0018228 | 2.5063e-06 | 5.6235e-07 | 0.011135 | 0.011135 | 0.011135 | 0.97191 | -0.1978 | 0.97226 | -0.19531 | 4.1239
120 | 0.0051251 | 0.001284 | -0.0051242 | -0.0012839 | 9.6107e-07 | 5.991e-08 | 0.0078479 | 0.007848 | 0.007848 | 0.97174 | -0.19903 | 0.97155 | -0.20039 | 2.9067
121 | -0.010054 | -0.0025191 | 0.010056 | 0.0025199 | 2.9377e-06 | 8.8321e-07 | 0.015387 | 0.015386 | 0.015387 | 0.97226 | -0.19531 | 0.97255 | -0.19319 | 5.6987
122 | 0.0034086 | 0.00085395 | -0.0034081 | -0.00085412 | 4.9836e-07 | -1.7116e-07 | 0.0052204 | 0.0052205 | 0.0052205 | 0.97155 | -0.20039 | 0.9714 | -0.20144 | 1.9335
123 | 0.0017883 | 0.00044817 | -0.0017883 | -0.00044819 | 1.0732e-08 | -2.4244e-08 | 0.0027394 | 0.0027394 | 0.0027394 | 0.9714 | -0.20144 | 0.9714 | -0.20149 | 1.0146
124 | 0.0035742 | 0.00089491 | -0.0035739 | -0.000895 | 3.1981e-07 | -8.974e-08 | 0.0054678 | 0.0054679 | 0.0054679 | 0.97264 | -0.19254 | 0.97255 | -0.19319 | 2.0251
125 | 0.0028521 | 0.0007141 | -0.0028519 | -0.00071428 | 2.6233e-07 | -1.7306e-07 | 0.0043635 | 0.0043636 | 0.0043636 | 0.97255 | -0.19319 | 0.97246 | -0.19385 | 1.6162
126 | 0.0014887 | 0.00037262 | -0.0014885 | -0.00037306 | 1.2747e-07 | -4.3943e-07 | 0.0022777 | 0.0022779 | 0.0022779 | 0.97246 | -0.19385 | 0.97238 | -0.19447 | 0.84366

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24463 | 0.061637

## res_load
| p_mw | q_mvar
0 | 0.0017983 | 0.0004507
1 | 0.00040758 | 0.00010215
2 | 0.0031011 | 0.00077721
3 | 0.0010913 | 0.00027349
4 | 0.0025891 | 0.00064889
5 | 0.0025752 | 0.00064541
6 | 0.0014688 | 0.00036812
7 | 0.0025602 | 0.00064165
8 | 0.0038292 | 0.00095968
9 | 0.00070299 | 0.00017619
10 | 0.0015686 | 0.00039314
11 | 0.0071158 | 0.0017834
12 | 0.0007049 | 0.00017666
13 | 0.00032633 | 8.1786e-05
14 | 0.00015859 | 3.9747e-05
15 | 0.00033938 | 8.5058e-05
16 | 0.0035864 | 0.00089883
17 | 0.0033458 | 0.00083853
18 | 0.0022706 | 0.00056906
19 | 0.0024161 | 0.00060552
20 | 0.0031292 | 0.00078426
21 | 0.00013761 | 3.4488e-05
22 | 0.00065602 | 0.00016441
23 | 0.0043552 | 0.0010915
24 | 0.003044 | 0.00076291
25 | 0.0037425 | 0.00093795
26 | 0.0021819 | 0.00054682
27 | 0.0014663 | 0.0003675
28 | 0.0018084 | 0.00045323
29 | 0.00091848 | 0.00023019
30 | 0.00025611 | 6.4187e-05
31 | 0.00025893 | 6.4893e-05
32 | 0.0011114 | 0.00027854
33 | 0.0011154 | 0.00027955
34 | 0.00074281 | 0.00018617
35 | 0.00025088 | 6.2877e-05
36 | 0.00087339 | 0.00021889
37 | 0.00032673 | 8.1886e-05
38 | 0.00066783 | 0.00016737
39 | 0.0031335 | 0.00078533
40 | 0.00035693 | 8.9455e-05
41 | 0.00045066 | 0.00011295
42 | 0.0020465 | 0.00051289
43 | 0.0012799 | 0.00032078
44 | 0.00019018 | 4.7664e-05
45 | 0.00051185 | 0.00012828
46 | 0.0028536 | 0.00071518
47 | 0.0021174 | 0.00053067
48 | 0.0086377 | 0.0021648
49 | 0.0010045 | 0.00025175
50 | 0.0012138 | 0.0003042
51 | 0.0024051 | 0.00060278
52 | 0.0004945 | 0.00012393
53 | 0.0034069 | 0.00085386
54 | 0.0079834 | 0.0020008
55 | 0.0068423 | 0.0017148
56 | 0.004471 | 0.0011205
57 | 0.0069472 | 0.0017411
58 | 0.0020851 | 0.00052258
59 | 0.0015288 | 0.00038314
60 | 0.0025435 | 0.00063747
61 | 0.003201 | 0.00080224
62 | 0.0034075 | 0.00085401
63 | 0.0085121 | 0.0021333
64 | 0.0025027 | 0.00062723
65 | 0.0032386 | 0.00081167
66 | 0.0057215 | 0.0014339
67 | 0.0082798 | 0.0020751
68 | 0.0015281 | 0.00038298
69 | 0.0023172 | 0.00058076
70 | 0.0028466 | 0.00071341
71 | 0.0051299 | 0.0012857
72 | 0.0056255 | 0.0014099
73 | 0.0031603 | 0.00079206
74 | 0.0014051 | 0.00035215
75 | 0.0019696 | 0.00049362
76 | 0.0026543 | 0.00066524
77 | 0.0028643 | 0.00071787
78 | 0.0014852 | 0.00037223
79 | 0.0021513 | 0.00053915
80 | 0.0010811 | 0.00027094
81 | 0.0067049 | 0.0016804
82 | 0.0049838 | 0.001249
83 | 0.0054726 | 0.0013716
84 | 0.0021465 | 0.00053795
85 | 0.0027782 | 0.00069629
86 | 0.0032113 | 0.00080482
87 | 0.0017156 | 0.00042997
88 | 0.0016198 | 0.00040595
89 | 0.0029573 | 0.00074118
90 | 0.001794 | 0.00044962
91 | 0.00072178 | 0.0001809
92 | 0.0013632 | 0.00034166
93 | 0.0014885 | 0.00037306
94 | 0.0017883 | 0.00044819

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1