## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1094-8_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1094-8_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1094-8_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1094-8_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1094-8_0_2_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1094-8_0_2_node_83 | 0.4 | n |  | TRUE
6 | bus_LV_1094-8_0_2_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1094-8_0_2_node_20 | 0.4 | n |  | TRUE
8 | bus_LV_1094-8_0_2_node_81 | 0.4 | n |  | TRUE
9 | bus_LV_1094-8_0_2_node_82 | 0.4 | n |  | TRUE
10 | bus_LV_1094-8_0_2_node_21 | 0.4 | n |  | TRUE
11 | bus_LV_1094-8_0_2_node_22 | 0.4 | n |  | TRUE
12 | bus_LV_1094-8_0_2_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_1094-8_0_2_node_24 | 0.4 | n |  | TRUE
14 | bus_LV_1094-8_0_2_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_1094-8_0_2_node_26 | 0.4 | n |  | TRUE
16 | bus_MV_2_1_node_248 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1094-8_0_2_load_0 | 0 | 0.0042359 | 0.0010616 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1094-8_0_2_load_1 | 1 | 0.0080584 | 0.0020196 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1094-8_0_2_load_83 | 5 | 0.0081193 | 0.0020349 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1094-8_0_2_load_81 | 8 | 0.022206 | 0.0055655 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1094-8_0_2_load_82 | 9 | 0.031018 | 0.0077739 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1094-8_0_2_load_21 | 10 | 0.016504 | 0.0041363 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1094-8_0_2_load_22 | 11 | 0.0025775 | 0.00064597 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1094-8_0_2_load_24 | 13 | 0.00049759 | 0.00012471 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1094-8_0_2_load_25 | 14 | 0.0020906 | 0.00052395 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1094-8_0_2_load_26 | 15 | 0.0019313 | 0.00048403 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1094-8_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.041912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1094-8_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.023712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1094-8_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.014667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1094-8_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.11355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1094-8_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.048852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1094-8_0_2_line_5 | NAYY 4x150 SE | 4 | 8 | 0.020856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1094-8_0_2_line_6 | NAYY 4x150 SE | 5 | 6 | 0.023524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1094-8_0_2_line_7 | NAYY 4x150 SE | 6 | 7 | 0.19098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1094-8_0_2_line_8 | NAYY 4x150 SE | 7 | 10 | 0.049309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1094-8_0_2_line_9 | NAYY 4x150 SE | 8 | 9 | 0.005473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1094-8_0_2_line_10 | NAYY 4x150 SE | 10 | 11 | 0.22378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1094-8_0_2_line_11 | NAYY 4x150 SE | 11 | 12 | 0.074341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1094-8_0_2_line_12 | NAYY 4x150 SE | 12 | 13 | 0.015392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1094-8_0_2_line_13 | NAYY 4x150 SE | 12 | 14 | 0.0045992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1094-8_0_2_line_14 | NAYY 4x150 SE | 13 | 15 | 0.0104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1094-8_0_2_trafo_81 | 0.25 MVA 20/0.4 kV | 16 | 8 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2652348.2622 | 1221119.2839 | 2652361.5586 | 1221119.1808 | 2652369.7642 | 1221115.1838 | 2652379.8004 | 1221104.8768 | 2652384.7292 | 1221103.5604
1 | 2652407.4697 | 1221096.8707 | 2652396.7272 | 1221100.3561 | 2652384.7292 | 1221103.5604
2 | 2652417.8549 | 1221107.2573 | 2652407.4697 | 1221096.8707
3 | 2652336.8481 | 1221052.9453 | 2652349.9678 | 1221066.4244 | 2652352.7297 | 1221071.5518 | 2652352.9495 | 1221077.613 | 2652352.8291 | 1221085.2722 | 2652353.8268 | 1221090.0061 | 2652357.5839 | 1221093.2411 | 2652362.443 | 1221094.529 | 2652369.2859 | 1221093.6553 | 2652376.296 | 1221089.3031 | 2652387.513 | 1221076.7162 | 2652394.2957 | 1221083.5578 | 2652407.4697 | 1221096.8707
4 | 2652417.8549 | 1221107.2573 | 2652414.3688 | 1221111.1623 | 2652403.7062 | 1221125.3995 | 2652384.8978 | 1221143.1033
5 | 2652336.8481 | 1221052.9453 | 2652329.4928 | 1221057.7392 | 2652323.2364 | 1221058.3402 | 2652317.6354 | 1221056.8679 | 2652317.6354 | 1221056.8679
6 | 2652367.7686 | 1221159.2266 | 2652384.8978 | 1221143.1033
7 | 2652237.7458 | 1221291.0329 | 2652241.1044 | 1221290.3953 | 2652242.2193 | 1221290.4273 | 2652243.4672 | 1221290.8608 | 2652245.4674 | 1221292.0123 | 2652248.1884 | 1221292.2808 | 2652249.9749 | 1221291.8518 | 2652253.3262 | 1221288.5903 | 2652259.6833 | 1221279.9407 | 2652272.5035 | 1221258.3621 | 2652276.9044 | 1221252.1969 | 2652294.9658 | 1221230.72 | 2652314.5201 | 1221209.4341 | 2652335.0436 | 1221189.2353 | 2652367.7686 | 1221159.2266
8 | 2652237.7458 | 1221291.0329 | 2652236.1558 | 1221285.4934 | 2652233.9843 | 1221280.5269 | 2652229.7591 | 1221275.3088 | 2652209.9611 | 1221259.5479 | 2652205.59 | 1221255.2846
9 | 2652317.6354 | 1221056.8679 | 2652313.5863 | 1221053.1857
10 | 2652205.59 | 1221255.2846 | 2652195.7901 | 1221245.7264 | 2652180.7538 | 1221235.4106 | 2652155.8915 | 1221219.2608 | 2652107.3225 | 1221178.8223 | 2652086.8429 | 1221158.5197 | 2652060.2461 | 1221124.6332 | 2652044.9286 | 1221102.2823
11 | 2651991.5062 | 1221051.744 | 2652004.215 | 1221065.4521 | 2652021.3593 | 1221076.831 | 2652034.9049 | 1221087.6558 | 2652044.9286 | 1221102.2823
12 | 2651991.5062 | 1221051.744 | 2652002.9325 | 1221041.4311
13 | 2651991.5062 | 1221051.744 | 2651988.3794 | 1221048.3713
14 | 2652010.4512 | 1221034.2559 | 2652007.8547 | 1221036.9887 | 2652002.9325 | 1221041.4311

## bus_geodata
| x | y | coords
0 | 2652348.2622 | 1221119.2839
1 | 2652384.7292 | 1221103.5604
2 | 2652407.4697 | 1221096.8707
3 | 2652417.8549 | 1221107.2573
4 | 2652336.8481 | 1221052.9453
5 | 2652384.8978 | 1221143.1033
6 | 2652367.7686 | 1221159.2266
7 | 2652237.7458 | 1221291.0329
8 | 2652317.6354 | 1221056.8679
9 | 2652313.5863 | 1221053.1857
10 | 2652205.59 | 1221255.2846
11 | 2652044.9286 | 1221102.2823
12 | 2651991.5062 | 1221051.744
13 | 2652002.9325 | 1221041.4311
14 | 2651988.3794 | 1221048.3713
15 | 2652010.4512 | 1221034.2559
16 | 2652315.4757 | 1221042.7848

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99075 | -0.064423 | 0.0042359 | 0.0010616
1 | 0.99101 | -0.062618 | 0.0080584 | 0.0020196
2 | 0.99143 | -0.059655 | 0 | 0
3 | 0.99075 | -0.064391 | 0 | 0
4 | 0.99867 | -0.0091905 | 0 | 0
5 | 0.9885 | -0.080212 | 0.0081193 | 0.0020349
6 | 0.98769 | -0.0859 | 0 | 0
7 | 0.98113 | -0.13241 | 0 | 0
8 | 1 | 0 | -0.07654 | -0.019066
9 | 0.99976 | -0.0016947 | 0.031018 | 0.0077739
10 | 0.97943 | -0.14451 | 0.016504 | 0.0041363
11 | 0.97712 | -0.16112 | 0.0025775 | 0.00064597
12 | 0.97663 | -0.16464 | 0 | 0
13 | 0.97657 | -0.16503 | 0.00049759 | 0.00012471
14 | 0.97661 | -0.16474 | 0.0020906 | 0.00052395
15 | 0.97654 | -0.16524 | 0.0019313 | 0.00048403
16 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0042359 | -0.0010616 | 0.004237 | 0.0010615 | 1.0585e-06 | -1.3276e-07 | 0.0063619 | 0.0063618 | 0.0063619 | 0.99075 | -0.064423 | 0.99101 | -0.062618 | 2.3563
1 | -0.012295 | -0.0030811 | 0.0123 | 0.0030827 | 5.043e-06 | 1.634e-06 | 0.018462 | 0.018461 | 0.018462 | 0.99101 | -0.062618 | 0.99143 | -0.059655 | 6.8376
2 | 0.032043 | 0.0080655 | -0.032021 | -0.0080576 | 2.1179e-05 | 7.9566e-06 | 0.048105 | 0.048105 | 0.048105 | 0.99143 | -0.059655 | 0.99075 | -0.064391 | 17.8165
3 | -0.044343 | -0.011148 | 0.044657 | 0.011268 | 0.00031397 | 0.00011928 | 0.066566 | 0.066565 | 0.066566 | 0.99143 | -0.059655 | 0.99867 | -0.0091905 | 24.654
4 | 0.032021 | 0.0080576 | -0.031951 | -0.0080311 | 7.0541e-05 | 2.6503e-05 | 0.048105 | 0.048105 | 0.048105 | 0.99075 | -0.064391 | 0.9885 | -0.080212 | 17.8166
5 | -0.044657 | -0.011268 | 0.044715 | 0.011289 | 5.7665e-05 | 2.1906e-05 | 0.066565 | 0.066565 | 0.066565 | 0.99867 | -0.0091905 | 1 | 0 | 24.6538
6 | 0.023832 | 0.0059962 | -0.023813 | -0.0059892 | 1.89e-05 | 6.9679e-06 | 0.035883 | 0.035883 | 0.035883 | 0.9885 | -0.080212 | 0.98769 | -0.0859 | 13.2899
7 | 0.023813 | 0.0059892 | -0.023659 | -0.0059326 | 0.00015345 | 5.659e-05 | 0.035883 | 0.035884 | 0.035884 | 0.98769 | -0.0859 | 0.98113 | -0.13241 | 13.2902
8 | 0.023659 | 0.0059326 | -0.02362 | -0.005918 | 3.9619e-05 | 1.4617e-05 | 0.035884 | 0.035884 | 0.035884 | 0.98113 | -0.13241 | 0.97943 | -0.14451 | 13.2903
9 | 0.031026 | 0.0077767 | -0.031018 | -0.0077739 | 7.2791e-06 | 2.7279e-06 | 0.046167 | 0.046167 | 0.046167 | 1 | 0 | 0.99976 | -0.0016947 | 17.0989
10 | 0.0071157 | 0.0017817 | -0.0070994 | -0.0017783 | 1.6319e-05 | 3.467e-06 | 0.01081 | 0.010811 | 0.010811 | 0.97943 | -0.14451 | 0.97712 | -0.16112 | 4.0041
11 | 0.0045219 | 0.0011323 | -0.0045197 | -0.0011324 | 2.1997e-06 | -8.4683e-08 | 0.0068859 | 0.0068862 | 0.0068862 | 0.97712 | -0.16112 | 0.97663 | -0.16464 | 2.5505
12 | 0.0024291 | 0.00060849 | -0.002429 | -0.00060863 | 1.3156e-07 | -1.4199e-07 | 0.0037009 | 0.003701 | 0.003701 | 0.97663 | -0.16464 | 0.97657 | -0.16503 | 1.3707
13 | 0.0020906 | 0.00052391 | -0.0020906 | -0.00052395 | 2.9119e-08 | -4.635e-08 | 0.0031853 | 0.0031853 | 0.0031853 | 0.97663 | -0.16464 | 0.97661 | -0.16474 | 1.1798
14 | 0.0019314 | 0.00048392 | -0.0019313 | -0.00048403 | 5.6202e-08 | -1.085e-07 | 0.0029428 | 0.0029428 | 0.0029428 | 0.97657 | -0.16503 | 0.97654 | -0.16524 | 1.0899

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.098747 | 0.024632

## res_load
| p_mw | q_mvar
0 | 0.0042359 | 0.0010616
1 | 0.0080584 | 0.0020196
2 | 0.0081193 | 0.0020349
3 | 0.022206 | 0.0055655
4 | 0.031018 | 0.0077739
5 | 0.016504 | 0.0041363
6 | 0.0025775 | 0.00064597
7 | 0.00049759 | 0.00012471
8 | 0.0020906 | 0.00052395
9 | 0.0019313 | 0.00048403

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1