## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1097-11_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1097-11_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1097-11_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1097-11_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1097-11_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1097-11_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1097-11_0_2_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_1097-11_0_2_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_1097-11_0_2_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1097-11_0_2_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_1097-11_0_2_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1097-11_0_2_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1097-11_0_2_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1097-11_0_2_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1097-11_0_2_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_1097-11_0_2_node_31 | 0.4 | n |  | TRUE
16 | bus_LV_1097-11_0_2_node_30 | 0.4 | n |  | TRUE
17 | bus_LV_1097-11_0_2_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1097-11_0_2_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_1097-11_0_2_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_1097-11_0_2_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1097-11_0_2_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1097-11_0_2_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_1097-11_0_2_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1097-11_0_2_node_28 | 0.4 | n |  | TRUE
25 | bus_LV_1097-11_0_2_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1097-11_0_2_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1097-11_0_2_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_1097-11_0_2_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_1097-11_0_2_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_1097-11_0_2_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_1097-11_0_2_node_32 | 0.4 | n |  | TRUE
32 | bus_MV_473_1_node_48 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1097-11_0_2_load_0 | 0 | 0.023289 | 0.0058368 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1097-11_0_2_load_4 | 4 | 0.0032642 | 0.0008181 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1097-11_0_2_load_5 | 5 | 0.0024191 | 0.00060629 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1097-11_0_2_load_12 | 6 | 0.0032556 | 0.00081593 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1097-11_0_2_load_11 | 7 | 0.0044338 | 0.0011112 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1097-11_0_2_load_7 | 8 | 0.005421 | 0.0013586 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1097-11_0_2_load_13 | 9 | 0.0048382 | 0.0012126 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1097-11_0_2_load_6 | 10 | 0.0032791 | 0.00082183 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1097-11_0_2_load_9 | 12 | 0.0021551 | 0.00054011 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1097-11_0_2_load_30 | 16 | 0.0025043 | 0.00062764 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1097-11_0_2_load_19 | 19 | 0.0044852 | 0.0011241 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1097-11_0_2_load_15 | 20 | 0.0027934 | 0.0007001 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1097-11_0_2_load_16 | 21 | 0.0012664 | 0.00031738 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1097-11_0_2_load_28 | 24 | 0.0094762 | 0.002375 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1097-11_0_2_load_22 | 25 | 0.0014149 | 0.00035461 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1097-11_0_2_load_23 | 26 | 0.0015822 | 0.00039654 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1097-11_0_2_load_24 | 27 | 0.001837 | 0.0004604 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1097-11_0_2_load_25 | 28 | 0.0021991 | 0.00055114 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1097-11_0_2_load_26 | 29 | 0.0029274 | 0.00073367 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1097-11_0_2_load_27 | 30 | 0.0035471 | 0.00088899 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1097-11_0_2_load_32 | 31 | 0.0019087 | 0.00047836 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1097-11_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.05765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1097-11_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0041472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1097-11_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.015056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1097-11_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.053179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1097-11_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.017747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1097-11_0_2_line_5 | NAYY 4x150 SE | 3 | 6 | 0.015711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1097-11_0_2_line_6 | NAYY 4x150 SE | 4 | 7 | 0.031135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1097-11_0_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.036528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1097-11_0_2_line_8 | NAYY 4x150 SE | 6 | 9 | 0.041511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1097-11_0_2_line_9 | NAYY 4x150 SE | 8 | 10 | 0.0055794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1097-11_0_2_line_10 | NAYY 4x150 SE | 9 | 17 | 0.03108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1097-11_0_2_line_11 | NAYY 4x150 SE | 10 | 11 | 0.023739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1097-11_0_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.022738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1097-11_0_2_line_13 | NAYY 4x150 SE | 11 | 13 | 0.12149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1097-11_0_2_line_14 | NAYY 4x150 SE | 13 | 14 | 0.071191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1097-11_0_2_line_15 | NAYY 4x150 SE | 14 | 15 | 0.075111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1097-11_0_2_line_16 | NAYY 4x150 SE | 14 | 16 | 0.091835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1097-11_0_2_line_17 | NAYY 4x150 SE | 15 | 31 | 0.072181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1097-11_0_2_line_18 | NAYY 4x150 SE | 16 | 30 | 0.0094329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1097-11_0_2_line_19 | NAYY 4x150 SE | 17 | 18 | 0.048895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1097-11_0_2_line_20 | NAYY 4x150 SE | 18 | 19 | 0.018506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1097-11_0_2_line_21 | NAYY 4x150 SE | 18 | 20 | 0.042784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1097-11_0_2_line_22 | NAYY 4x150 SE | 19 | 22 | 0.079333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1097-11_0_2_line_23 | NAYY 4x150 SE | 20 | 21 | 0.033304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1097-11_0_2_line_24 | NAYY 4x150 SE | 22 | 23 | 0.019593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1097-11_0_2_line_25 | NAYY 4x150 SE | 23 | 24 | 0.022199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1097-11_0_2_line_26 | NAYY 4x150 SE | 25 | 26 | 0.023281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1097-11_0_2_line_27 | NAYY 4x150 SE | 26 | 27 | 0.0078545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1097-11_0_2_line_28 | NAYY 4x150 SE | 27 | 28 | 0.029419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1097-11_0_2_line_29 | NAYY 4x150 SE | 28 | 29 | 0.0034605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1097-11_0_2_line_30 | NAYY 4x150 SE | 29 | 30 | 0.026214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1097-11_0_2_trafo_4 | 0.25 MVA 20/0.4 kV | 32 | 4 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2656158.1457 | 1233296.6532 | 2656152.796 | 1233300.3607 | 2656145.703 | 1233304.274 | 2656137.7353 | 1233307.0228 | 2656123.6465 | 1233307.7792 | 2656110.8861 | 1233307.3585 | 2656103.1622 | 1233306.9309
1 | 2656099.0213 | 1233306.7017 | 2656103.1622 | 1233306.9309
2 | 2656158.1457 | 1233296.6532 | 2656162.2945 | 1233291.0443 | 2656165.6197 | 1233283.671
3 | 2656099.0213 | 1233306.7017 | 2656099.5783 | 1233297.4232 | 2656099.9634 | 1233281.4832 | 2656099.9808 | 1233266.8072 | 2656104.7168 | 1233254.4184
4 | 2656099.0213 | 1233306.7017 | 2656089.8364 | 1233311.6738 | 2656084.0843 | 1233316.1732
5 | 2656165.6197 | 1233283.671 | 2656169.0017 | 1233268.3287
6 | 2656104.7168 | 1233254.4184 | 2656115.8345 | 1233225.3357
7 | 2656084.0843 | 1233316.1732 | 2656077.3509 | 1233321.4402 | 2656066.3282 | 1233338.2582 | 2656063.2463 | 1233345.5003
8 | 2656169.0017 | 1233268.3287 | 2656177.9379 | 1233227.791
9 | 2656061.0615 | 1233350.6341 | 2656063.2463 | 1233345.5003
10 | 2656182.088 | 1233196.9927 | 2656178.157 | 1233226.7971 | 2656177.9379 | 1233227.791
11 | 2656053.1001 | 1233372.9782 | 2656057.3881 | 1233359.8212 | 2656058.1755 | 1233357.416 | 2656061.0615 | 1233350.6341
12 | 2656053.1001 | 1233372.9782 | 2656035.8504 | 1233358.106
13 | 2655963.191 | 1233368.8954 | 2656026.0281 | 1233394.5704 | 2656047.8453 | 1233402.759 | 2656051.4709 | 1233377.9549 | 2656053.1001 | 1233372.9782
14 | 2655963.191 | 1233368.8954 | 2655903.861 | 1233329.2895
15 | 2655842.9524 | 1233285.1777 | 2655884.7093 | 1233316.9682 | 2655903.861 | 1233329.2895
16 | 2655903.861 | 1233329.2895 | 2655935.2774 | 1233242.9949
17 | 2655842.9524 | 1233285.1777 | 2655847.2332 | 1233264.6824 | 2655852.0965 | 1233232.1626 | 2655853.1095 | 1233213.8284
18 | 2655935.2774 | 1233242.9949 | 2655938.5043 | 1233234.1312
19 | 2656151.3208 | 1233159.2111 | 2656171.5038 | 1233187.3754 | 2656182.088 | 1233196.9927
20 | 2656151.3208 | 1233159.2111 | 2656140.9575 | 1233143.8791
21 | 2656151.3208 | 1233159.2111 | 2656149.4197 | 1233133.6544 | 2656150.0766 | 1233116.51
22 | 2656095.188 | 1233079.1629 | 2656105.8039 | 1233091.8713 | 2656140.9575 | 1233143.8791
23 | 2656150.0766 | 1233116.51 | 2656151.3517 | 1233083.2309
24 | 2656095.188 | 1233079.1629 | 2656086.6931 | 1233096.8275
25 | 2656086.6931 | 1233096.8275 | 2656077.8436 | 1233117.1868
26 | 2655958.3496 | 1233146.2659 | 2655954.2753 | 1233169.1875
27 | 2655952.9007 | 1233176.9208 | 2655954.2753 | 1233169.1875
28 | 2655946.7422 | 1233205.6776 | 2655951.1017 | 1233187.0419 | 2655952.9007 | 1233176.9208
29 | 2655946.7422 | 1233205.6776 | 2655945.954 | 1233209.0471
30 | 2655938.5043 | 1233234.1312 | 2655942.9294 | 1233221.9765 | 2655945.954 | 1233209.0471

## bus_geodata
| x | y | coords
0 | 2656103.1622 | 1233306.9309
1 | 2656158.1457 | 1233296.6532
2 | 2656099.0213 | 1233306.7017
3 | 2656165.6197 | 1233283.671
4 | 2656104.7168 | 1233254.4184
5 | 2656084.0843 | 1233316.1732
6 | 2656169.0017 | 1233268.3287
7 | 2656115.8345 | 1233225.3357
8 | 2656063.2463 | 1233345.5003
9 | 2656177.9379 | 1233227.791
10 | 2656061.0615 | 1233350.6341
11 | 2656053.1001 | 1233372.9782
12 | 2656035.8504 | 1233358.106
13 | 2655963.191 | 1233368.8954
14 | 2655903.861 | 1233329.2895
15 | 2655842.9524 | 1233285.1777
16 | 2655935.2774 | 1233242.9949
17 | 2656182.088 | 1233196.9927
18 | 2656151.3208 | 1233159.2111
19 | 2656140.9575 | 1233143.8791
20 | 2656150.0766 | 1233116.51
21 | 2656151.3517 | 1233083.2309
22 | 2656095.188 | 1233079.1629
23 | 2656086.6931 | 1233096.8275
24 | 2656077.8436 | 1233117.1868
25 | 2655958.3496 | 1233146.2659
26 | 2655954.2753 | 1233169.1875
27 | 2655952.9007 | 1233176.9208
28 | 2655946.7422 | 1233205.6776
29 | 2655945.954 | 1233209.0471
30 | 2655938.5043 | 1233234.1312
31 | 2655853.1095 | 1233213.8284
32 | 2656120.6604 | 1233212.7118

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99353 | -0.045172 | 0.023289 | 0.0058368
1 | 0.99135 | -0.06045 | 0 | 0
2 | 0.99382 | -0.043099 | 0 | 0
3 | 0.99078 | -0.06445 | 0 | 0
4 | 1 | 0 | -0.086727 | -0.021641
5 | 0.99302 | -0.048709 | 0.0024191 | 0.00060629
6 | 0.99019 | -0.068629 | 0.0032556 | 0.00081593
7 | 0.9998 | -0.0013785 | 0.0044338 | 0.0011112
8 | 0.9915 | -0.059385 | 0.005421 | 0.0013586
9 | 0.98882 | -0.078314 | 0.0048382 | 0.0012126
10 | 0.99131 | -0.060711 | 0.0032791 | 0.00082183
11 | 0.99062 | -0.065568 | 0 | 0
12 | 0.99055 | -0.066066 | 0.0021551 | 0.00054011
13 | 0.98747 | -0.087836 | 0 | 0
14 | 0.98562 | -0.10094 | 0 | 0
15 | 0.98541 | -0.10243 | 0 | 0
16 | 0.98349 | -0.1161 | 0.0025043 | 0.00062764
17 | 0.98801 | -0.084045 | 0 | 0
18 | 0.98673 | -0.093077 | 0 | 0
19 | 0.98636 | -0.095728 | 0.0044852 | 0.0011241
20 | 0.98648 | -0.09486 | 0.0027934 | 0.0007001
21 | 0.98642 | -0.095293 | 0.0012664 | 0.00031738
22 | 0.98527 | -0.10346 | 0 | 0
23 | 0.985 | -0.10537 | 0 | 0
24 | 0.9847 | -0.10753 | 0.0094762 | 0.002375
25 | 0.9826 | -0.12242 | 0.0014149 | 0.00035461
26 | 0.98265 | -0.12208 | 0.0015822 | 0.00039654
27 | 0.98268 | -0.12183 | 0.001837 | 0.0004604
28 | 0.98289 | -0.12036 | 0.0021991 | 0.00055114
29 | 0.98292 | -0.12011 | 0.0029274 | 0.00073367
30 | 0.9833 | -0.11741 | 0.0035471 | 0.00088899
31 | 0.98521 | -0.10384 | 0.0019087 | 0.00047836
32 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.02629 | 0.0066069 | -0.026234 | -0.0065862 | 5.5792e-05 | 2.0713e-05 | 0.039381 | 0.039382 | 0.039382 | 0.99353 | -0.045172 | 0.99135 | -0.06045 | 14.5858
1 | -0.049579 | -0.012444 | 0.049593 | 0.012449 | 1.4272e-05 | 5.4354e-06 | 0.074262 | 0.074262 | 0.074262 | 0.99353 | -0.045172 | 0.99382 | -0.043099 | 27.5043
2 | 0.026234 | 0.0065862 | -0.02622 | -0.0065808 | 1.4571e-05 | 5.4101e-06 | 0.039382 | 0.039382 | 0.039382 | 0.99135 | -0.06045 | 0.99078 | -0.06445 | 14.5858
3 | -0.081004 | -0.020342 | 0.081493 | 0.020529 | 0.00048825 | 0.0001871 | 0.1213 | 0.1213 | 0.1213 | 0.99382 | -0.043099 | 1 | 0 | 44.9258
4 | 0.031411 | 0.0078931 | -0.031387 | -0.0078839 | 2.4503e-05 | 9.1943e-06 | 0.047038 | 0.047038 | 0.047038 | 0.99382 | -0.043099 | 0.99302 | -0.048709 | 17.4215
5 | 0.02622 | 0.0065808 | -0.026204 | -0.0065751 | 1.5204e-05 | 5.6456e-06 | 0.039382 | 0.039382 | 0.039382 | 0.99078 | -0.06445 | 0.99019 | -0.068629 | 14.5858
6 | 0.0044347 | 0.0011111 | -0.0044338 | -0.0011112 | 8.46e-07 | -8.3008e-08 | 0.0065988 | 0.0065989 | 0.0065989 | 1 | 0 | 0.9998 | -0.0013785 | 2.444
7 | 0.028967 | 0.0072777 | -0.028924 | -0.0072616 | 4.2959e-05 | 1.6051e-05 | 0.043413 | 0.043413 | 0.043413 | 0.99302 | -0.048709 | 0.9915 | -0.059385 | 16.079
8 | 0.022949 | 0.0057592 | -0.022918 | -0.0057479 | 3.0812e-05 | 1.1318e-05 | 0.034489 | 0.03449 | 0.03449 | 0.99019 | -0.068629 | 0.98882 | -0.078314 | 12.7739
9 | 0.023503 | 0.005903 | -0.023499 | -0.0059014 | 4.3328e-06 | 1.5945e-06 | 0.035278 | 0.035278 | 0.035278 | 0.9915 | -0.059385 | 0.99131 | -0.060711 | 13.0658
10 | 0.01808 | 0.0045353 | -0.018065 | -0.0045302 | 1.4358e-05 | 5.1239e-06 | 0.027209 | 0.027209 | 0.027209 | 0.98882 | -0.078314 | 0.98801 | -0.084045 | 10.0774
11 | 0.02022 | 0.0050796 | -0.020206 | -0.0050746 | 1.365e-05 | 4.9441e-06 | 0.030356 | 0.030356 | 0.030356 | 0.99131 | -0.060711 | 0.99062 | -0.065568 | 11.2428
12 | 0.0021552 | 0.00053987 | -0.0021551 | -0.00054011 | 1.487e-07 | -2.3553e-07 | 0.0032372 | 0.0032373 | 0.0032373 | 0.99062 | -0.065568 | 0.99055 | -0.066066 | 1.199
13 | 0.018051 | 0.0045347 | -0.017995 | -0.0045149 | 5.5751e-05 | 1.9884e-05 | 0.027118 | 0.027119 | 0.027119 | 0.99062 | -0.065568 | 0.98747 | -0.087836 | 10.0441
14 | 0.017995 | 0.0045149 | -0.017963 | -0.0045032 | 3.2671e-05 | 1.1657e-05 | 0.027119 | 0.027119 | 0.027119 | 0.98747 | -0.087836 | 0.98562 | -0.10094 | 10.0442
15 | 0.0019094 | 0.00047678 | -0.0019091 | -0.00047759 | 3.8937e-07 | -8.073e-07 | 0.0028821 | 0.0028825 | 0.0028825 | 0.98562 | -0.10094 | 0.98541 | -0.10243 | 1.0676
16 | 0.016053 | 0.0040264 | -0.01602 | -0.0040146 | 3.3664e-05 | 1.178e-05 | 0.024237 | 0.024238 | 0.024238 | 0.98562 | -0.10094 | 0.98349 | -0.1161 | 8.9769
17 | 0.0019091 | 0.00047759 | -0.0019087 | -0.00047836 | 3.7427e-07 | -7.754e-07 | 0.0028825 | 0.0028828 | 0.0028828 | 0.98541 | -0.10243 | 0.98521 | -0.10384 | 1.0677
18 | 0.013515 | 0.003387 | -0.013513 | -0.0033862 | 2.4612e-06 | 8.2696e-07 | 0.020449 | 0.020449 | 0.020449 | 0.98349 | -0.1161 | 0.9833 | -0.11741 | 7.5736
19 | 0.018065 | 0.0045302 | -0.018043 | -0.0045221 | 2.2588e-05 | 8.0623e-06 | 0.027209 | 0.027209 | 0.027209 | 0.98801 | -0.084045 | 0.98673 | -0.093077 | 10.0775
20 | 0.013982 | 0.0035052 | -0.013977 | -0.0035035 | 5.1341e-06 | 1.7384e-06 | 0.021086 | 0.021086 | 0.021086 | 0.98673 | -0.093077 | 0.98636 | -0.095728 | 7.8095
21 | 0.0040609 | 0.0010169 | -0.0040599 | -0.0010171 | 1.0011e-06 | -1.6131e-07 | 0.0061236 | 0.0061238 | 0.0061238 | 0.98673 | -0.093077 | 0.98648 | -0.09486 | 2.2681
22 | 0.0094917 | 0.0023794 | -0.0094815 | -0.0023765 | 1.0151e-05 | 2.8926e-06 | 0.014319 | 0.01432 | 0.01432 | 0.98636 | -0.095728 | 0.98527 | -0.10346 | 5.3036
23 | 0.0012664 | 0.00031698 | -0.0012664 | -0.00031738 | 7.5831e-08 | -3.96e-07 | 0.0019102 | 0.0019103 | 0.0019103 | 0.98648 | -0.09486 | 0.98642 | -0.095293 | 0.70752
24 | 0.0094815 | 0.0023765 | -0.009479 | -0.0023758 | 2.507e-06 | 7.1476e-07 | 0.01432 | 0.01432 | 0.01432 | 0.98527 | -0.10346 | 0.985 | -0.10537 | 5.3036
25 | 0.009479 | 0.0023758 | -0.0094762 | -0.002375 | 2.8405e-06 | 8.1003e-07 | 0.01432 | 0.01432 | 0.01432 | 0.985 | -0.10537 | 0.9847 | -0.10753 | 5.3036
26 | -0.0014149 | -0.00035461 | 0.001415 | 0.00035434 | 6.6695e-08 | -2.6925e-07 | 0.0021427 | 0.0021426 | 0.0021427 | 0.9826 | -0.12242 | 0.98265 | -0.12208 | 0.7936
27 | -0.0029972 | -0.00075088 | 0.0029973 | 0.00075082 | 1.0096e-07 | -6.0674e-08 | 0.0045385 | 0.0045385 | 0.0045385 | 0.98265 | -0.12208 | 0.98268 | -0.12183 | 1.6809
28 | -0.0048343 | -0.0012112 | 0.0048353 | 0.0012112 | 9.8366e-07 | 5.5547e-09 | 0.0073202 | 0.0073201 | 0.0073202 | 0.98268 | -0.12183 | 0.98289 | -0.12036 | 2.7112
29 | -0.0070344 | -0.0017624 | 0.0070346 | 0.0017624 | 2.4488e-07 | 5.0326e-08 | 0.010649 | 0.010649 | 0.010649 | 0.98289 | -0.12036 | 0.98292 | -0.12011 | 3.9442
30 | -0.009962 | -0.0024961 | 0.0099657 | 0.0024972 | 3.7202e-06 | 1.0985e-06 | 0.015081 | 0.015081 | 0.015081 | 0.98292 | -0.12011 | 0.9833 | -0.11741 | 5.5855

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.089992 | 0.022459

## res_load
| p_mw | q_mvar
0 | 0.023289 | 0.0058368
1 | 0.0032642 | 0.0008181
2 | 0.0024191 | 0.00060629
3 | 0.0032556 | 0.00081593
4 | 0.0044338 | 0.0011112
5 | 0.005421 | 0.0013586
6 | 0.0048382 | 0.0012126
7 | 0.0032791 | 0.00082183
8 | 0.0021551 | 0.00054011
9 | 0.0025043 | 0.00062764
10 | 0.0044852 | 0.0011241
11 | 0.0027934 | 0.0007001
12 | 0.0012664 | 0.00031738
13 | 0.0094762 | 0.002375
14 | 0.0014149 | 0.00035461
15 | 0.0015822 | 0.00039654
16 | 0.001837 | 0.0004604
17 | 0.0021991 | 0.00055114
18 | 0.0029274 | 0.00073367
19 | 0.0035471 | 0.00088899
20 | 0.0019087 | 0.00047836

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1