## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1097-8_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1097-8_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1097-8_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1097-8_0_6_node_9 | 0.4 | n |  | TRUE
4 | bus_LV_1097-8_0_6_node_146 | 0.4 | n |  | TRUE
5 | bus_LV_1097-8_0_6_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1097-8_0_6_node_29 | 0.4 | n |  | TRUE
7 | bus_LV_1097-8_0_6_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_1097-8_0_6_node_145 | 0.4 | n |  | TRUE
9 | bus_LV_1097-8_0_6_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1097-8_0_6_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_1097-8_0_6_node_25 | 0.4 | n |  | TRUE
12 | bus_LV_1097-8_0_6_node_26 | 0.4 | n |  | TRUE
13 | bus_LV_1097-8_0_6_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_1097-8_0_6_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_1097-8_0_6_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_1097-8_0_6_node_34 | 0.4 | n |  | TRUE
17 | bus_LV_1097-8_0_6_node_33 | 0.4 | n |  | TRUE
18 | bus_LV_1097-8_0_6_node_35 | 0.4 | n |  | TRUE
19 | bus_LV_1097-8_0_6_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_1097-8_0_6_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_1097-8_0_6_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_1097-8_0_6_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_1097-8_0_6_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_1097-8_0_6_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_1097-8_0_6_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1097-8_0_6_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_1097-8_0_6_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_1097-8_0_6_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_1097-8_0_6_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_1097-8_0_6_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_1097-8_0_6_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_1097-8_0_6_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_1097-8_0_6_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_1097-8_0_6_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_1097-8_0_6_node_39 | 0.4 | n |  | TRUE
36 | bus_LV_1097-8_0_6_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_1097-8_0_6_node_37 | 0.4 | n |  | TRUE
38 | bus_LV_1097-8_0_6_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_1097-8_0_6_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_1097-8_0_6_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_1097-8_0_6_node_40 | 0.4 | n |  | TRUE
42 | bus_LV_1097-8_0_6_node_103 | 0.4 | n |  | TRUE
43 | bus_LV_1097-8_0_6_node_83 | 0.4 | n |  | TRUE
44 | bus_LV_1097-8_0_6_node_82 | 0.4 | n |  | TRUE
45 | bus_LV_1097-8_0_6_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_1097-8_0_6_node_107 | 0.4 | n |  | TRUE
47 | bus_LV_1097-8_0_6_node_105 | 0.4 | n |  | TRUE
48 | bus_LV_1097-8_0_6_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_1097-8_0_6_node_45 | 0.4 | n |  | TRUE
50 | bus_LV_1097-8_0_6_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_1097-8_0_6_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_1097-8_0_6_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_1097-8_0_6_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_1097-8_0_6_node_49 | 0.4 | n |  | TRUE
55 | bus_LV_1097-8_0_6_node_62 | 0.4 | n |  | TRUE
56 | bus_LV_1097-8_0_6_node_73 | 0.4 | n |  | TRUE
57 | bus_LV_1097-8_0_6_node_125 | 0.4 | n |  | TRUE
58 | bus_LV_1097-8_0_6_node_50 | 0.4 | n |  | TRUE
59 | bus_LV_1097-8_0_6_node_59 | 0.4 | n |  | TRUE
60 | bus_LV_1097-8_0_6_node_61 | 0.4 | n |  | TRUE
61 | bus_LV_1097-8_0_6_node_71 | 0.4 | n |  | TRUE
62 | bus_LV_1097-8_0_6_node_116 | 0.4 | n |  | TRUE
63 | bus_LV_1097-8_0_6_node_117 | 0.4 | n |  | TRUE
64 | bus_LV_1097-8_0_6_node_115 | 0.4 | n |  | TRUE
65 | bus_LV_1097-8_0_6_node_123 | 0.4 | n |  | TRUE
66 | bus_LV_1097-8_0_6_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_1097-8_0_6_node_60 | 0.4 | n |  | TRUE
68 | bus_LV_1097-8_0_6_node_63 | 0.4 | n |  | TRUE
69 | bus_LV_1097-8_0_6_node_69 | 0.4 | n |  | TRUE
70 | bus_LV_1097-8_0_6_node_70 | 0.4 | n |  | TRUE
71 | bus_LV_1097-8_0_6_node_52 | 0.4 | n |  | TRUE
72 | bus_LV_1097-8_0_6_node_53 | 0.4 | n |  | TRUE
73 | bus_LV_1097-8_0_6_node_54 | 0.4 | n |  | TRUE
74 | bus_LV_1097-8_0_6_node_56 | 0.4 | n |  | TRUE
75 | bus_LV_1097-8_0_6_node_58 | 0.4 | n |  | TRUE
76 | bus_LV_1097-8_0_6_node_92 | 0.4 | n |  | TRUE
77 | bus_LV_1097-8_0_6_node_93 | 0.4 | n |  | TRUE
78 | bus_LV_1097-8_0_6_node_64 | 0.4 | n |  | TRUE
79 | bus_LV_1097-8_0_6_node_65 | 0.4 | n |  | TRUE
80 | bus_LV_1097-8_0_6_node_66 | 0.4 | n |  | TRUE
81 | bus_LV_1097-8_0_6_node_67 | 0.4 | n |  | TRUE
82 | bus_LV_1097-8_0_6_node_68 | 0.4 | n |  | TRUE
83 | bus_LV_1097-8_0_6_node_124 | 0.4 | n |  | TRUE
84 | bus_LV_1097-8_0_6_node_118 | 0.4 | n |  | TRUE
85 | bus_LV_1097-8_0_6_node_136 | 0.4 | n |  | TRUE
86 | bus_LV_1097-8_0_6_node_72 | 0.4 | n |  | TRUE
87 | bus_LV_1097-8_0_6_node_74 | 0.4 | n |  | TRUE
88 | bus_LV_1097-8_0_6_node_94 | 0.4 | n |  | TRUE
89 | bus_LV_1097-8_0_6_node_95 | 0.4 | n |  | TRUE
90 | bus_LV_1097-8_0_6_node_75 | 0.4 | n |  | TRUE
91 | bus_LV_1097-8_0_6_node_76 | 0.4 | n |  | TRUE
92 | bus_LV_1097-8_0_6_node_77 | 0.4 | n |  | TRUE
93 | bus_LV_1097-8_0_6_node_78 | 0.4 | n |  | TRUE
94 | bus_LV_1097-8_0_6_node_80 | 0.4 | n |  | TRUE
95 | bus_LV_1097-8_0_6_node_81 | 0.4 | n |  | TRUE
96 | bus_LV_1097-8_0_6_node_86 | 0.4 | n |  | TRUE
97 | bus_LV_1097-8_0_6_node_99 | 0.4 | n |  | TRUE
98 | bus_LV_1097-8_0_6_node_104 | 0.4 | n |  | TRUE
99 | bus_LV_1097-8_0_6_node_101 | 0.4 | n |  | TRUE
100 | bus_LV_1097-8_0_6_node_87 | 0.4 | n |  | TRUE
101 | bus_LV_1097-8_0_6_node_100 | 0.4 | n |  | TRUE
102 | bus_LV_1097-8_0_6_node_91 | 0.4 | n |  | TRUE
103 | bus_LV_1097-8_0_6_node_110 | 0.4 | n |  | TRUE
104 | bus_LV_1097-8_0_6_node_85 | 0.4 | n |  | TRUE
105 | bus_LV_1097-8_0_6_node_84 | 0.4 | n |  | TRUE
106 | bus_LV_1097-8_0_6_node_88 | 0.4 | n |  | TRUE
107 | bus_LV_1097-8_0_6_node_89 | 0.4 | n |  | TRUE
108 | bus_LV_1097-8_0_6_node_90 | 0.4 | n |  | TRUE
109 | bus_LV_1097-8_0_6_node_98 | 0.4 | n |  | TRUE
110 | bus_LV_1097-8_0_6_node_102 | 0.4 | n |  | TRUE
111 | bus_LV_1097-8_0_6_node_132 | 0.4 | n |  | TRUE
112 | bus_LV_1097-8_0_6_node_97 | 0.4 | n |  | TRUE
113 | bus_LV_1097-8_0_6_node_96 | 0.4 | n |  | TRUE
114 | bus_LV_1097-8_0_6_node_133 | 0.4 | n |  | TRUE
115 | bus_LV_1097-8_0_6_node_108 | 0.4 | n |  | TRUE
116 | bus_LV_1097-8_0_6_node_109 | 0.4 | n |  | TRUE
117 | bus_LV_1097-8_0_6_node_106 | 0.4 | n |  | TRUE
118 | bus_LV_1097-8_0_6_node_111 | 0.4 | n |  | TRUE
119 | bus_LV_1097-8_0_6_node_112 | 0.4 | n |  | TRUE
120 | bus_LV_1097-8_0_6_node_114 | 0.4 | n |  | TRUE
121 | bus_LV_1097-8_0_6_node_135 | 0.4 | n |  | TRUE
122 | bus_LV_1097-8_0_6_node_119 | 0.4 | n |  | TRUE
123 | bus_LV_1097-8_0_6_node_120 | 0.4 | n |  | TRUE
124 | bus_LV_1097-8_0_6_node_121 | 0.4 | n |  | TRUE
125 | bus_LV_1097-8_0_6_node_122 | 0.4 | n |  | TRUE
126 | bus_LV_1097-8_0_6_node_126 | 0.4 | n |  | TRUE
127 | bus_LV_1097-8_0_6_node_130 | 0.4 | n |  | TRUE
128 | bus_LV_1097-8_0_6_node_127 | 0.4 | n |  | TRUE
129 | bus_LV_1097-8_0_6_node_131 | 0.4 | n |  | TRUE
130 | bus_LV_1097-8_0_6_node_137 | 0.4 | n |  | TRUE
131 | bus_LV_1097-8_0_6_node_128 | 0.4 | n |  | TRUE
132 | bus_LV_1097-8_0_6_node_129 | 0.4 | n |  | TRUE
133 | bus_LV_1097-8_0_6_node_138 | 0.4 | n |  | TRUE
134 | bus_LV_1097-8_0_6_node_140 | 0.4 | n |  | TRUE
135 | bus_LV_1097-8_0_6_node_139 | 0.4 | n |  | TRUE
136 | bus_LV_1097-8_0_6_node_144 | 0.4 | n |  | TRUE
137 | bus_LV_1097-8_0_6_node_134 | 0.4 | n |  | TRUE
138 | bus_LV_1097-8_0_6_node_141 | 0.4 | n |  | TRUE
139 | bus_LV_1097-8_0_6_node_142 | 0.4 | n |  | TRUE
140 | bus_LV_1097-8_0_6_node_143 | 0.4 | n |  | TRUE
141 | bus_MV_473_1_node_73 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1097-8_0_6_load_0 | 0 | 0.0024262 | 0.00060807 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1097-8_0_6_load_1 | 1 | 0.0011894 | 0.0002981 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1097-8_0_6_load_8 | 5 | 0.0016934 | 0.00042441 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1097-8_0_6_load_29 | 6 | 0.0011425 | 0.00028633 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1097-8_0_6_load_24 | 7 | 0.0017644 | 0.00044219 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1097-8_0_6_load_145 | 8 | 0.00098481 | 0.00024682 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1097-8_0_6_load_5 | 9 | 0.001129 | 0.00028297 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1097-8_0_6_load_4 | 10 | 0.00095375 | 0.00023903 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1097-8_0_6_load_26 | 12 | 0.0019312 | 0.000484 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1097-8_0_6_load_15 | 13 | 0.0012834 | 0.00032166 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1097-8_0_6_load_6 | 14 | 0.0012504 | 0.00031338 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1097-8_0_6_load_7 | 15 | 0.0010083 | 0.0002527 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1097-8_0_6_load_34 | 16 | 0.0013241 | 0.00033186 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1097-8_0_6_load_33 | 17 | 0.0017321 | 0.00043411 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1097-8_0_6_load_35 | 18 | 0.00082502 | 0.00020677 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1097-8_0_6_load_23 | 19 | 0.0018744 | 0.00046976 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1097-8_0_6_load_10 | 20 | 0.0021173 | 0.00053065 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1097-8_0_6_load_11 | 21 | 0.0012305 | 0.00030839 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1097-8_0_6_load_13 | 23 | 0.0016701 | 0.00041857 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1097-8_0_6_load_14 | 24 | 0.0011653 | 0.00029204 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1097-8_0_6_load_19 | 25 | 0.0016197 | 0.00040594 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1097-8_0_6_load_27 | 26 | 0.0019312 | 0.000484 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1097-8_0_6_load_17 | 27 | 0.0020715 | 0.00051917 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1097-8_0_6_load_28 | 28 | 0.0014806 | 0.00037106 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1097-8_0_6_load_16 | 29 | 0.0016367 | 0.0004102 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1097-8_0_6_load_18 | 30 | 0.0017204 | 0.00043116 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1097-8_0_6_load_20 | 31 | 0.0014848 | 0.00037212 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1097-8_0_6_load_22 | 33 | 0.0014316 | 0.00035879 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1097-8_0_6_load_38 | 34 | 0.0010771 | 0.00026996 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1097-8_0_6_load_39 | 35 | 0.0020988 | 0.00052601 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1097-8_0_6_load_36 | 36 | 0.0075089 | 0.0018819 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1097-8_0_6_load_30 | 38 | 0.00061312 | 0.00015366 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1097-8_0_6_load_32 | 40 | 0.00094841 | 0.0002377 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1097-8_0_6_load_103 | 42 | 0.00081487 | 0.00020423 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1097-8_0_6_load_83 | 43 | 0.00065593 | 0.00016439 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1097-8_0_6_load_82 | 44 | 0.0010784 | 0.00027026 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1097-8_0_6_load_42 | 45 | 0.00095942 | 0.00024045 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1097-8_0_6_load_107 | 46 | 0.001463 | 0.00036665 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1097-8_0_6_load_105 | 47 | 0.00033626 | 8.4275e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1097-8_0_6_load_43 | 48 | 0.0031771 | 0.00079625 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1097-8_0_6_load_48 | 53 | 0.00054581 | 0.00013679 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1097-8_0_6_load_49 | 54 | 0.00027492 | 6.8901e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1097-8_0_6_load_62 | 55 | 0.0014029 | 0.00035161 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1097-8_0_6_load_73 | 56 | 0.0021195 | 0.00053121 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1097-8_0_6_load_125 | 57 | 0.0019539 | 0.00048969 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1097-8_0_6_load_50 | 58 | 0.0018855 | 0.00047255 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1097-8_0_6_load_59 | 59 | 0.00010061 | 2.5215e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1097-8_0_6_load_61 | 60 | 0.00039722 | 9.9554e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1097-8_0_6_load_71 | 61 | 0.0016438 | 0.00041197 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1097-8_0_6_load_115 | 64 | 0.0024593 | 0.00061636 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1097-8_0_6_load_123 | 65 | 0.0022305 | 0.00055902 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1097-8_0_6_load_51 | 66 | 0.00041044 | 0.00010287 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1097-8_0_6_load_60 | 67 | 0.0044344 | 0.0011114 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1097-8_0_6_load_69 | 69 | 0.00063865 | 0.00016006 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1097-8_0_6_load_70 | 70 | 0.00052194 | 0.00013081 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1097-8_0_6_load_52 | 71 | 0.00027171 | 6.8096e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1097-8_0_6_load_53 | 72 | 0.00093509 | 0.00023436 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1097-8_0_6_load_54 | 73 | 0.0024762 | 0.00062058 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1097-8_0_6_load_56 | 74 | 0.00043826 | 0.00010984 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1097-8_0_6_load_58 | 75 | 0.0012365 | 0.00030989 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1097-8_0_6_load_92 | 76 | 0.0011351 | 0.00028449 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1097-8_0_6_load_93 | 77 | 0.00094574 | 0.00023702 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1097-8_0_6_load_64 | 78 | 0.0070058 | 0.0017558 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1097-8_0_6_load_65 | 79 | 0.0074755 | 0.0018735 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1097-8_0_6_load_66 | 80 | 0.0035116 | 0.00088009 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1097-8_0_6_load_124 | 83 | 0.0047571 | 0.0011922 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1097-8_0_6_load_118 | 84 | 0.0041229 | 0.0010333 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1097-8_0_6_load_136 | 85 | 0.0075887 | 0.0019019 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1097-8_0_6_load_72 | 86 | 0.00078472 | 0.00019667 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1097-8_0_6_load_74 | 87 | 0.0019185 | 0.00048082 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1097-8_0_6_load_95 | 89 | 0.0016891 | 0.00042333 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1097-8_0_6_load_75 | 90 | 0.0039777 | 0.00099691 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1097-8_0_6_load_76 | 91 | 0.0025159 | 0.00063054 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1097-8_0_6_load_78 | 93 | 0.0023726 | 0.00059464 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1097-8_0_6_load_80 | 94 | 0.0013483 | 0.00033793 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1097-8_0_6_load_86 | 96 | 0.0025815 | 0.00064699 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1097-8_0_6_load_104 | 98 | 0.00069352 | 0.00017381 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1097-8_0_6_load_101 | 99 | 0.0010763 | 0.00026973 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1097-8_0_6_load_87 | 100 | 0.005064 | 0.0012692 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1097-8_0_6_load_100 | 101 | 0.0024918 | 0.00062451 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1097-8_0_6_load_91 | 102 | 0.0068594 | 0.0017191 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1097-8_0_6_load_110 | 103 | 0.00097766 | 0.00024503 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1097-8_0_6_load_85 | 104 | 0.00053916 | 0.00013513 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1097-8_0_6_load_84 | 105 | 0.00099678 | 0.00024982 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1097-8_0_6_load_88 | 106 | 0.0005491 | 0.00013762 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1097-8_0_6_load_98 | 109 | 0.0039735 | 0.00099586 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1097-8_0_6_load_102 | 110 | 0.0031794 | 0.00079685 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1097-8_0_6_load_132 | 111 | 0.003737 | 0.00093658 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1097-8_0_6_load_97 | 112 | 0.0023268 | 0.00058316 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1097-8_0_6_load_96 | 113 | 0.0021889 | 0.00054859 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1097-8_0_6_load_109 | 116 | 0.00040636 | 0.00010184 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1097-8_0_6_load_106 | 117 | 0.0005981 | 0.0001499 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1097-8_0_6_load_111 | 118 | 0.0010722 | 0.00026873 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1097-8_0_6_load_112 | 119 | 0.00054507 | 0.00013661 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1097-8_0_6_load_114 | 120 | 0.00093781 | 0.00023504 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1097-8_0_6_load_135 | 121 | 0.00083236 | 0.00020861 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1097-8_0_6_load_119 | 122 | 0.0010335 | 0.00025901 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1097-8_0_6_load_121 | 124 | 0.0026172 | 0.00065594 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1097-8_0_6_load_122 | 125 | 0.005773 | 0.0014469 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1097-8_0_6_load_126 | 126 | 0.0030158 | 0.00075584 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1097-8_0_6_load_130 | 127 | 0.0061111 | 0.0015316 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1097-8_0_6_load_127 | 128 | 0.0021394 | 0.00053618 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1097-8_0_6_load_128 | 131 | 0.012107 | 0.0030344 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1097-8_0_6_load_129 | 132 | 0.0068385 | 0.0017139 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1097-8_0_6_load_138 | 133 | 0.0051061 | 0.0012797 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1097-8_0_6_load_140 | 134 | 0.0030141 | 0.0007554 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1097-8_0_6_load_139 | 135 | 0.0026526 | 0.00066481 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1097-8_0_6_load_144 | 136 | 0.0024384 | 0.00061113 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1097-8_0_6_load_134 | 137 | 0.0027815 | 0.0006971 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1097-8_0_6_load_142 | 139 | 0.0019038 | 0.00047713 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1097-8_0_6_load_143 | 140 | 0.0016151 | 0.00040479 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 102 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1097-8_0_6_line_0 | NAYY 4x150 SE | 0 | 1 | 0.027762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_1097-8_0_6_line_1 | NAYY 4x150 SE | 0 | 2 | 0.011765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_1097-8_0_6_line_2 | NAYY 4x150 SE | 1 | 3 | 0.16233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_1097-8_0_6_line_3 | NAYY 4x150 SE | 2 | 4 | 0.55848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_1097-8_0_6_line_4 | NAYY 4x150 SE | 3 | 6 | 0.021707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_1097-8_0_6_line_5 | NAYY 4x150 SE | 3 | 7 | 0.057985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1097-8_0_6_line_6 | NAYY 4x150 SE | 3 | 5 | 0.062797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1097-8_0_6_line_7 | NAYY 4x150 SE | 4 | 9 | 0.68038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1097-8_0_6_line_8 | NAYY 4x150 SE | 4 | 8 | 0.02255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1097-8_0_6_line_9 | NAYY 4x150 SE | 6 | 18 | 0.015291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_1097-8_0_6_line_10 | NAYY 4x150 SE | 7 | 19 | 0.037904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1097-8_0_6_line_11 | NAYY 4x150 SE | 9 | 14 | 0.028587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1097-8_0_6_line_12 | NAYY 4x150 SE | 10 | 11 | 0.021739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1097-8_0_6_line_13 | NAYY 4x150 SE | 11 | 12 | 0.020484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1097-8_0_6_line_14 | NAYY 4x150 SE | 11 | 13 | 0.0085741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1097-8_0_6_line_15 | NAYY 4x150 SE | 12 | 34 | 0.087875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1097-8_0_6_line_16 | NAYY 4x150 SE | 13 | 22 | 0.055751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1097-8_0_6_line_17 | NAYY 4x150 SE | 14 | 15 | 0.022909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1097-8_0_6_line_18 | NAYY 4x150 SE | 15 | 16 | 0.019084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1097-8_0_6_line_19 | NAYY 4x150 SE | 16 | 17 | 0.024784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1097-8_0_6_line_20 | NAYY 4x150 SE | 17 | 40 | 0.033263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1097-8_0_6_line_21 | NAYY 4x150 SE | 18 | 33 | 0.0079237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_1097-8_0_6_line_22 | NAYY 4x150 SE | 20 | 21 | 0.019355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_1097-8_0_6_line_23 | NAYY 4x150 SE | 20 | 22 | 0.011551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
24 | LV_1097-8_0_6_line_24 | NAYY 4x150 SE | 21 | 23 | 0.024773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_1097-8_0_6_line_25 | NAYY 4x150 SE | 22 | 24 | 0.034454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_1097-8_0_6_line_26 | NAYY 4x150 SE | 23 | 25 | 0.0023421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_1097-8_0_6_line_27 | NAYY 4x150 SE | 24 | 26 | 0.0015854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_1097-8_0_6_line_28 | NAYY 4x150 SE | 25 | 27 | 0.023087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
29 | LV_1097-8_0_6_line_29 | NAYY 4x150 SE | 26 | 28 | 0.021447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_1097-8_0_6_line_30 | NAYY 4x150 SE | 27 | 29 | 0.0050891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_1097-8_0_6_line_31 | NAYY 4x150 SE | 28 | 36 | 0.050039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_1097-8_0_6_line_32 | NAYY 4x150 SE | 29 | 30 | 0.028078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_1097-8_0_6_line_33 | NAYY 4x150 SE | 30 | 31 | 0.038955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_1097-8_0_6_line_34 | NAYY 4x150 SE | 31 | 32 | 0.0090436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_1097-8_0_6_line_35 | NAYY 4x150 SE | 32 | 33 | 0.063538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_1097-8_0_6_line_36 | NAYY 4x150 SE | 34 | 35 | 0.084636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1097-8_0_6_line_37 | NAYY 4x150 SE | 36 | 37 | 0.016352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_1097-8_0_6_line_38 | NAYY 4x150 SE | 37 | 41 | 0.027107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_1097-8_0_6_line_39 | NAYY 4x150 SE | 38 | 39 | 0.012628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1097-8_0_6_line_40 | NAYY 4x150 SE | 39 | 40 | 0.020386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1097-8_0_6_line_41 | NAYY 4x150 SE | 41 | 42 | 0.05826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1097-8_0_6_line_42 | NAYY 4x150 SE | 41 | 43 | 0.013811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_1097-8_0_6_line_43 | NAYY 4x150 SE | 43 | 44 | 0.029607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
44 | LV_1097-8_0_6_line_44 | NAYY 4x150 SE | 44 | 105 | 0.048524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_1097-8_0_6_line_45 | NAYY 4x150 SE | 45 | 46 | 0.094097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1097-8_0_6_line_46 | NAYY 4x150 SE | 46 | 47 | 0.015728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1097-8_0_6_line_47 | NAYY 4x150 SE | 47 | 117 | 0.010194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1097-8_0_6_line_48 | NAYY 4x150 SE | 48 | 49 | 0.02028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1097-8_0_6_line_49 | NAYY 4x150 SE | 49 | 53 | 0.011029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1097-8_0_6_line_50 | NAYY 4x150 SE | 49 | 54 | 0.0039449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1097-8_0_6_line_51 | NAYY 4x150 SE | 50 | 51 | 0.019126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_1097-8_0_6_line_52 | NAYY 4x150 SE | 50 | 52 | 0.029484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
53 | LV_1097-8_0_6_line_53 | NAYY 4x150 SE | 51 | 55 | 0.016537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1097-8_0_6_line_54 | NAYY 4x150 SE | 51 | 56 | 0.013253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_1097-8_0_6_line_55 | NAYY 4x150 SE | 52 | 57 | 0.0051921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
56 | LV_1097-8_0_6_line_56 | NAYY 4x150 SE | 53 | 58 | 0.012508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1097-8_0_6_line_57 | NAYY 4x150 SE | 54 | 59 | 0.016622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1097-8_0_6_line_58 | NAYY 4x150 SE | 55 | 60 | 0.011224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1097-8_0_6_line_59 | NAYY 4x150 SE | 56 | 61 | 0.018514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
60 | LV_1097-8_0_6_line_60 | NAYY 4x150 SE | 57 | 65 | 0.0017255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_1097-8_0_6_line_61 | NAYY 4x150 SE | 58 | 66 | 0.0089505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1097-8_0_6_line_62 | NAYY 4x150 SE | 59 | 67 | 0.0082682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1097-8_0_6_line_63 | NAYY 4x150 SE | 60 | 75 | 0.011147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1097-8_0_6_line_64 | NAYY 4x150 SE | 61 | 86 | 0.0097342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
65 | LV_1097-8_0_6_line_65 | NAYY 4x150 SE | 62 | 63 | 0.008909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1097-8_0_6_line_66 | NAYY 4x150 SE | 62 | 64 | 0.028944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1097-8_0_6_line_67 | NAYY 4x150 SE | 63 | 65 | 0.0052053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
68 | LV_1097-8_0_6_line_68 | NAYY 4x150 SE | 63 | 122 | 0.013778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
69 | LV_1097-8_0_6_line_69 | NAYY 4x150 SE | 64 | 69 | 0.016445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1097-8_0_6_line_70 | NAYY 4x150 SE | 66 | 68 | 0.013848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1097-8_0_6_line_71 | NAYY 4x150 SE | 67 | 74 | 0.0024113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1097-8_0_6_line_72 | NAYY 4x150 SE | 68 | 69 | 0.0023166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1097-8_0_6_line_73 | NAYY 4x150 SE | 68 | 70 | 0.010149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1097-8_0_6_line_74 | NAYY 4x150 SE | 71 | 72 | 0.0033254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1097-8_0_6_line_75 | NAYY 4x150 SE | 71 | 73 | 0.0082997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1097-8_0_6_line_76 | NAYY 4x150 SE | 73 | 74 | 0.00042016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1097-8_0_6_line_77 | NAYY 4x150 SE | 76 | 77 | 0.015581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1097-8_0_6_line_78 | NAYY 4x150 SE | 77 | 88 | 0.037791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1097-8_0_6_line_79 | NAYY 4x150 SE | 78 | 79 | 0.0087094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1097-8_0_6_line_80 | NAYY 4x150 SE | 78 | 80 | 0.012074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1097-8_0_6_line_81 | NAYY 4x150 SE | 79 | 81 | 0.027456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1097-8_0_6_line_82 | NAYY 4x150 SE | 80 | 82 | 0.040692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1097-8_0_6_line_83 | NAYY 4x150 SE | 81 | 83 | 0.031096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1097-8_0_6_line_84 | NAYY 4x150 SE | 82 | 84 | 0.020876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1097-8_0_6_line_85 | NAYY 4x150 SE | 83 | 85 | 0.016086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1097-8_0_6_line_86 | NAYY 4x150 SE | 85 | 130 | 0.017312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1097-8_0_6_line_87 | NAYY 4x150 SE | 86 | 87 | 0.017158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_1097-8_0_6_line_88 | NAYY 4x150 SE | 87 | 88 | 0.0096558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
89 | LV_1097-8_0_6_line_89 | NAYY 4x150 SE | 88 | 89 | 0.0031252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
90 | LV_1097-8_0_6_line_90 | NAYY 4x150 SE | 89 | 113 | 0.0093372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
91 | LV_1097-8_0_6_line_91 | NAYY 4x150 SE | 90 | 91 | 0.025138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1097-8_0_6_line_92 | NAYY 4x150 SE | 90 | 92 | 0.026375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1097-8_0_6_line_93 | NAYY 4x150 SE | 91 | 93 | 0.022542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1097-8_0_6_line_94 | NAYY 4x150 SE | 92 | 94 | 0.045435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
95 | LV_1097-8_0_6_line_95 | NAYY 4x150 SE | 92 | 95 | 0.064262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_1097-8_0_6_line_96 | NAYY 4x150 SE | 93 | 96 | 0.018301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1097-8_0_6_line_97 | NAYY 4x150 SE | 94 | 97 | 0.013737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
98 | LV_1097-8_0_6_line_98 | NAYY 4x150 SE | 95 | 98 | 0.051478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1097-8_0_6_line_99 | NAYY 4x150 SE | 95 | 99 | 0.038638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_1097-8_0_6_line_100 | NAYY 4x150 SE | 96 | 100 | 0.024969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1097-8_0_6_line_101 | NAYY 4x150 SE | 97 | 102 | 0.038532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
102 | LV_1097-8_0_6_line_102 | NAYY 4x150 SE | 97 | 101 | 0.013486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1097-8_0_6_line_103 | NAYY 4x150 SE | 98 | 103 | 0.0023404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1097-8_0_6_line_104 | NAYY 4x150 SE | 99 | 104 | 0.037495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
105 | LV_1097-8_0_6_line_105 | NAYY 4x150 SE | 102 | 107 | 0.038854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
106 | LV_1097-8_0_6_line_106 | NAYY 4x150 SE | 103 | 116 | 0.020616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1097-8_0_6_line_107 | NAYY 4x150 SE | 104 | 105 | 0.019108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
108 | LV_1097-8_0_6_line_108 | NAYY 4x150 SE | 106 | 107 | 0.045908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1097-8_0_6_line_109 | NAYY 4x150 SE | 107 | 108 | 0.03232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
110 | LV_1097-8_0_6_line_110 | NAYY 4x150 SE | 108 | 109 | 0.002091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
111 | LV_1097-8_0_6_line_111 | NAYY 4x150 SE | 109 | 112 | 0.027796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
112 | LV_1097-8_0_6_line_112 | NAYY 4x150 SE | 110 | 111 | 0.040638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1097-8_0_6_line_113 | NAYY 4x150 SE | 111 | 114 | 0.015001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1097-8_0_6_line_114 | NAYY 4x150 SE | 112 | 113 | 0.012723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
115 | LV_1097-8_0_6_line_115 | NAYY 4x150 SE | 114 | 137 | 0.02978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1097-8_0_6_line_116 | NAYY 4x150 SE | 114 | 121 | 0.01492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1097-8_0_6_line_117 | NAYY 4x150 SE | 115 | 116 | 0.056189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1097-8_0_6_line_118 | NAYY 4x150 SE | 115 | 117 | 0.01509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1097-8_0_6_line_119 | NAYY 4x150 SE | 118 | 119 | 0.036864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1097-8_0_6_line_120 | NAYY 4x150 SE | 119 | 120 | 0.0018245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1097-8_0_6_line_121 | NAYY 4x150 SE | 120 | 121 | 0.019923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_1097-8_0_6_line_122 | NAYY 4x150 SE | 122 | 123 | 0.041581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
123 | LV_1097-8_0_6_line_123 | NAYY 4x150 SE | 123 | 124 | 0.011812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
124 | LV_1097-8_0_6_line_124 | NAYY 4x150 SE | 123 | 125 | 0.026945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_1097-8_0_6_line_125 | NAYY 4x150 SE | 124 | 126 | 0.027126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
126 | LV_1097-8_0_6_line_126 | NAYY 4x150 SE | 125 | 127 | 0.021655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_1097-8_0_6_line_127 | NAYY 4x150 SE | 126 | 128 | 0.0018053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_1097-8_0_6_line_128 | NAYY 4x150 SE | 127 | 129 | 0.022736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_1097-8_0_6_line_129 | NAYY 4x150 SE | 128 | 131 | 0.027089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_1097-8_0_6_line_130 | NAYY 4x150 SE | 129 | 134 | 0.039224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_1097-8_0_6_line_131 | NAYY 4x150 SE | 129 | 135 | 0.015169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_1097-8_0_6_line_132 | NAYY 4x150 SE | 130 | 133 | 0.0015186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_1097-8_0_6_line_133 | NAYY 4x150 SE | 130 | 132 | 0.021928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_1097-8_0_6_line_134 | NAYY 4x150 SE | 131 | 132 | 0.0014222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_1097-8_0_6_line_135 | NAYY 4x150 SE | 133 | 138 | 0.028786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_1097-8_0_6_line_136 | NAYY 4x150 SE | 134 | 136 | 0.016646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_1097-8_0_6_line_137 | NAYY 4x150 SE | 135 | 137 | 0.030306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_1097-8_0_6_line_138 | NAYY 4x150 SE | 136 | 140 | 0.012474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_1097-8_0_6_line_139 | NAYY 4x150 SE | 138 | 139 | 0.022738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1097-8_0_6_trafo_91 | 0.25 MVA 20/0.4 kV | 141 | 102 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2654956.429 | 1233301.6943 | 2654960.6494 | 1233300.0898 | 2654982.8601 | 1233293.2281
1 | 2654945.4317 | 1233305.8751 | 2654956.429 | 1233301.6943
2 | 2655104.3697 | 1233400.8737 | 2654982.8601 | 1233293.2281
3 | 2654945.4317 | 1233305.8751 | 2654387.7006 | 1233277.0186
4 | 2655104.3697 | 1233400.8737 | 2655122.1701 | 1233413.2963
5 | 2655104.3697 | 1233400.8737 | 2655133.1637 | 1233378.5373 | 2655148.549 | 1233363.4577
6 | 2655104.3697 | 1233400.8737 | 2655086.5459 | 1233411.76 | 2655072.2038 | 1233425.1914 | 2655057.0295 | 1233441.4816
7 | 2655020.0237 | 1233528.1756 | 2654387.7006 | 1233277.0186
8 | 2654387.7006 | 1233277.0186 | 2654384.7585 | 1233280.0047 | 2654368.1264 | 1233287.7748
9 | 2655134.7093 | 1233422.0473 | 2655122.1701 | 1233413.2963
10 | 2655148.549 | 1233363.4577 | 2655165.8866 | 1233346.4645 | 2655175.5983 | 1233336.9047
11 | 2655040.3928 | 1233532.7119 | 2655035.7825 | 1233536.2704 | 2655029.2738 | 1233540.1571 | 2655026.1014 | 1233536.9256 | 2655020.0237 | 1233528.1756
12 | 2655239.5432 | 1233274.6797 | 2655217.9929 | 1233271.8222
13 | 2655239.5432 | 1233274.6797 | 2655251.4996 | 1233258.0478
14 | 2655239.5432 | 1233274.6797 | 2655248.0365 | 1233275.8545
15 | 2655289.8717 | 1233179.6447 | 2655281.1774 | 1233195.4822 | 2655269.4116 | 1233230.551 | 2655252.4134 | 1233256.7766 | 2655251.4996 | 1233258.0478
16 | 2655303.3688 | 1233282.4223 | 2655289.2648 | 1233281.5573 | 2655248.0365 | 1233275.8545
17 | 2655058.5279 | 1233518.714 | 2655058.5279 | 1233518.714 | 2655040.3928 | 1233532.7119
18 | 2655058.5279 | 1233518.714 | 2655067.2671 | 1233529.0238 | 2655072.3949 | 1233531.1949 | 2655072.3949 | 1233531.1949
19 | 2655094.3034 | 1233522.1183 | 2655090.1663 | 1233526.7344 | 2655086.0482 | 1233529.1645 | 2655072.3949 | 1233531.1949
20 | 2655094.3034 | 1233522.1183 | 2655101.679 | 1233513.8884 | 2655117.468 | 1233498.2657
21 | 2655134.7093 | 1233422.0473 | 2655141.2071 | 1233426.5821
22 | 2655283.0964 | 1233305.6808 | 2655286.5395 | 1233302.7012 | 2655295.9924 | 1233291.3107
23 | 2655303.3688 | 1233282.4223 | 2655295.9924 | 1233291.3107
24 | 2655264.8033 | 1233322.3789 | 2655276.2818 | 1233311.5782 | 2655283.0964 | 1233305.6808
25 | 2655303.3688 | 1233282.4223 | 2655323.0602 | 1233281.6383 | 2655337.7587 | 1233282.829
26 | 2655264.8033 | 1233322.3789 | 2655263.0976 | 1233323.9839
27 | 2655339.3389 | 1233282.957 | 2655337.7587 | 1233282.829
28 | 2655263.0976 | 1233323.9839 | 2655246.2836 | 1233339.805
29 | 2655360.716 | 1233284.6886 | 2655339.3389 | 1233282.957
30 | 2655242.5773 | 1233343.2925 | 2655246.2836 | 1233339.805
31 | 2655360.716 | 1233284.6886 | 2655403.8629 | 1233288.1837 | 2655410.6109 | 1233288.3863
32 | 2655242.5773 | 1233343.2925 | 2655222.1289 | 1233362.5334
33 | 2655193.7585 | 1233389.2285 | 2655222.1289 | 1233362.5334
34 | 2655189.6712 | 1233397.2958 | 2655193.7585 | 1233389.2285 | 2655193.7585 | 1233389.2285
35 | 2655189.6712 | 1233397.2958 | 2655154.8352 | 1233431.1055 | 2655148.2406 | 1233431.1666 | 2655143.4913 | 1233428.1762 | 2655141.2071 | 1233426.5821
36 | 2655289.8717 | 1233179.6447 | 2655348.9932 | 1233119.0811
37 | 2655426.9464 | 1233288.1766 | 2655418.9019 | 1233288.6352 | 2655410.6109 | 1233288.3863
38 | 2655426.9464 | 1233288.1766 | 2655432.7871 | 1233286.9747 | 2655434.6947 | 1233286.192 | 2655452.5563 | 1233279.4764
39 | 2655131.9589 | 1233483.9275 | 2655123.0991 | 1233474.9285
40 | 2655131.9589 | 1233483.9275 | 2655117.468 | 1233498.2657
41 | 2655452.5563 | 1233279.4764 | 2655485.6463 | 1233231.5256
42 | 2655452.5563 | 1233279.4764 | 2655465.4126 | 1233274.4317
43 | 2655492.9739 | 1233263.617 | 2655465.4126 | 1233274.4317
44 | 2655492.9739 | 1233263.617 | 2655511.9778 | 1233256.1601 | 2655539.0069 | 1233248.4433
45 | 2655507.7075 | 1233130.0656 | 2655443.3801 | 1233061.3913
46 | 2655519.7807 | 1233140.1457 | 2655507.7075 | 1233130.0656
47 | 2655519.7807 | 1233140.1457 | 2655527.6057 | 1233146.6788
48 | 2655951.5028 | 1233486.9951 | 2655934.9161 | 1233475.3273
49 | 2655951.5028 | 1233486.9951 | 2655960.6213 | 1233480.7911
50 | 2655951.5028 | 1233486.9951 | 2655948.2424 | 1233489.2157
51 | 2655915.3285 | 1233448.6078 | 2655901.3961 | 1233461.752
52 | 2655935.3359 | 1233427.0709 | 2655934.2696 | 1233427.7502 | 2655928.324 | 1233432.8643 | 2655915.3285 | 1233448.6078
53 | 2655901.3961 | 1233461.752 | 2655901.0264 | 1233468.0526 | 2655895.087 | 1233476.3759
54 | 2655901.3961 | 1233461.752 | 2655888.67 | 1233458.0526
55 | 2655935.3359 | 1233427.0709 | 2655934.7 | 1233425.4639 | 2655934.6481 | 1233423.7401 | 2655935.1935 | 1233422.0886
56 | 2655960.6213 | 1233480.7911 | 2655963.0919 | 1233479.1102 | 2655969.0471 | 1233471.6825
57 | 2655948.2424 | 1233489.2157 | 2655940.8433 | 1233494.2551 | 2655934.2144 | 1233498.1137
58 | 2655895.087 | 1233476.3759 | 2655890.9151 | 1233482.2223 | 2655888.6571 | 1233485.5742
59 | 2655871.5713 | 1233451.0509 | 2655883.9255 | 1233456.6734 | 2655888.67 | 1233458.0526
60 | 2655936.2586 | 1233420.7311 | 2655935.1935 | 1233422.0886
61 | 2655969.0471 | 1233471.6825 | 2655974.6459 | 1233464.6993
62 | 2655934.2144 | 1233498.1137 | 2655927.0686 | 1233502.2731
63 | 2655882.4289 | 1233494.8194 | 2655888.6571 | 1233485.5742
64 | 2655871.5713 | 1233451.0509 | 2655862.7115 | 1233447.0187
65 | 2655941.1442 | 1233419.6652 | 2655942.7262 | 1233420.4918 | 2655943.9174 | 1233421.8261 | 2655944.5681 | 1233423.4777 | 2655944.6043 | 1233425.257 | 2655944.0055 | 1233426.9413
66 | 2655944.0055 | 1233426.9413 | 2655946.0862 | 1233427.8726 | 2655954.702 | 1233433.4573 | 2655968.0711 | 1233442.9501
67 | 2655941.1442 | 1233419.6652 | 2655939.4278 | 1233419.4378 | 2655937.7284 | 1233419.811 | 2655936.2586 | 1233420.7311
68 | 2655941.1442 | 1233419.6652 | 2655941.8605 | 1233417.5595 | 2655943.2713 | 1233414.0594 | 2655946.4111 | 1233406.9406
69 | 2655968.0711 | 1233442.9501 | 2655975.8868 | 1233448.4997 | 2655981.4345 | 1233452.533
70 | 2655983.3082 | 1233453.8953 | 2655974.6459 | 1233464.6993
71 | 2655924.9847 | 1233503.4861 | 2655927.0686 | 1233502.2731
72 | 2655983.3082 | 1233453.8953 | 2655981.4345 | 1233452.533
73 | 2655983.3082 | 1233453.8953 | 2655992.2578 | 1233458.6819
74 | 2655916.529 | 1233505.5402 | 2655913.2866 | 1233506.2785
75 | 2655916.529 | 1233505.5402 | 2655924.6216 | 1233503.6975
76 | 2655924.6216 | 1233503.6975 | 2655924.6216 | 1233503.6975 | 2655924.9847 | 1233503.4861
77 | 2655834.5716 | 1233485.9947 | 2655833.9134 | 1233470.4278
78 | 2655839.7207 | 1233433.3208 | 2655835.1307 | 1233451.2782 | 2655833.5977 | 1233462.9603 | 2655833.9134 | 1233470.4278
79 | 2656069.1784 | 1233466.0533 | 2656064.1779 | 1233465.876 | 2656060.4731 | 1233465.789
80 | 2656069.1784 | 1233466.0533 | 2656081.2451 | 1233466.4811
81 | 2656033.0242 | 1233465.1486 | 2656041.2441 | 1233465.3373 | 2656060.4731 | 1233465.789
82 | 2656121.7252 | 1233470.3328 | 2656118.057 | 1233469.9647 | 2656092.8078 | 1233466.8911 | 2656081.2451 | 1233466.4811
83 | 2656033.0242 | 1233465.1486 | 2656038.8942 | 1233446.3806 | 2656043.0917 | 1233435.7475
84 | 2656121.7252 | 1233470.3328 | 2656123.1766 | 1233460.9405 | 2656124.1968 | 1233449.6143
85 | 2656043.0917 | 1233435.7475 | 2656043.9666 | 1233433.5312 | 2656045.6803 | 1233419.9352
86 | 2656047.8453 | 1233402.759 | 2656045.6803 | 1233419.9352
87 | 2655862.7115 | 1233447.0187 | 2655856.8101 | 1233444.3329 | 2655847.8373 | 1233438.551
88 | 2655839.7207 | 1233433.3208 | 2655847.8373 | 1233438.551
89 | 2655839.7207 | 1233433.3208 | 2655837.405 | 1233431.2221
90 | 2655830.4867 | 1233424.9517 | 2655837.405 | 1233431.2221
91 | 2655650.0151 | 1233302.1074 | 2655629.3971 | 1233316.4891
92 | 2655672.7051 | 1233288.6725 | 2655651.611 | 1233300.9942 | 2655650.0151 | 1233302.1074
93 | 2655629.3971 | 1233316.4891 | 2655610.9082 | 1233329.3857
94 | 2655672.7051 | 1233288.6725 | 2655712.4778 | 1233310.637
95 | 2655631.5628 | 1233239.6114 | 2655633.4421 | 1233241.041 | 2655647.9048 | 1233261.0003 | 2655652.3299 | 1233266.2674 | 2655667.7987 | 1233284.6796 | 2655672.7051 | 1233288.6725
96 | 2655595.8981 | 1233339.8558 | 2655610.9082 | 1233329.3857
97 | 2655724.8715 | 1233316.5458 | 2655715.2221 | 1233312.1526 | 2655712.4778 | 1233310.637
98 | 2655631.5628 | 1233239.6114 | 2655627.3901 | 1233225.9858 | 2655617.829 | 1233206.4615 | 2655607.1304 | 1233199.2791 | 2655604.5668 | 1233198.8333
99 | 2655631.5628 | 1233239.6114 | 2655627.8266 | 1233236.7746 | 2655619.4917 | 1233234.2839 | 2655605.9886 | 1233235.5474 | 2655594.4615 | 1233237.464
100 | 2655595.8981 | 1233339.8558 | 2655581.5252 | 1233349.8814 | 2655574.4911 | 1233352.3216
101 | 2655724.8715 | 1233316.5458 | 2655747.9132 | 1233347.4298
102 | 2655724.8715 | 1233316.5458 | 2655717.8413 | 1233305.0372
103 | 2655604.5668 | 1233198.8333 | 2655602.261 | 1233198.4323
104 | 2655557.4741 | 1233243.6138 | 2655594.4615 | 1233237.464
105 | 2655772.8084 | 1233377.1788 | 2655759.7057 | 1233363.2358 | 2655747.9132 | 1233347.4298
106 | 2655583.4783 | 1233190.6628 | 2655594.7645 | 1233197.1287 | 2655602.261 | 1233198.4323
107 | 2655557.4741 | 1233243.6138 | 2655553.7592 | 1233244.2315 | 2655539.0069 | 1233248.4433
108 | 2655772.8084 | 1233377.1788 | 2655755.3939 | 1233419.6557
109 | 2655798.914 | 1233396.3361 | 2655772.8084 | 1233377.1788
110 | 2655798.914 | 1233396.3361 | 2655800.4633 | 1233397.7403
111 | 2655800.4633 | 1233397.7403 | 2655821.0592 | 1233416.4072
112 | 2655832.5357 | 1233295.9726 | 2655831.2781 | 1233297.2759 | 2655816.5838 | 1233309.3012 | 2655800.0274 | 1233320.2322
113 | 2655842.9524 | 1233285.1777 | 2655832.5357 | 1233295.9726
114 | 2655830.4867 | 1233424.9517 | 2655821.0592 | 1233416.4072
115 | 2655842.9524 | 1233285.1777 | 2655866.6466 | 1233303.2167
116 | 2655842.9524 | 1233285.1777 | 2655846.0029 | 1233270.5726
117 | 2655539.1889 | 1233156.3498 | 2655570.1271 | 1233182.7336 | 2655581.8421 | 1233189.7254 | 2655583.4783 | 1233190.6628
118 | 2655539.1889 | 1233156.3498 | 2655527.6057 | 1233146.6788
119 | 2655849.5597 | 1233249.1252 | 2655852.0965 | 1233232.1626 | 2655853.184 | 1233212.4795
120 | 2655849.5597 | 1233249.1252 | 2655849.2899 | 1233250.9296
121 | 2655846.0029 | 1233270.5726 | 2655847.2332 | 1233264.6824 | 2655849.2899 | 1233250.9296
122 | 2655963.191 | 1233368.8954 | 2655946.4111 | 1233406.9406
123 | 2655963.191 | 1233368.8954 | 2655974.1259 | 1233373.3633
124 | 2655963.191 | 1233368.8954 | 2655940.7809 | 1233353.9355
125 | 2655999.2368 | 1233383.6236 | 2655974.1259 | 1233373.3633
126 | 2655940.7809 | 1233353.9355 | 2655922.7705 | 1233341.9126
127 | 2655999.2368 | 1233383.6236 | 2656000.908 | 1233384.3064
128 | 2655903.861 | 1233329.2895 | 2655922.7705 | 1233341.9126
129 | 2656000.908 | 1233384.3064 | 2656025.9846 | 1233394.5526
130 | 2655903.861 | 1233329.2895 | 2655917.2795 | 1233292.4317
131 | 2655903.861 | 1233329.2895 | 2655891.1042 | 1233321.0824
132 | 2656047.8453 | 1233402.759 | 2656048.0649 | 1233401.2564
133 | 2656047.8453 | 1233402.759 | 2656027.3156 | 1233395.0536
134 | 2656027.3156 | 1233395.0536 | 2656026.0281 | 1233394.5704 | 2656025.9846 | 1233394.5526
135 | 2656053.1001 | 1233372.9782 | 2656051.4709 | 1233377.9549 | 2656048.0649 | 1233401.2564
136 | 2655917.2795 | 1233292.4317 | 2655922.974 | 1233276.79
137 | 2655891.1042 | 1233321.0824 | 2655884.7093 | 1233316.9682 | 2655866.6466 | 1233303.2167
138 | 2655927.2411 | 1233265.069 | 2655922.974 | 1233276.79
139 | 2656053.1001 | 1233372.9782 | 2656035.8504 | 1233358.106

## bus_geodata
| x | y | coords
0 | 2654956.429 | 1233301.6943
1 | 2654982.8601 | 1233293.2281
2 | 2654945.4317 | 1233305.8751
3 | 2655104.3697 | 1233400.8737
4 | 2654387.7006 | 1233277.0186
5 | 2655057.0295 | 1233441.4816
6 | 2655122.1701 | 1233413.2963
7 | 2655148.549 | 1233363.4577
8 | 2654368.1264 | 1233287.7748
9 | 2655020.0237 | 1233528.1756
10 | 2655217.9929 | 1233271.8222
11 | 2655239.5432 | 1233274.6797
12 | 2655251.4996 | 1233258.0478
13 | 2655248.0365 | 1233275.8545
14 | 2655040.3928 | 1233532.7119
15 | 2655058.5279 | 1233518.714
16 | 2655072.3949 | 1233531.1949
17 | 2655094.3034 | 1233522.1183
18 | 2655134.7093 | 1233422.0473
19 | 2655175.5983 | 1233336.9047
20 | 2655295.9924 | 1233291.3107
21 | 2655283.0964 | 1233305.6808
22 | 2655303.3688 | 1233282.4223
23 | 2655264.8033 | 1233322.3789
24 | 2655337.7587 | 1233282.829
25 | 2655263.0976 | 1233323.9839
26 | 2655339.3389 | 1233282.957
27 | 2655246.2836 | 1233339.805
28 | 2655360.716 | 1233284.6886
29 | 2655242.5773 | 1233343.2925
30 | 2655222.1289 | 1233362.5334
31 | 2655193.7585 | 1233389.2285
32 | 2655189.6712 | 1233397.2958
33 | 2655141.2071 | 1233426.5821
34 | 2655289.8717 | 1233179.6447
35 | 2655348.9932 | 1233119.0811
36 | 2655410.6109 | 1233288.3863
37 | 2655426.9464 | 1233288.1766
38 | 2655123.0991 | 1233474.9285
39 | 2655131.9589 | 1233483.9275
40 | 2655117.468 | 1233498.2657
41 | 2655452.5563 | 1233279.4764
42 | 2655485.6463 | 1233231.5256
43 | 2655465.4126 | 1233274.4317
44 | 2655492.9739 | 1233263.617
45 | 2655443.3801 | 1233061.3913
46 | 2655507.7075 | 1233130.0656
47 | 2655519.7807 | 1233140.1457
48 | 2655934.9161 | 1233475.3273
49 | 2655951.5028 | 1233486.9951
50 | 2655915.3285 | 1233448.6078
51 | 2655901.3961 | 1233461.752
52 | 2655935.3359 | 1233427.0709
53 | 2655960.6213 | 1233480.7911
54 | 2655948.2424 | 1233489.2157
55 | 2655895.087 | 1233476.3759
56 | 2655888.67 | 1233458.0526
57 | 2655935.1935 | 1233422.0886
58 | 2655969.0471 | 1233471.6825
59 | 2655934.2144 | 1233498.1137
60 | 2655888.6571 | 1233485.5742
61 | 2655871.5713 | 1233451.0509
62 | 2655944.0055 | 1233426.9413
63 | 2655941.1442 | 1233419.6652
64 | 2655968.0711 | 1233442.9501
65 | 2655936.2586 | 1233420.7311
66 | 2655974.6459 | 1233464.6993
67 | 2655927.0686 | 1233502.2731
68 | 2655983.3082 | 1233453.8953
69 | 2655981.4345 | 1233452.533
70 | 2655992.2578 | 1233458.6819
71 | 2655916.529 | 1233505.5402
72 | 2655913.2866 | 1233506.2785
73 | 2655924.6216 | 1233503.6975
74 | 2655924.9847 | 1233503.4861
75 | 2655882.4289 | 1233494.8194
76 | 2655834.5716 | 1233485.9947
77 | 2655833.9134 | 1233470.4278
78 | 2656069.1784 | 1233466.0533
79 | 2656060.4731 | 1233465.789
80 | 2656081.245 | 1233466.4811
81 | 2656033.0242 | 1233465.1486
82 | 2656121.7252 | 1233470.3328
83 | 2656043.0917 | 1233435.7475
84 | 2656124.1968 | 1233449.6143
85 | 2656045.6803 | 1233419.9352
86 | 2655862.7115 | 1233447.0187
87 | 2655847.8373 | 1233438.551
88 | 2655839.7207 | 1233433.3208
89 | 2655837.405 | 1233431.2221
90 | 2655650.0151 | 1233302.1074
91 | 2655629.3971 | 1233316.4891
92 | 2655672.7051 | 1233288.6725
93 | 2655610.9082 | 1233329.3857
94 | 2655712.4778 | 1233310.637
95 | 2655631.5628 | 1233239.6114
96 | 2655595.8981 | 1233339.8558
97 | 2655724.8715 | 1233316.5458
98 | 2655604.5668 | 1233198.8333
99 | 2655594.4615 | 1233237.464
100 | 2655574.4911 | 1233352.3216
101 | 2655717.8413 | 1233305.0372
102 | 2655747.9132 | 1233347.4298
103 | 2655602.261 | 1233198.4323
104 | 2655557.4741 | 1233243.6138
105 | 2655539.0069 | 1233248.4433
106 | 2655755.3939 | 1233419.6557
107 | 2655772.8084 | 1233377.1788
108 | 2655798.914 | 1233396.3361
109 | 2655800.4633 | 1233397.7403
110 | 2655800.0274 | 1233320.2322
111 | 2655832.5357 | 1233295.9726
112 | 2655821.0592 | 1233416.4072
113 | 2655830.4867 | 1233424.9517
114 | 2655842.9524 | 1233285.1777
115 | 2655539.1889 | 1233156.3498
116 | 2655583.4783 | 1233190.6628
117 | 2655527.6057 | 1233146.6788
118 | 2655853.184 | 1233212.4795
119 | 2655849.5597 | 1233249.1252
120 | 2655849.2899 | 1233250.9296
121 | 2655846.0029 | 1233270.5726
122 | 2655946.4111 | 1233406.9406
123 | 2655963.191 | 1233368.8954
124 | 2655974.1259 | 1233373.3633
125 | 2655940.7809 | 1233353.9355
126 | 2655999.2368 | 1233383.6236
127 | 2655922.7705 | 1233341.9126
128 | 2656000.908 | 1233384.3064
129 | 2655903.861 | 1233329.2895
130 | 2656047.8453 | 1233402.759
131 | 2656025.9846 | 1233394.5526
132 | 2656027.3156 | 1233395.0536
133 | 2656048.0649 | 1233401.2564
134 | 2655917.2795 | 1233292.4317
135 | 2655891.1042 | 1233321.0824
136 | 2655922.974 | 1233276.79
137 | 2655866.6466 | 1233303.2167
138 | 2656053.1001 | 1233372.9782
139 | 2656035.8504 | 1233358.106
140 | 2655927.2411 | 1233265.069
141 | 2655724.8715 | 1233316.5458

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98103 | -0.13469 | 0.0024262 | 0.00060807
1 | 0.98118 | -0.13357 | 0.0011894 | 0.0002981
2 | 0.98098 | -0.13507 | 0 | 0
3 | 0.98218 | -0.12631 | 0 | 0
4 | 0.97853 | -0.1529 | 0 | 0
5 | 0.98202 | -0.12742 | 0.0016934 | 0.00042441
6 | 0.98236 | -0.12494 | 0.0011425 | 0.00028633
7 | 0.98187 | -0.1285 | 0.0017644 | 0.00044219
8 | 0.9785 | -0.15313 | 0.00098481 | 0.00024682
9 | 0.97455 | -0.18168 | 0.001129 | 0.00028297
10 | 0.9847 | -0.10808 | 0.00095375 | 0.00023903
11 | 0.98473 | -0.10787 | 0 | 0
12 | 0.98457 | -0.10895 | 0.0019312 | 0.000484
13 | 0.9848 | -0.10733 | 0.0012834 | 0.00032166
14 | 0.97426 | -0.18375 | 0.0012504 | 0.00031338
15 | 0.97407 | -0.18511 | 0.0010083 | 0.0002527
16 | 0.97394 | -0.18604 | 0.0013241 | 0.00033186
17 | 0.97382 | -0.1869 | 0.0017321 | 0.00043411
18 | 0.98251 | -0.12392 | 0.00082502 | 0.00020677
19 | 0.98177 | -0.12924 | 0.0018744 | 0.00046976
20 | 0.9852 | -0.10451 | 0.0021173 | 0.00053065
21 | 0.98489 | -0.10671 | 0.0012305 | 0.00030839
22 | 0.98539 | -0.10311 | 0 | 0
23 | 0.98451 | -0.10943 | 0.0016701 | 0.00041857
24 | 0.9861 | -0.098069 | 0.0011653 | 0.00029204
25 | 0.98448 | -0.10967 | 0.0016197 | 0.00040594
26 | 0.98613 | -0.097831 | 0.0019312 | 0.000484
27 | 0.98416 | -0.11195 | 0.0020715 | 0.00051917
28 | 0.9866 | -0.094471 | 0.0014806 | 0.00037106
29 | 0.9841 | -0.11241 | 0.0016367 | 0.0004102
30 | 0.98377 | -0.11482 | 0.0017204 | 0.00043116
31 | 0.98333 | -0.11793 | 0.0014848 | 0.00037212
32 | 0.98324 | -0.11861 | 0 | 0
33 | 0.98258 | -0.12336 | 0.0014316 | 0.00035879
34 | 0.98417 | -0.11184 | 0.0010771 | 0.00026996
35 | 0.98391 | -0.11367 | 0.0020988 | 0.00052601
36 | 0.98773 | -0.086389 | 0.0075089 | 0.0018819
37 | 0.98816 | -0.083333 | 0 | 0
38 | 0.97372 | -0.18766 | 0.00061312 | 0.00015366
39 | 0.97373 | -0.18758 | 0 | 0
40 | 0.97375 | -0.18745 | 0.00094841 | 0.0002377
41 | 0.98888 | -0.078273 | 0 | 0
42 | 0.98881 | -0.078759 | 0.00081487 | 0.00020423
43 | 0.98924 | -0.075659 | 0.00065593 | 0.00016439
44 | 0.99004 | -0.069994 | 0.0010784 | 0.00027026
45 | 0.99298 | -0.049248 | 0.00095942 | 0.00024045
46 | 0.99311 | -0.04833 | 0.001463 | 0.00036665
47 | 0.99316 | -0.047943 | 0.00033626 | 8.4275e-05
48 | 0.98041 | -0.13686 | 0.0031771 | 0.00079625
49 | 0.98051 | -0.13619 | 0 | 0
50 | 0.98543 | -0.10124 | 0 | 0
51 | 0.98661 | -0.092947 | 0 | 0
52 | 0.98362 | -0.11407 | 0 | 0
53 | 0.9807 | -0.13481 | 0.00054581 | 0.00013679
54 | 0.98046 | -0.13656 | 0.00027492 | 6.8901e-05
55 | 0.98654 | -0.093462 | 0.0014029 | 0.00035161
56 | 0.98745 | -0.087071 | 0.0021195 | 0.00053121
57 | 0.9833 | -0.11634 | 0.0019539 | 0.00048969
58 | 0.98093 | -0.13316 | 0.0018855 | 0.00047255
59 | 0.98025 | -0.13805 | 0.00010061 | 2.5215e-05
60 | 0.98651 | -0.09365 | 0.00039722 | 9.9554e-05
61 | 0.98864 | -0.078746 | 0.0016438 | 0.00041197
62 | 0.98264 | -0.12099 | 0 | 0
63 | 0.98288 | -0.11927 | 0 | 0
64 | 0.98186 | -0.12655 | 0.0024593 | 0.00061636
65 | 0.98319 | -0.11708 | 0.0022305 | 0.00055902
66 | 0.98112 | -0.13181 | 0.00041044 | 0.00010287
67 | 0.98014 | -0.13879 | 0.0044344 | 0.0011114
68 | 0.98142 | -0.12967 | 0 | 0
69 | 0.98147 | -0.1293 | 0.00063865 | 0.00016006
70 | 0.98141 | -0.12972 | 0.00052194 | 0.00013081
71 | 0.98011 | -0.13901 | 0.00027171 | 6.8096e-05
72 | 0.98011 | -0.13905 | 0.00093509 | 0.00023436
73 | 0.98013 | -0.13891 | 0.0024762 | 0.00062058
74 | 0.98013 | -0.13889 | 0.00043826 | 0.00010984
75 | 0.98649 | -0.093792 | 0.0012365 | 0.00030989
76 | 0.99089 | -0.063013 | 0.0011351 | 0.00028449
77 | 0.99092 | -0.062833 | 0.00094574 | 0.00023702
78 | 0.97081 | -0.2055 | 0.0070058 | 0.0017558
79 | 0.971 | -0.20415 | 0.0074755 | 0.0018735
80 | 0.97067 | -0.20648 | 0.0035116 | 0.00088009
81 | 0.97189 | -0.19773 | 0 | 0
82 | 0.97043 | -0.20826 | 0 | 0
83 | 0.9729 | -0.19047 | 0.0047571 | 0.0011922
84 | 0.9703 | -0.20917 | 0.0041229 | 0.0010333
85 | 0.97353 | -0.18591 | 0.0075887 | 0.0019019
86 | 0.98927 | -0.074323 | 0.00078472 | 0.00019667
87 | 0.99039 | -0.066493 | 0.0019185 | 0.00048082
88 | 0.99103 | -0.062032 | 0 | 0
89 | 0.99124 | -0.060568 | 0.0016891 | 0.00042333
90 | 0.99547 | -0.031725 | 0.0039777 | 0.00099691
91 | 0.99501 | -0.034902 | 0.0025159 | 0.00063054
92 | 0.99609 | -0.027339 | 0 | 0
93 | 0.99469 | -0.03718 | 0.0023726 | 0.00059464
94 | 0.99787 | -0.014859 | 0.0013483 | 0.00033793
95 | 0.99408 | -0.041487 | 0 | 0
96 | 0.99449 | -0.038592 | 0.0025815 | 0.00064699
97 | 0.99842 | -0.011032 | 0 | 0
98 | 0.99368 | -0.044325 | 0.00069352 | 0.00017381
99 | 0.99297 | -0.049307 | 0.0010763 | 0.00026973
100 | 0.99431 | -0.039869 | 0.005064 | 0.0012692
101 | 0.99837 | -0.011369 | 0.0024918 | 0.00062451
102 | 1 | 0 | -0.23935 | -0.06025
103 | 0.99366 | -0.044438 | 0.00097766 | 0.00024503
104 | 0.99191 | -0.056775 | 0.00053916 | 0.00013513
105 | 0.99137 | -0.060551 | 0.00099678 | 0.00024982
106 | 0.99715 | -0.019588 | 0.0005491 | 0.00013762
107 | 0.99719 | -0.019334 | 0 | 0
108 | 0.99486 | -0.035439 | 0 | 0
109 | 0.99471 | -0.036484 | 0.0039735 | 0.00099586
110 | 0.97535 | -0.17302 | 0.0031794 | 0.00079685
111 | 0.97554 | -0.17166 | 0.003737 | 0.00093658
112 | 0.99276 | -0.050026 | 0.0023268 | 0.00058316
113 | 0.99188 | -0.056142 | 0.0021889 | 0.00054859
114 | 0.97569 | -0.17057 | 0 | 0
115 | 0.99328 | -0.047143 | 0 | 0
116 | 0.99355 | -0.045226 | 0.00040636 | 0.00010184
117 | 0.9932 | -0.047657 | 0.0005981 | 0.0001499
118 | 0.97548 | -0.17209 | 0.0010722 | 0.00026873
119 | 0.97553 | -0.17167 | 0.00054507 | 0.00013661
120 | 0.97554 | -0.17164 | 0.00093781 | 0.00023504
121 | 0.97561 | -0.17111 | 0.00083236 | 0.00020861
122 | 0.98218 | -0.12421 | 0.0010335 | 0.00025901
123 | 0.9801 | -0.13901 | 0 | 0
124 | 0.97971 | -0.1418 | 0.0026172 | 0.00065594
125 | 0.97873 | -0.14874 | 0.005773 | 0.0014469
126 | 0.9784 | -0.15106 | 0.0030158 | 0.00075584
127 | 0.97782 | -0.15528 | 0.0061111 | 0.0015316
128 | 0.97824 | -0.15224 | 0.0021394 | 0.00053618
129 | 0.97706 | -0.1607 | 0 | 0
130 | 0.97441 | -0.17963 | 0 | 0
131 | 0.97584 | -0.16936 | 0.012107 | 0.0030344
132 | 0.97574 | -0.17008 | 0.0068385 | 0.0017139
133 | 0.97439 | -0.17974 | 0.0051061 | 0.0012797
134 | 0.97666 | -0.1636 | 0.0030141 | 0.0007554
135 | 0.97671 | -0.1632 | 0.0026526 | 0.00066481
136 | 0.97656 | -0.16431 | 0.0024384 | 0.00061113
137 | 0.97614 | -0.16735 | 0.0027815 | 0.0006971
138 | 0.97431 | -0.18032 | 0 | 0
139 | 0.97425 | -0.18077 | 0.0019038 | 0.00047713
140 | 0.97653 | -0.16452 | 0.0016151 | 0.00040479
141 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.011475 | -0.0028428 | 0.011477 | 0.0028424 | 1.7468e-06 | -3.7987e-07 | 0.017393 | 0.017393 | 0.017393 | 0.98103 | -0.13469 | 0.98118 | -0.13357 | 2.1473
1 | 0.0090486 | 0.0022347 | -0.0090481 | -0.002235 | 4.6019e-07 | -2.6863e-07 | 0.013713 | 0.013713 | 0.013713 | 0.98103 | -0.13469 | 0.98098 | -0.13507 | 1.693
2 | -0.012666 | -0.0031405 | 0.012678 | 0.0031391 | 1.2441e-05 | -1.372e-06 | 0.019197 | 0.019194 | 0.019197 | 0.98118 | -0.13357 | 0.98218 | -0.12631 | 2.3699
3 | 0.0090481 | 0.002235 | -0.0090263 | -0.0022477 | 2.1857e-05 | -1.2693e-05 | 0.013713 | 0.013721 | 0.013721 | 0.98098 | -0.13507 | 0.97853 | -0.1529 | 1.6939
4 | -0.018012 | -0.0044741 | 0.018015 | 0.0044745 | 3.3586e-06 | 4.6747e-07 | 0.027274 | 0.027274 | 0.027274 | 0.98218 | -0.12631 | 0.98236 | -0.12494 | 3.3672
5 | 0.00364 | 0.00091123 | -0.0036389 | -0.00091154 | 1.1003e-06 | -3.1043e-07 | 0.0055143 | 0.0055146 | 0.0055146 | 0.98218 | -0.12631 | 0.98187 | -0.1285 | 2.0424
6 | 0.0016937 | 0.00042372 | -0.0016934 | -0.00042441 | 2.5798e-07 | -6.954e-07 | 0.0025657 | 0.002566 | 0.002566 | 0.98218 | -0.12631 | 0.98202 | -0.12742 | 0.95036
7 | 0.0080414 | 0.0020011 | -0.0080097 | -0.002006 | 3.1731e-05 | -4.8199e-06 | 0.012223 | 0.012229 | 0.012229 | 0.97853 | -0.1529 | 0.97455 | -0.18168 | 2.2647
8 | 0.00098484 | 0.00024655 | -0.00098481 | -0.00024682 | 3.1557e-08 | -2.7112e-07 | 0.0014975 | 0.0014976 | 0.0014976 | 0.97853 | -0.1529 | 0.9785 | -0.15313 | 0.55467
9 | -0.019158 | -0.0047609 | 0.019161 | 0.0047613 | 2.6756e-06 | 4.4823e-07 | 0.029005 | 0.029004 | 0.029005 | 0.98236 | -0.12494 | 0.98251 | -0.12392 | 3.5808
10 | 0.0018745 | 0.00046935 | -0.0018744 | -0.00046976 | 1.9087e-07 | -4.0594e-07 | 0.0028407 | 0.0028409 | 0.0028409 | 0.98187 | -0.1285 | 0.98177 | -0.12924 | 1.0522
11 | 0.0068806 | 0.001723 | -0.0068787 | -0.0017226 | 1.9687e-06 | 4.0111e-07 | 0.010505 | 0.010506 | 0.010506 | 0.97455 | -0.18168 | 0.97426 | -0.18375 | 3.8909
12 | -0.00095375 | -0.00023903 | 0.00095378 | 0.00023877 | 2.8176e-08 | -2.6571e-07 | 0.0014413 | 0.0014412 | 0.0014413 | 0.9847 | -0.10808 | 0.98473 | -0.10787 | 0.5338
13 | 0.0051097 | 0.0012785 | -0.0051089 | -0.0012785 | 7.6187e-07 | 3.2485e-08 | 0.0077205 | 0.0077206 | 0.0077206 | 0.98473 | -0.10787 | 0.98457 | -0.10895 | 2.8595
14 | -0.0060635 | -0.0015173 | 0.0060639 | 0.0015173 | 4.4908e-07 | 6.3636e-08 | 0.0091616 | 0.0091616 | 0.0091616 | 0.98473 | -0.10787 | 0.9848 | -0.10733 | 3.3932
15 | 0.0031778 | 0.00079447 | -0.0031765 | -0.0007951 | 1.2645e-06 | -6.3076e-07 | 0.0048019 | 0.0048023 | 0.0048023 | 0.98457 | -0.10895 | 0.98417 | -0.11184 | 1.7786
16 | -0.0073473 | -0.001839 | 0.0073516 | 0.0018399 | 4.2869e-06 | 9.3901e-07 | 0.011101 | 0.011101 | 0.011101 | 0.9848 | -0.10733 | 0.98539 | -0.10311 | 4.1114
17 | 0.0056283 | 0.0014092 | -0.0056272 | -0.0014091 | 1.0562e-06 | 1.2103e-07 | 0.0085957 | 0.0085958 | 0.0085958 | 0.97426 | -0.18375 | 0.97407 | -0.18511 | 3.1836
18 | 0.0046189 | 0.0011564 | -0.0046183 | -0.0011564 | 5.9282e-07 | -9.5144e-09 | 0.0070556 | 0.0070556 | 0.0070556 | 0.97407 | -0.18511 | 0.97394 | -0.18604 | 2.6132
19 | 0.0032942 | 0.00082454 | -0.0032938 | -0.0008247 | 3.9169e-07 | -1.5773e-07 | 0.0050326 | 0.0050327 | 0.0050327 | 0.97394 | -0.18604 | 0.97382 | -0.1869 | 1.864
20 | 0.0015617 | 0.00039059 | -0.0015616 | -0.00039095 | 1.1817e-07 | -3.6836e-07 | 0.002386 | 0.0023861 | 0.0023861 | 0.97382 | -0.1869 | 0.97375 | -0.18745 | 0.88375
21 | -0.019986 | -0.0049681 | 0.019987 | 0.0049684 | 1.5085e-06 | 2.7914e-07 | 0.030254 | 0.030254 | 0.030254 | 0.98251 | -0.12392 | 0.98258 | -0.12336 | 3.735
22 | 0.032919 | 0.0082103 | -0.032909 | -0.0082072 | 9.9469e-06 | 3.0866e-06 | 0.049706 | 0.049706 | 0.049706 | 0.9852 | -0.10451 | 0.98489 | -0.10671 | 6.1366
23 | -0.035037 | -0.008741 | 0.035043 | 0.0087431 | 6.7243e-06 | 2.1449e-06 | 0.052904 | 0.052904 | 0.052904 | 0.9852 | -0.10451 | 0.98539 | -0.10311 | 6.5314
24 | 0.031679 | 0.0078988 | -0.031667 | -0.0078952 | 1.1797e-05 | 3.5918e-06 | 0.047847 | 0.047848 | 0.047848 | 0.98489 | -0.10671 | 0.98451 | -0.10943 | 5.9071
25 | -0.042395 | -0.010583 | 0.042424 | 0.010593 | 2.9357e-05 | 9.9736e-06 | 0.064005 | 0.064004 | 0.064005 | 0.98539 | -0.10311 | 0.9861 | -0.098069 | 7.9018
26 | 0.029997 | 0.0074767 | -0.029996 | -0.0074764 | 1.0007e-06 | 2.9555e-07 | 0.045323 | 0.045323 | 0.045323 | 0.98451 | -0.10943 | 0.98448 | -0.10967 | 5.5955
27 | -0.04359 | -0.010885 | 0.043591 | 0.010886 | 1.4261e-06 | 4.8783e-07 | 0.065762 | 0.065762 | 0.065762 | 0.9861 | -0.098069 | 0.98613 | -0.097831 | 8.1188
28 | 0.028376 | 0.0070704 | -0.028367 | -0.0070679 | 8.8278e-06 | 2.5149e-06 | 0.042875 | 0.042876 | 0.042876 | 0.98448 | -0.10967 | 0.98416 | -0.11195 | 5.2933
29 | -0.045522 | -0.01137 | 0.045543 | 0.011377 | 2.104e-05 | 7.2711e-06 | 0.068676 | 0.068676 | 0.068676 | 0.98613 | -0.097831 | 0.9866 | -0.094471 | 8.4786
30 | 0.026296 | 0.0065487 | -0.026294 | -0.0065483 | 1.672e-06 | 4.4909e-07 | 0.039744 | 0.039744 | 0.039744 | 0.98416 | -0.11195 | 0.9841 | -0.11241 | 4.9066
31 | -0.047024 | -0.011748 | 0.047076 | 0.011766 | 5.2333e-05 | 1.8209e-05 | 0.070909 | 0.070908 | 0.070909 | 0.9866 | -0.094471 | 0.98773 | -0.086389 | 8.7542
32 | 0.024658 | 0.0061381 | -0.024649 | -0.006136 | 8.1118e-06 | 2.0501e-06 | 0.037269 | 0.037269 | 0.037269 | 0.9841 | -0.11241 | 0.98377 | -0.11482 | 4.6011
33 | 0.022929 | 0.0057049 | -0.022919 | -0.0057026 | 9.738e-06 | 2.2622e-06 | 0.034667 | 0.034668 | 0.034668 | 0.98377 | -0.11482 | 0.98333 | -0.11793 | 4.2799
34 | 0.021435 | 0.0053305 | -0.021433 | -0.0053301 | 1.9772e-06 | 4.1633e-07 | 0.032421 | 0.032421 | 0.032421 | 0.98333 | -0.11793 | 0.98324 | -0.11861 | 4.0026
35 | 0.021433 | 0.0053301 | -0.021419 | -0.0053272 | 1.3892e-05 | 2.927e-06 | 0.032421 | 0.032422 | 0.032422 | 0.98324 | -0.11861 | 0.98258 | -0.12336 | 4.0027
36 | 0.0020994 | 0.00052514 | -0.0020988 | -0.00052601 | 5.3204e-07 | -8.7058e-07 | 0.0031738 | 0.0031741 | 0.0031741 | 0.98417 | -0.11184 | 0.98391 | -0.11367 | 1.1756
37 | -0.054585 | -0.013648 | 0.054608 | 0.013656 | 2.2993e-05 | 8.2154e-06 | 0.082221 | 0.08222 | 0.082221 | 0.98773 | -0.086389 | 0.98816 | -0.083333 | 10.1507
38 | -0.054608 | -0.013656 | 0.054646 | 0.01367 | 3.8116e-05 | 1.3617e-05 | 0.08222 | 0.08222 | 0.08222 | 0.98816 | -0.083333 | 0.98888 | -0.078273 | 10.1507
39 | -0.00061312 | -0.00015366 | 0.00061313 | 0.00015351 | 6.9175e-09 | -1.5442e-07 | 0.00093696 | 0.00093691 | 0.00093696 | 0.97372 | -0.18766 | 0.97373 | -0.18758 | 0.34702
40 | -0.00061313 | -0.00015351 | 0.00061314 | 0.00015326 | 1.1165e-08 | -2.4929e-07 | 0.00093691 | 0.00093681 | 0.00093691 | 0.97373 | -0.18758 | 0.97375 | -0.18745 | 0.347
41 | 0.00081493 | 0.0002035 | -0.00081487 | -0.00020423 | 5.4655e-08 | -7.2635e-07 | 0.001226 | 0.0012263 | 0.0012263 | 0.98888 | -0.078273 | 0.98881 | -0.078759 | 0.45417
42 | -0.055461 | -0.013873 | 0.055481 | 0.01388 | 2.0003e-05 | 7.1616e-06 | 0.083446 | 0.083446 | 0.083446 | 0.98888 | -0.078273 | 0.98924 | -0.075659 | 10.302
43 | -0.056137 | -0.014045 | 0.056181 | 0.014061 | 4.3901e-05 | 1.5744e-05 | 0.084432 | 0.084432 | 0.084432 | 0.98924 | -0.075659 | 0.99004 | -0.069994 | 10.4238
44 | -0.057259 | -0.014331 | 0.057334 | 0.014358 | 7.4738e-05 | 2.6871e-05 | 0.086053 | 0.086052 | 0.086053 | 0.99004 | -0.069994 | 0.99137 | -0.060551 | 10.6238
45 | -0.00095942 | -0.00024045 | 0.00095954 | 0.00023928 | 1.2133e-07 | -1.1707e-06 | 0.0014377 | 0.0014373 | 0.0014377 | 0.99298 | -0.049248 | 0.99311 | -0.04833 | 0.53249
46 | -0.0024225 | -0.00060593 | 0.0024226 | 0.00060578 | 1.2927e-07 | -1.538e-07 | 0.0036293 | 0.0036292 | 0.0036293 | 0.99311 | -0.04833 | 0.99316 | -0.047943 | 1.3442
47 | -0.0027589 | -0.00069005 | 0.002759 | 0.00068996 | 1.0866e-07 | -9.0128e-08 | 0.004133 | 0.004133 | 0.004133 | 0.99316 | -0.047943 | 0.9932 | -0.047657 | 1.5308
48 | -0.0031771 | -0.00079625 | 0.0031774 | 0.00079611 | 2.9423e-07 | -1.4259e-07 | 0.004822 | 0.0048219 | 0.004822 | 0.98041 | -0.13686 | 0.98051 | -0.13619 | 1.7859
49 | -0.012112 | -0.0030352 | 0.012114 | 0.0030359 | 2.3251e-06 | 7.5512e-07 | 0.018381 | 0.018381 | 0.018381 | 0.98051 | -0.13619 | 0.9807 | -0.13481 | 6.8076
50 | 0.0089344 | 0.002239 | -0.0089339 | -0.0022389 | 4.5254e-07 | 1.243e-07 | 0.013559 | 0.013559 | 0.013559 | 0.98051 | -0.13619 | 0.98046 | -0.13656 | 5.0218
51 | -0.12785 | -0.032185 | 0.128 | 0.032241 | 0.00014834 | 5.6323e-05 | 0.1931 | 0.1931 | 0.1931 | 0.98543 | -0.10124 | 0.98661 | -0.092947 | 23.8399
52 | 0.12785 | 0.032185 | -0.12762 | -0.032098 | 0.00022868 | 8.6829e-05 | 0.1931 | 0.1931 | 0.1931 | 0.98543 | -0.10124 | 0.98362 | -0.11407 | 23.8399
53 | 0.0030369 | 0.00076067 | -0.0030367 | -0.0007608 | 2.1647e-07 | -1.2791e-07 | 0.0045802 | 0.0045802 | 0.0045802 | 0.98661 | -0.092947 | 0.98654 | -0.093462 | 1.6964
54 | -0.13103 | -0.033002 | 0.13114 | 0.033043 | 0.00010772 | 4.0924e-05 | 0.19768 | 0.19768 | 0.19768 | 0.98661 | -0.092947 | 0.98745 | -0.087071 | 24.4053
55 | 0.12762 | 0.032098 | -0.12758 | -0.032083 | 4.0271e-05 | 1.5291e-05 | 0.1931 | 0.1931 | 0.1931 | 0.98362 | -0.11407 | 0.9833 | -0.11634 | 23.84
56 | -0.01266 | -0.0031727 | 0.012663 | 0.0031737 | 2.8799e-06 | 9.498e-07 | 0.019209 | 0.019209 | 0.019209 | 0.9807 | -0.13481 | 0.98093 | -0.13316 | 7.1143
57 | 0.008659 | 0.00217 | -0.0086572 | -0.0021695 | 1.7913e-06 | 4.7937e-07 | 0.013142 | 0.013142 | 0.013142 | 0.98046 | -0.13656 | 0.98025 | -0.13805 | 4.8673
58 | 0.0016338 | 0.00040919 | -0.0016337 | -0.00040931 | 4.2528e-08 | -1.2695e-07 | 0.0024642 | 0.0024642 | 0.0024642 | 0.98654 | -0.093462 | 0.98651 | -0.09365 | 0.91267
59 | -0.13326 | -0.033574 | 0.13342 | 0.033633 | 0.00015539 | 5.9055e-05 | 0.20088 | 0.20088 | 0.20088 | 0.98745 | -0.087071 | 0.98864 | -0.078746 | 24.7996
60 | 0.12563 | 0.031593 | -0.12561 | -0.031588 | 1.2976e-05 | 4.9253e-06 | 0.19015 | 0.19015 | 0.19015 | 0.9833 | -0.11634 | 0.98319 | -0.11708 | 23.4749
61 | -0.014548 | -0.0036462 | 0.014551 | 0.0036471 | 2.7202e-06 | 9.332e-07 | 0.022069 | 0.022069 | 0.022069 | 0.98093 | -0.13316 | 0.98112 | -0.13181 | 8.1737
62 | 0.0085566 | 0.0021443 | -0.0085557 | -0.0021441 | 8.7044e-07 | 2.3056e-07 | 0.012989 | 0.012989 | 0.012989 | 0.98025 | -0.13805 | 0.98014 | -0.13879 | 4.8107
63 | 0.0012365 | 0.00030976 | -0.0012365 | -0.00030989 | 2.4196e-08 | -1.3302e-07 | 0.0018651 | 0.0018651 | 0.0018651 | 0.98651 | -0.09365 | 0.98649 | -0.093792 | 0.69078
64 | -0.13506 | -0.034045 | 0.13514 | 0.034077 | 8.3725e-05 | 3.1827e-05 | 0.20335 | 0.20335 | 0.20335 | 0.98864 | -0.078746 | 0.98927 | -0.074323 | 25.105
65 | -0.018607 | -0.0046662 | 0.018611 | 0.0046678 | 4.4139e-06 | 1.5848e-06 | 0.028178 | 0.028178 | 0.028178 | 0.98264 | -0.12099 | 0.98288 | -0.11927 | 10.4362
66 | 0.018607 | 0.0046662 | -0.018593 | -0.0046611 | 1.434e-05 | 5.149e-06 | 0.028178 | 0.028178 | 0.028178 | 0.98264 | -0.12099 | 0.98186 | -0.12655 | 10.4362
67 | -0.12334 | -0.031015 | 0.12338 | 0.031029 | 3.7768e-05 | 1.4328e-05 | 0.18677 | 0.18677 | 0.18677 | 0.98288 | -0.11927 | 0.98319 | -0.11708 | 23.0582
68 | 0.10473 | 0.026347 | -0.10466 | -0.02632 | 7.2083e-05 | 2.7201e-05 | 0.15859 | 0.15859 | 0.15859 | 0.98288 | -0.11927 | 0.98218 | -0.12421 | 19.5795
69 | 0.016133 | 0.0040447 | -0.016127 | -0.0040426 | 6.1347e-06 | 2.1516e-06 | 0.024451 | 0.024451 | 0.024451 | 0.98186 | -0.12655 | 0.98147 | -0.1293 | 9.0559
70 | -0.014961 | -0.00375 | 0.014966 | 0.0037515 | 4.4492e-06 | 1.5363e-06 | 0.022691 | 0.022691 | 0.022691 | 0.98112 | -0.13181 | 0.98142 | -0.12967 | 8.4042
71 | 0.0041213 | 0.0010327 | -0.0041212 | -0.0010327 | 5.8902e-08 | -7.7355e-09 | 0.0062567 | 0.0062567 | 0.0062567 | 0.98014 | -0.13879 | 0.98013 | -0.13889 | 2.3173
72 | -0.015488 | -0.0038822 | 0.015489 | 0.0038825 | 7.9711e-07 | 2.7731e-07 | 0.023483 | 0.023483 | 0.023483 | 0.98142 | -0.12967 | 0.98147 | -0.1293 | 8.6973
73 | 0.00052194 | 0.00013068 | -0.00052194 | -0.00013081 | 3.9659e-09 | -1.2672e-07 | 0.00079131 | 0.00079136 | 0.00079136 | 0.98142 | -0.12967 | 0.98141 | -0.12972 | 0.2931
74 | 0.00093509 | 0.00023432 | -0.00093509 | -0.00023436 | 4.1821e-09 | -4.03e-08 | 0.0014197 | 0.0014197 | 0.0014197 | 0.98011 | -0.13901 | 0.98011 | -0.13905 | 0.5258
75 | -0.0012068 | -0.00030241 | 0.0012068 | 0.00030231 | 1.7385e-08 | -9.7914e-08 | 0.0018322 | 0.0018321 | 0.0018322 | 0.98011 | -0.13901 | 0.98013 | -0.13891 | 0.67858
76 | -0.003683 | -0.0009229 | 0.003683 | 0.00092289 | 8.1965e-09 | -2.1429e-09 | 0.0055914 | 0.0055914 | 0.0055914 | 0.98013 | -0.13891 | 0.98013 | -0.13889 | 2.0709
77 | -0.0011351 | -0.00028449 | 0.0011351 | 0.0002843 | 2.8249e-08 | -1.8984e-07 | 0.0017046 | 0.0017045 | 0.0017046 | 0.99089 | -0.063013 | 0.99092 | -0.062833 | 0.63133
78 | -0.0020809 | -0.00052132 | 0.0020811 | 0.00052092 | 2.3023e-07 | -3.9833e-07 | 0.0031247 | 0.0031245 | 0.0031247 | 0.99092 | -0.062833 | 0.99103 | -0.062032 | 1.1573
79 | -0.014643 | -0.0036693 | 0.014646 | 0.0036702 | 2.7376e-06 | 9.4521e-07 | 0.022444 | 0.022444 | 0.022444 | 0.97081 | -0.2055 | 0.971 | -0.20415 | 8.3125
80 | 0.007637 | 0.0019135 | -0.007636 | -0.0019132 | 1.0324e-06 | 2.4779e-07 | 0.011706 | 0.011706 | 0.011706 | 0.97081 | -0.2055 | 0.97067 | -0.20648 | 4.3354
81 | -0.022121 | -0.0055438 | 0.022141 | 0.005551 | 1.9689e-05 | 7.2327e-06 | 0.0339 | 0.0339 | 0.0339 | 0.971 | -0.20415 | 0.97189 | -0.19773 | 12.5554
82 | 0.0041244 | 0.0010331 | -0.0041234 | -0.0010332 | 1.015e-06 | -1.1248e-07 | 0.0063224 | 0.0063226 | 0.0063226 | 0.97067 | -0.20648 | 0.97043 | -0.20826 | 2.3417
83 | -0.022141 | -0.005551 | 0.022163 | 0.0055592 | 2.2299e-05 | 8.1906e-06 | 0.0339 | 0.033899 | 0.0339 | 0.97189 | -0.19773 | 0.9729 | -0.19047 | 12.5554
84 | 0.0041234 | 0.0010332 | -0.0041229 | -0.0010333 | 5.2074e-07 | -5.7598e-08 | 0.0063226 | 0.0063227 | 0.0063227 | 0.97043 | -0.20826 | 0.9703 | -0.20917 | 2.3417
85 | -0.02692 | -0.0067514 | 0.026937 | 0.0067578 | 1.7018e-05 | 6.3456e-06 | 0.041175 | 0.041175 | 0.041175 | 0.9729 | -0.19047 | 0.97353 | -0.18591 | 15.2501
86 | -0.034526 | -0.0086597 | 0.034556 | 0.008671 | 3.0087e-05 | 1.1356e-05 | 0.052774 | 0.052774 | 0.052774 | 0.97353 | -0.18591 | 0.97441 | -0.17963 | 19.546
87 | -0.13593 | -0.034274 | 0.13608 | 0.034331 | 0.0001493 | 5.676e-05 | 0.20453 | 0.20453 | 0.20453 | 0.98927 | -0.074323 | 0.99039 | -0.066493 | 25.2507
88 | -0.138 | -0.034811 | 0.13808 | 0.034844 | 8.6402e-05 | 3.2858e-05 | 0.20741 | 0.20741 | 0.20741 | 0.99039 | -0.066493 | 0.99103 | -0.062032 | 25.6065
89 | -0.14016 | -0.035365 | 0.14019 | 0.035376 | 2.8814e-05 | 1.0961e-05 | 0.21054 | 0.21054 | 0.21054 | 0.99103 | -0.062032 | 0.99124 | -0.060568 | 25.9923
90 | -0.14188 | -0.035799 | 0.14197 | 0.035833 | 8.8173e-05 | 3.3551e-05 | 0.21307 | 0.21307 | 0.21307 | 0.99124 | -0.060568 | 0.99188 | -0.056142 | 26.3053
91 | 0.012545 | 0.0031444 | -0.01254 | -0.0031426 | 5.5163e-06 | 1.795e-06 | 0.018753 | 0.018753 | 0.018753 | 0.99547 | -0.031725 | 0.99501 | -0.034902 | 6.9454
92 | -0.016523 | -0.0041413 | 0.016533 | 0.0041448 | 1.004e-05 | 3.5182e-06 | 0.024698 | 0.024698 | 0.024698 | 0.99547 | -0.031725 | 0.99609 | -0.027339 | 9.1476
93 | 0.010024 | 0.0025121 | -0.010021 | -0.0025112 | 3.1608e-06 | 9.23e-07 | 0.01499 | 0.01499 | 0.01499 | 0.99501 | -0.034902 | 0.99469 | -0.03718 | 5.552
94 | -0.082203 | -0.020621 | 0.082345 | 0.020674 | 0.00014252 | 5.3039e-05 | 0.12281 | 0.1228 | 0.12281 | 0.99609 | -0.027339 | 0.99787 | -0.014859 | 15.1612
95 | 0.06567 | 0.016476 | -0.065541 | -0.016429 | 0.00012865 | 4.6978e-05 | 0.098107 | 0.098108 | 0.098108 | 0.99609 | -0.027339 | 0.99408 | -0.041487 | 12.1121
96 | 0.0076479 | 0.0019165 | -0.0076464 | -0.0019162 | 1.4948e-06 | 3.3742e-07 | 0.011441 | 0.011441 | 0.011441 | 0.99469 | -0.03718 | 0.99449 | -0.038592 | 4.2374
97 | -0.083693 | -0.021012 | 0.083738 | 0.021028 | 4.4515e-05 | 1.6583e-05 | 0.12482 | 0.12482 | 0.12482 | 0.99787 | -0.014859 | 0.99842 | -0.011032 | 15.4093
98 | 0.0054384 | 0.0013601 | -0.0054362 | -0.0013599 | 2.1283e-06 | 1.5145e-07 | 0.0081396 | 0.0081398 | 0.0081398 | 0.99408 | -0.041487 | 0.99368 | -0.044325 | 3.0148
99 | 0.060103 | 0.015069 | -0.060038 | -0.015045 | 6.5051e-05 | 2.3519e-05 | 0.089969 | 0.089969 | 0.089969 | 0.99408 | -0.041487 | 0.99297 | -0.049307 | 11.1073
100 | 0.0050649 | 0.0012692 | -0.005064 | -0.0012692 | 8.9485e-07 | 2.025e-08 | 0.0075784 | 0.0075785 | 0.0075785 | 0.99449 | -0.038592 | 0.99431 | -0.039869 | 2.8068
101 | -0.08623 | -0.021653 | 0.086362 | 0.021702 | 0.0001324 | 4.9409e-05 | 0.12853 | 0.12853 | 0.12853 | 0.99842 | -0.011032 | 1 | 0 | 15.8678
102 | 0.002492 | 0.00062438 | -0.0024918 | -0.00062451 | 1.1607e-07 | -1.3172e-07 | 0.0037139 | 0.003714 | 0.003714 | 0.99842 | -0.011032 | 0.99837 | -0.011369 | 1.3755
103 | 0.0047427 | 0.0011861 | -0.0047427 | -0.0011861 | 7.3646e-08 | -1.9912e-09 | 0.0071013 | 0.0071013 | 0.0071013 | 0.99368 | -0.044325 | 0.99366 | -0.044438 | 2.6301
104 | 0.058961 | 0.014776 | -0.0589 | -0.014754 | 6.0886e-05 | 2.1964e-05 | 0.088356 | 0.088357 | 0.088357 | 0.99297 | -0.049307 | 0.99191 | -0.056775 | 10.9082
105 | 0.15219 | 0.038548 | -0.15178 | -0.03839 | 0.00041499 | 0.00015809 | 0.22661 | 0.22661 | 0.22661 | 1 | 0 | 0.99719 | -0.019334 | 27.9761
106 | 0.003765 | 0.00094111 | -0.0037646 | -0.00094122 | 4.0882e-07 | -1.0978e-07 | 0.0056372 | 0.0056373 | 0.0056373 | 0.99366 | -0.044438 | 0.99355 | -0.045226 | 2.0879
107 | 0.058361 | 0.014619 | -0.058331 | -0.014608 | 3.0462e-05 | 1.0977e-05 | 0.087548 | 0.087548 | 0.087548 | 0.99191 | -0.056775 | 0.99137 | -0.060551 | 10.8084
108 | -0.0005491 | -0.00013762 | 0.00054912 | 0.00013703 | 1.9229e-08 | -5.9148e-07 | 0.0008194 | 0.00081919 | 0.0008194 | 0.99715 | -0.019588 | 0.99719 | -0.019334 | 0.30348
109 | 0.15123 | 0.038253 | -0.15088 | -0.038123 | 0.00034272 | 0.00013055 | 0.22579 | 0.22579 | 0.22579 | 0.99719 | -0.019334 | 0.99486 | -0.035439 | 27.875
110 | 0.15088 | 0.038123 | -0.15086 | -0.038114 | 2.2172e-05 | 8.4463e-06 | 0.22579 | 0.22579 | 0.22579 | 0.99486 | -0.035439 | 0.99471 | -0.036484 | 27.875
111 | 0.14689 | 0.037118 | -0.14661 | -0.037012 | 0.00027944 | 0.00010639 | 0.21984 | 0.21984 | 0.21984 | 0.99471 | -0.036484 | 0.99276 | -0.050026 | 27.1412
112 | -0.0031794 | -0.00079685 | 0.00318 | 0.00079657 | 5.9663e-07 | -2.7781e-07 | 0.0048507 | 0.0048505 | 0.0048507 | 0.97535 | -0.17302 | 0.97554 | -0.17166 | 1.7965
113 | -0.006917 | -0.0017331 | 0.0069181 | 0.0017334 | 1.042e-06 | 2.1344e-07 | 0.010551 | 0.010551 | 0.010551 | 0.97554 | -0.17166 | 0.97569 | -0.17057 | 3.9076
114 | 0.14428 | 0.036429 | -0.14416 | -0.036382 | 0.00012388 | 4.7154e-05 | 0.21636 | 0.21636 | 0.21636 | 0.99276 | -0.050026 | 0.99188 | -0.056142 | 26.7107
115 | -0.010306 | -0.0025816 | 0.010311 | 0.002583 | 4.5904e-06 | 1.3935e-06 | 0.015717 | 0.015717 | 0.015717 | 0.97569 | -0.17057 | 0.97614 | -0.16735 | 5.8212
116 | 0.003388 | 0.00084826 | -0.0033877 | -0.00084835 | 2.4854e-07 | -9.0735e-08 | 0.0051667 | 0.0051668 | 0.0051668 | 0.97569 | -0.17057 | 0.97561 | -0.17111 | 1.9136
117 | -0.0033573 | -0.00083976 | 0.0033582 | 0.00083937 | 8.867e-07 | -3.8644e-07 | 0.005029 | 0.0050287 | 0.005029 | 0.99328 | -0.047143 | 0.99355 | -0.045226 | 1.8626
118 | 0.0033573 | 0.00083976 | -0.0033571 | -0.00083986 | 2.3814e-07 | -1.0371e-07 | 0.005029 | 0.0050291 | 0.0050291 | 0.99328 | -0.047143 | 0.9932 | -0.047657 | 1.8626
119 | -0.0010722 | -0.00026873 | 0.0010723 | 0.00026829 | 6.1533e-08 | -4.3657e-07 | 0.0016356 | 0.0016354 | 0.0016356 | 0.97548 | -0.17209 | 0.97553 | -0.17167 | 0.60578
120 | -0.0016174 | -0.0004049 | 0.0016174 | 0.00040488 | 6.9282e-09 | -2.0115e-08 | 0.0024669 | 0.0024669 | 0.0024669 | 0.97553 | -0.17167 | 0.97554 | -0.17164 | 0.91365
121 | -0.0025552 | -0.00063992 | 0.0025554 | 0.00063974 | 1.8883e-07 | -1.7614e-07 | 0.0038973 | 0.0038972 | 0.0038973 | 0.97554 | -0.17164 | 0.97561 | -0.17111 | 1.4435
122 | 0.10363 | 0.026061 | -0.10341 | -0.025981 | 0.00021326 | 8.0449e-05 | 0.15703 | 0.15703 | 0.15703 | 0.98218 | -0.12421 | 0.9801 | -0.13901 | 19.3862
123 | 0.068611 | 0.017247 | -0.068584 | -0.017237 | 2.667e-05 | 9.8111e-06 | 0.10419 | 0.10419 | 0.10419 | 0.9801 | -0.13901 | 0.97971 | -0.1418 | 12.8624
124 | 0.034803 | 0.0087334 | -0.034756 | -0.0087156 | 4.695e-05 | 1.7718e-05 | 0.052843 | 0.052843 | 0.052843 | 0.9801 | -0.13901 | 0.97873 | -0.14874 | 19.5715
125 | 0.065967 | 0.016582 | -0.065882 | -0.016549 | 8.4991e-05 | 3.2006e-05 | 0.10021 | 0.10021 | 0.10021 | 0.97971 | -0.1418 | 0.9784 | -0.15106 | 18.5575
126 | 0.028983 | 0.0072688 | -0.028957 | -0.007259 | 2.6239e-05 | 9.82e-06 | 0.044066 | 0.044066 | 0.044066 | 0.97873 | -0.14874 | 0.97782 | -0.15528 | 16.3208
127 | 0.062866 | 0.015794 | -0.062856 | -0.01579 | 1.0301e-05 | 3.9392e-06 | 0.095624 | 0.095624 | 0.095624 | 0.9784 | -0.15106 | 0.97824 | -0.15224 | 35.4163
128 | 0.022846 | 0.0057274 | -0.022829 | -0.0057211 | 1.7148e-05 | 6.3105e-06 | 0.034767 | 0.034767 | 0.034767 | 0.97782 | -0.15528 | 0.97706 | -0.1607 | 12.8765
129 | 0.060716 | 0.015254 | -0.060572 | -0.015198 | 0.00014422 | 5.5132e-05 | 0.09237 | 0.09237 | 0.09237 | 0.97824 | -0.15224 | 0.97584 | -0.16936 | 34.2111
130 | 0.0070709 | 0.0017717 | -0.0070681 | -0.0017711 | 2.8383e-06 | 6.0059e-07 | 0.010768 | 0.010769 | 0.010769 | 0.97706 | -0.1607 | 0.97666 | -0.1636 | 3.9884
131 | 0.015758 | 0.0039493 | -0.015752 | -0.0039474 | 5.4512e-06 | 1.9067e-06 | 0.023998 | 0.023998 | 0.023998 | 0.97706 | -0.1607 | 0.97671 | -0.1632 | 8.8883
132 | 0.0070102 | 0.0017563 | -0.0070101 | -0.0017563 | 1.0859e-07 | 2.2851e-08 | 0.010705 | 0.010705 | 0.010705 | 0.97441 | -0.17963 | 0.97439 | -0.17974 | 3.9649
133 | -0.041566 | -0.010427 | 0.041621 | 0.010448 | 5.5138e-05 | 2.0933e-05 | 0.063479 | 0.063479 | 0.063479 | 0.97441 | -0.17963 | 0.97574 | -0.17008 | 23.5108
134 | 0.048465 | 0.012164 | -0.04846 | -0.012162 | 4.8476e-06 | 1.8467e-06 | 0.073908 | 0.073908 | 0.073908 | 0.97584 | -0.16936 | 0.97574 | -0.17008 | 27.3733
135 | 0.001904 | 0.00047659 | -0.0019039 | -0.00047689 | 1.5185e-07 | -3.0012e-07 | 0.0029075 | 0.0029076 | 0.0029076 | 0.97439 | -0.17974 | 0.97431 | -0.18032 | 1.0769
136 | 0.004054 | 0.0010157 | -0.0040536 | -0.0010158 | 3.9626e-07 | -5.5879e-08 | 0.0061765 | 0.0061765 | 0.0061765 | 0.97666 | -0.1636 | 0.97656 | -0.16431 | 2.2876
137 | 0.0131 | 0.0032826 | -0.013092 | -0.0032801 | 7.5319e-06 | 2.5178e-06 | 0.019957 | 0.019957 | 0.019957 | 0.97671 | -0.1632 | 0.97614 | -0.16735 | 7.3915
138 | 0.0016152 | 0.00040465 | -0.0016151 | -0.00040479 | 4.7143e-08 | -1.3793e-07 | 0.002461 | 0.0024611 | 0.0024611 | 0.97656 | -0.16431 | 0.97653 | -0.16452 | 0.91152
139 | 0.0019039 | 0.00047689 | -0.0019038 | -0.00047713 | 1.1996e-07 | -2.3702e-07 | 0.0029076 | 0.0029077 | 0.0029077 | 0.97431 | -0.18032 | 0.97425 | -0.18077 | 1.0769

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24621 | 0.06197

## res_load
| p_mw | q_mvar
0 | 0.0024262 | 0.00060807
1 | 0.0011894 | 0.0002981
2 | 0.0016934 | 0.00042441
3 | 0.0011425 | 0.00028633
4 | 0.0017644 | 0.00044219
5 | 0.00098481 | 0.00024682
6 | 0.001129 | 0.00028297
7 | 0.00095375 | 0.00023903
8 | 0.0019312 | 0.000484
9 | 0.0012834 | 0.00032166
10 | 0.0012504 | 0.00031338
11 | 0.0010083 | 0.0002527
12 | 0.0013241 | 0.00033186
13 | 0.0017321 | 0.00043411
14 | 0.00082502 | 0.00020677
15 | 0.0018744 | 0.00046976
16 | 0.0021173 | 0.00053065
17 | 0.0012305 | 0.00030839
18 | 0.0016701 | 0.00041857
19 | 0.0011653 | 0.00029204
20 | 0.0016197 | 0.00040594
21 | 0.0019312 | 0.000484
22 | 0.0020715 | 0.00051917
23 | 0.0014806 | 0.00037106
24 | 0.0016367 | 0.0004102
25 | 0.0017204 | 0.00043116
26 | 0.0014848 | 0.00037212
27 | 0.0014316 | 0.00035879
28 | 0.0010771 | 0.00026996
29 | 0.0020988 | 0.00052601
30 | 0.0075089 | 0.0018819
31 | 0.00061312 | 0.00015366
32 | 0.00094841 | 0.0002377
33 | 0.00081487 | 0.00020423
34 | 0.00065593 | 0.00016439
35 | 0.0010784 | 0.00027026
36 | 0.00095942 | 0.00024045
37 | 0.001463 | 0.00036665
38 | 0.00033626 | 8.4275e-05
39 | 0.0031771 | 0.00079625
40 | 0.00054581 | 0.00013679
41 | 0.00027492 | 6.8901e-05
42 | 0.0014029 | 0.00035161
43 | 0.0021195 | 0.00053121
44 | 0.0019539 | 0.00048969
45 | 0.0018855 | 0.00047255
46 | 0.00010061 | 2.5215e-05
47 | 0.00039722 | 9.9554e-05
48 | 0.0016438 | 0.00041197
49 | 0.0024593 | 0.00061636
50 | 0.0022305 | 0.00055902
51 | 0.00041044 | 0.00010287
52 | 0.0044344 | 0.0011114
53 | 0.00063865 | 0.00016006
54 | 0.00052194 | 0.00013081
55 | 0.00027171 | 6.8096e-05
56 | 0.00093509 | 0.00023436
57 | 0.0024762 | 0.00062058
58 | 0.00043826 | 0.00010984
59 | 0.0012365 | 0.00030989
60 | 0.0011351 | 0.00028449
61 | 0.00094574 | 0.00023702
62 | 0.0070058 | 0.0017558
63 | 0.0074755 | 0.0018735
64 | 0.0035116 | 0.00088009
65 | 0.0047571 | 0.0011922
66 | 0.0041229 | 0.0010333
67 | 0.0075887 | 0.0019019
68 | 0.00078472 | 0.00019667
69 | 0.0019185 | 0.00048082
70 | 0.0016891 | 0.00042333
71 | 0.0039777 | 0.00099691
72 | 0.0025159 | 0.00063054
73 | 0.0023726 | 0.00059464
74 | 0.0013483 | 0.00033793
75 | 0.0025815 | 0.00064699
76 | 0.00069352 | 0.00017381
77 | 0.0010763 | 0.00026973
78 | 0.005064 | 0.0012692
79 | 0.0024918 | 0.00062451
80 | 0.0068594 | 0.0017191
81 | 0.00097766 | 0.00024503
82 | 0.00053916 | 0.00013513
83 | 0.00099678 | 0.00024982
84 | 0.0005491 | 0.00013762
85 | 0.0039735 | 0.00099586
86 | 0.0031794 | 0.00079685
87 | 0.003737 | 0.00093658
88 | 0.0023268 | 0.00058316
89 | 0.0021889 | 0.00054859
90 | 0.00040636 | 0.00010184
91 | 0.0005981 | 0.0001499
92 | 0.0010722 | 0.00026873
93 | 0.00054507 | 0.00013661
94 | 0.00093781 | 0.00023504
95 | 0.00083236 | 0.00020861
96 | 0.0010335 | 0.00025901
97 | 0.0026172 | 0.00065594
98 | 0.005773 | 0.0014469
99 | 0.0030158 | 0.00075584
100 | 0.0061111 | 0.0015316
101 | 0.0021394 | 0.00053618
102 | 0.012107 | 0.0030344
103 | 0.0068385 | 0.0017139
104 | 0.0051061 | 0.0012797
105 | 0.0030141 | 0.0007554
106 | 0.0026526 | 0.00066481
107 | 0.0024384 | 0.00061113
108 | 0.0027815 | 0.0006971
109 | 0.0019038 | 0.00047713
110 | 0.0016151 | 0.00040479

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1