## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1100-3_1_2_node_27 | 0.4 | n |  | TRUE
1 | bus_LV_1100-3_1_2_node_28 | 0.4 | n |  | TRUE
2 | bus_LV_1100-3_1_2_node_69 | 0.4 | n |  | TRUE
3 | bus_LV_1100-3_1_2_node_65 | 0.4 | n |  | TRUE
4 | bus_LV_1100-3_1_2_node_63 | 0.4 | n |  | TRUE
5 | bus_LV_1100-3_1_2_node_64 | 0.4 | n |  | TRUE
6 | bus_LV_1100-3_1_2_node_66 | 0.4 | n |  | TRUE
7 | bus_LV_1100-3_1_2_node_67 | 0.4 | n |  | TRUE
8 | bus_LV_1100-3_1_2_node_68 | 0.4 | n |  | TRUE
9 | bus_LV_1100-3_1_2_node_85 | 0.4 | n |  | TRUE
10 | bus_LV_1100-3_1_2_node_84 | 0.4 | n |  | TRUE
11 | bus_LV_1100-3_1_2_node_70 | 0.4 | n |  | TRUE
12 | bus_LV_1100-3_1_2_node_71 | 0.4 | n |  | TRUE
13 | bus_LV_1100-3_1_2_node_72 | 0.4 | n |  | TRUE
14 | bus_LV_1100-3_1_2_node_73 | 0.4 | n |  | TRUE
15 | bus_LV_1100-3_1_2_node_74 | 0.4 | n |  | TRUE
16 | bus_LV_1100-3_1_2_node_75 | 0.4 | n |  | TRUE
17 | bus_LV_1100-3_1_2_node_76 | 0.4 | n |  | TRUE
18 | bus_LV_1100-3_1_2_node_79 | 0.4 | n |  | TRUE
19 | bus_LV_1100-3_1_2_node_81 | 0.4 | n |  | TRUE
20 | bus_LV_1100-3_1_2_node_77 | 0.4 | n |  | TRUE
21 | bus_LV_1100-3_1_2_node_78 | 0.4 | n |  | TRUE
22 | bus_LV_1100-3_1_2_node_88 | 0.4 | n |  | TRUE
23 | bus_LV_1100-3_1_2_node_80 | 0.4 | n |  | TRUE
24 | bus_LV_1100-3_1_2_node_82 | 0.4 | n |  | TRUE
25 | bus_LV_1100-3_1_2_node_83 | 0.4 | n |  | TRUE
26 | bus_LV_1100-3_1_2_node_86 | 0.4 | n |  | TRUE
27 | bus_LV_1100-3_1_2_node_93 | 0.4 | n |  | TRUE
28 | bus_LV_1100-3_1_2_node_87 | 0.4 | n |  | TRUE
29 | bus_LV_1100-3_1_2_node_90 | 0.4 | n |  | TRUE
30 | bus_LV_1100-3_1_2_node_91 | 0.4 | n |  | TRUE
31 | bus_LV_1100-3_1_2_node_92 | 0.4 | n |  | TRUE
32 | bus_LV_1100-3_1_2_node_98 | 0.4 | n |  | TRUE
33 | bus_LV_1100-3_1_2_node_94 | 0.4 | n |  | TRUE
34 | bus_LV_1100-3_1_2_node_95 | 0.4 | n |  | TRUE
35 | bus_LV_1100-3_1_2_node_96 | 0.4 | n |  | TRUE
36 | bus_LV_1100-3_1_2_node_97 | 0.4 | n |  | TRUE
37 | bus_MV_0_node_68 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1100-3_1_2_load_27 | 0 | 0.001626 | 0.00040752 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1100-3_1_2_load_63 | 4 | 0.0027478 | 0.00068867 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1100-3_1_2_load_64 | 5 | 0.0017477 | 0.00043803 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1100-3_1_2_load_66 | 6 | 0.0001291 | 3.2355e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1100-3_1_2_load_67 | 7 | 0.00059551 | 0.00014925 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1100-3_1_2_load_68 | 8 | 0.0002309 | 5.7869e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1100-3_1_2_load_84 | 10 | 0.00010914 | 2.7353e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1100-3_1_2_load_70 | 11 | 3.9135e-05 | 9.8083e-06 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1100-3_1_2_load_71 | 12 | 0.00013564 | 3.3995e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1100-3_1_2_load_73 | 14 | 0.00048488 | 0.00012152 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1100-3_1_2_load_74 | 15 | 0.00010944 | 2.7429e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1100-3_1_2_load_75 | 16 | 0.0002225 | 5.5765e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1100-3_1_2_load_76 | 17 | 0.00028418 | 7.1221e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1100-3_1_2_load_79 | 18 | 0.00042751 | 0.00010714 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1100-3_1_2_load_81 | 19 | 8.4943e-05 | 2.1289e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1100-3_1_2_load_77 | 20 | 0.00023335 | 5.8482e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1100-3_1_2_load_78 | 21 | 0.00057369 | 0.00014378 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1100-3_1_2_load_80 | 23 | 0.00052715 | 0.00013212 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1100-3_1_2_load_82 | 24 | 4.1232e-05 | 1.0334e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1100-3_1_2_load_83 | 25 | 0.00030617 | 7.6734e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1100-3_1_2_load_86 | 26 | 4.8265e-05 | 1.2096e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1100-3_1_2_load_93 | 27 | 0.00049837 | 0.0001249 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1100-3_1_2_load_87 | 28 | 0.0001588 | 3.9799e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1100-3_1_2_load_90 | 29 | 0.00012757 | 3.1972e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1100-3_1_2_load_91 | 30 | 0.0003057 | 7.6617e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1100-3_1_2_load_94 | 33 | 6.3197e-05 | 1.5839e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1100-3_1_2_load_95 | 34 | 0.00019881 | 4.9826e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1100-3_1_2_load_96 | 35 | 0.00074466 | 0.00018663 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1100-3_1_2_load_97 | 36 | 0.00015157 | 3.7986e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1100-3_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0025839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1100-3_1_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.004373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1100-3_1_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.031654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1100-3_1_2_line_3 | NAYY 4x150 SE | 2 | 10 | 0.027117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1100-3_1_2_line_4 | NAYY 4x150 SE | 3 | 6 | 0.03117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1100-3_1_2_line_5 | NAYY 4x150 SE | 3 | 5 | 0.1215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1100-3_1_2_line_6 | NAYY 4x150 SE | 4 | 5 | 0.065455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1100-3_1_2_line_7 | NAYY 4x150 SE | 6 | 7 | 0.063522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1100-3_1_2_line_8 | NAYY 4x150 SE | 7 | 8 | 0.017677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1100-3_1_2_line_9 | NAYY 4x150 SE | 8 | 9 | 0.3226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1100-3_1_2_line_10 | NAYY 4x150 SE | 9 | 26 | 0.053935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1100-3_1_2_line_11 | NAYY 4x150 SE | 10 | 25 | 0.02958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1100-3_1_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.011238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1100-3_1_2_line_13 | NAYY 4x150 SE | 11 | 13 | 0.02142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1100-3_1_2_line_14 | NAYY 4x150 SE | 12 | 14 | 0.014115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1100-3_1_2_line_15 | NAYY 4x150 SE | 13 | 15 | 0.11651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1100-3_1_2_line_16 | NAYY 4x150 SE | 13 | 16 | 0.034583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1100-3_1_2_line_17 | NAYY 4x150 SE | 14 | 17 | 0.015935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1100-3_1_2_line_18 | NAYY 4x150 SE | 15 | 18 | 0.0068255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1100-3_1_2_line_19 | NAYY 4x150 SE | 16 | 19 | 0.012213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1100-3_1_2_line_20 | NAYY 4x150 SE | 17 | 20 | 0.09458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1100-3_1_2_line_21 | NAYY 4x150 SE | 19 | 23 | 0.0054772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1100-3_1_2_line_22 | NAYY 4x150 SE | 20 | 21 | 0.033718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1100-3_1_2_line_23 | NAYY 4x150 SE | 21 | 22 | 0.037137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1100-3_1_2_line_24 | NAYY 4x150 SE | 22 | 28 | 0.11505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1100-3_1_2_line_25 | NAYY 4x150 SE | 23 | 24 | 0.0056244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1100-3_1_2_line_26 | NAYY 4x150 SE | 24 | 25 | 0.028289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1100-3_1_2_line_27 | NAYY 4x150 SE | 26 | 27 | 0.074832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1100-3_1_2_line_28 | NAYY 4x150 SE | 27 | 30 | 0.0051136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1100-3_1_2_line_29 | NAYY 4x150 SE | 29 | 30 | 0.030124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1100-3_1_2_line_30 | NAYY 4x150 SE | 29 | 31 | 0.1078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1100-3_1_2_line_31 | NAYY 4x150 SE | 31 | 32 | 0.33086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1100-3_1_2_line_32 | NAYY 4x150 SE | 32 | 35 | 0.078164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1100-3_1_2_line_33 | NAYY 4x150 SE | 33 | 34 | 0.033205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1100-3_1_2_line_34 | NAYY 4x150 SE | 33 | 35 | 0.0079495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1100-3_1_2_line_35 | NAYY 4x150 SE | 34 | 36 | 0.00035212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1100-3_1_2_trafo_68 | 0.25 MVA 20/0.4 kV | 37 | 8 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2651443.5719 | 1230677.8468 | 2651441.7806 | 1230679.709
1 | 2651447.4242 | 1230679.937 | 2651443.5719 | 1230677.8468
2 | 2651464.8763 | 1230654.3828 | 2651443.5719 | 1230677.8468
3 | 2651447.4242 | 1230679.937 | 2651471.241 | 1230692.9029
4 | 2651464.8763 | 1230654.3828 | 2651485.8269 | 1230631.3036
5 | 2651464.8763 | 1230654.3828 | 2651413.2312 | 1230607.6734 | 2651403.1369 | 1230597.8022 | 2651397.1401 | 1230584.4308 | 2651394.2597 | 1230561.5223
6 | 2651392.6849 | 1230496.7832 | 2651390.2945 | 1230504.51 | 2651389.1885 | 1230521.1888 | 2651394.2597 | 1230561.5223
7 | 2651485.8269 | 1230631.3036 | 2651504.2814 | 1230610.9741 | 2651517.5518 | 1230591.6879 | 2651523.6986 | 1230580.6263
8 | 2651531.2961 | 1230564.6804 | 2651526.1538 | 1230576.2081 | 2651523.6986 | 1230580.6263
9 | 2651531.2961 | 1230564.6804 | 2651640.6086 | 1230261.1676
10 | 2651640.6086 | 1230261.1676 | 2651667.4894 | 1230237.7862 | 2651682.6873 | 1230227.5772
11 | 2651471.241 | 1230692.9029 | 2651497.2206 | 1230707.0463
12 | 2651593.9784 | 1230751.3969 | 2651600.511 | 1230751.4635 | 2651605.1734 | 1230750.8337
13 | 2651572.9166 | 1230748.2555 | 2651585.8112 | 1230751.3137 | 2651593.9784 | 1230751.3969
14 | 2651605.1734 | 1230750.8337 | 2651612.1885 | 1230749.886 | 2651618.7927 | 1230747.4575
15 | 2651572.9166 | 1230748.2555 | 2651571.0176 | 1230756.7556 | 2651574.3195 | 1230797.8325 | 2651577.1715 | 1230820.049 | 2651582.5382 | 1230834.3824 | 2651595.0201 | 1230860.4299
16 | 2651572.9166 | 1230748.2555 | 2651542.543 | 1230731.72
17 | 2651630.3227 | 1230736.5571 | 2651619.5436 | 1230747.1814 | 2651618.7927 | 1230747.4575
18 | 2651597.9697 | 1230866.5851 | 2651595.0201 | 1230860.4299
19 | 2651531.8164 | 1230725.8804 | 2651542.543 | 1230731.72
20 | 2651630.3227 | 1230736.5571 | 2651630.3227 | 1230736.5571 | 2651647.8406 | 1230713.9615 | 2651667.5392 | 1230691.4516 | 2651679.9348 | 1230680.4856 | 2651692.2947 | 1230676.2347 | 2651698.6135 | 1230674.9068
21 | 2651527.0059 | 1230723.2616 | 2651531.8164 | 1230725.8804
22 | 2651731.5461 | 1230667.6745 | 2651706.4689 | 1230673.256 | 2651698.6135 | 1230674.9068
23 | 2651767.6594 | 1230670.6753 | 2651762.019 | 1230667.8022 | 2651752.909 | 1230665.8773 | 2651736.323 | 1230666.6113 | 2651731.5461 | 1230667.6745
24 | 2651767.6594 | 1230670.6753 | 2651771.0392 | 1230683.524 | 2651769.7943 | 1230696.01 | 2651766.282 | 1230707.0864 | 2651754.7923 | 1230722.7408 | 2651747.9638 | 1230738.9028 | 2651744.185 | 1230754.5021 | 2651742.0828 | 1230777.6207 | 2651742.3058 | 1230778.9712
25 | 2651527.0059 | 1230723.2616 | 2651522.066 | 1230720.5723
26 | 2651497.2206 | 1230707.0463 | 2651522.066 | 1230720.5723
27 | 2651750.4506 | 1230196.6438 | 2651733.7099 | 1230201.7054 | 2651694.1562 | 1230219.8731 | 2651682.6873 | 1230227.5772
28 | 2651750.4506 | 1230196.6438 | 2651755.3453 | 1230195.1638
29 | 2651784.1798 | 1230186.4457 | 2651755.3453 | 1230195.1638
30 | 2651887.3657 | 1230155.2472 | 2651784.1798 | 1230186.4457
31 | 2651887.3657 | 1230155.2472 | 2652085.1513 | 1230420.4765
32 | 2652085.1513 | 1230420.4765 | 2652140.6909 | 1230378.5252 | 2652147.3978 | 1230373.2046
33 | 2652153.6256 | 1230368.2641 | 2652179.639 | 1230347.6274
34 | 2652153.6256 | 1230368.2641 | 2652147.3978 | 1230373.2046
35 | 2652179.9149 | 1230347.4086 | 2652179.639 | 1230347.6274

## bus_geodata
| x | y | coords
0 | 2651441.7806 | 1230679.709
1 | 2651443.5719 | 1230677.8468
2 | 2651447.4242 | 1230679.937
3 | 2651464.8763 | 1230654.3828
4 | 2651392.6849 | 1230496.7832
5 | 2651394.2597 | 1230561.5223
6 | 2651485.8269 | 1230631.3036
7 | 2651523.6986 | 1230580.6263
8 | 2651531.2961 | 1230564.6804
9 | 2651640.6086 | 1230261.1676
10 | 2651471.241 | 1230692.9029
11 | 2651593.9784 | 1230751.3969
12 | 2651605.1734 | 1230750.8337
13 | 2651572.9166 | 1230748.2555
14 | 2651618.7927 | 1230747.4575
15 | 2651595.0201 | 1230860.4299
16 | 2651542.543 | 1230731.72
17 | 2651630.3227 | 1230736.5571
18 | 2651597.9697 | 1230866.5851
19 | 2651531.8164 | 1230725.8804
20 | 2651698.6135 | 1230674.9068
21 | 2651731.5461 | 1230667.6745
22 | 2651767.6594 | 1230670.6753
23 | 2651527.0059 | 1230723.2616
24 | 2651522.066 | 1230720.5723
25 | 2651497.2206 | 1230707.0463
26 | 2651682.6873 | 1230227.5772
27 | 2651750.4506 | 1230196.6438
28 | 2651742.3058 | 1230778.9712
29 | 2651784.1798 | 1230186.4457
30 | 2651755.3453 | 1230195.1638
31 | 2651887.3657 | 1230155.2472
32 | 2652085.1513 | 1230420.4765
33 | 2652153.6256 | 1230368.2641
34 | 2652179.639 | 1230347.6274
35 | 2652147.3978 | 1230373.2046
36 | 2652179.9149 | 1230347.4086
37 | 2651531.2961 | 1230564.6804

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99814 | -0.013145 | 0.001626 | 0.00040752
1 | 0.99815 | -0.013102 | 0 | 0
2 | 0.99812 | -0.013269 | 0 | 0
3 | 0.99839 | -0.011383 | 0 | 0
4 | 0.99735 | -0.018677 | 0.0027478 | 0.00068867
5 | 0.99761 | -0.016871 | 0.0017477 | 0.00043803
6 | 0.99883 | -0.008281 | 0.0001291 | 3.2355e-05
7 | 0.99973 | -0.0018839 | 0.00059551 | 0.00014925
8 | 1 | 0 | -0.01355 | -0.0031731
9 | 0.99902 | -0.0071687 | 0 | 0
10 | 0.99798 | -0.0143 | 0.00010914 | 2.7353e-05
11 | 0.99742 | -0.018306 | 3.9135e-05 | 9.8083e-06
12 | 0.99739 | -0.018521 | 0.00013564 | 3.3995e-05
13 | 0.99747 | -0.017889 | 0 | 0
14 | 0.99735 | -0.018771 | 0.00048488 | 0.00012152
15 | 0.99739 | -0.018524 | 0.00010944 | 2.7429e-05
16 | 0.9976 | -0.017024 | 0.0002225 | 5.5765e-05
17 | 0.99732 | -0.018975 | 0.00028418 | 7.1221e-05
18 | 0.99738 | -0.018553 | 0.00042751 | 0.00010714
19 | 0.99764 | -0.016691 | 8.4943e-05 | 2.1289e-05
20 | 0.99719 | -0.019913 | 0.00023335 | 5.8482e-05
21 | 0.99716 | -0.020167 | 0.00057369 | 0.00014378
22 | 0.99715 | -0.020231 | 0 | 0
23 | 0.99766 | -0.016537 | 0.00052715 | 0.00013212
24 | 0.99769 | -0.016349 | 4.1232e-05 | 1.0334e-05
25 | 0.99782 | -0.015392 | 0.00030617 | 7.6734e-05
26 | 0.99885 | -0.0083587 | 4.8265e-05 | 1.2096e-05
27 | 0.99863 | -0.0099696 | 0.00049837 | 0.0001249
28 | 0.99712 | -0.020421 | 0.0001588 | 3.9799e-05
29 | 0.99856 | -0.010458 | 0.00012757 | 3.1972e-05
30 | 0.99862 | -0.010054 | 0.0003057 | 7.6617e-05
31 | 0.99838 | -0.011761 | 0 | 0
32 | 0.99784 | -0.015693 | 0 | 0
33 | 0.9977 | -0.01664 | 6.3197e-05 | 1.5839e-05
34 | 0.99769 | -0.016757 | 0.00019881 | 4.9826e-05
35 | 0.99771 | -0.016606 | 0.00074466 | 0.00018663
36 | 0.99769 | -0.016757 | 0.00015157 | 3.7986e-05
37 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.001626 | -0.00040752 | 0.001626 | 0.00040749 | 9.4743e-09 | -3.013e-08 | 0.002424 | 0.002424 | 0.002424 | 0.99814 | -0.013145 | 0.99815 | -0.013102 | 0.89779
1 | 0.0037404 | 0.00092976 | -0.0037403 | -0.00092978 | 8.4762e-08 | -2.4556e-08 | 0.0055734 | 0.0055734 | 0.0055734 | 0.99815 | -0.013102 | 0.99812 | -0.013269 | 2.0642
2 | -0.0053664 | -0.0013372 | 0.0053676 | 0.0013373 | 1.2633e-06 | 7.2041e-08 | 0.0079974 | 0.0079973 | 0.0079974 | 0.99815 | -0.013102 | 0.99839 | -0.011383 | 2.962
3 | 0.0037403 | 0.00092978 | -0.0037397 | -0.00092993 | 5.2563e-07 | -1.5221e-07 | 0.0055734 | 0.0055735 | 0.0055735 | 0.99812 | -0.013269 | 0.99798 | -0.0143 | 2.0643
4 | -0.0098673 | -0.0024632 | 0.0098715 | 0.0024644 | 4.2047e-06 | 1.2094e-06 | 0.014703 | 0.014703 | 0.014703 | 0.99839 | -0.011383 | 0.99883 | -0.008281 | 5.4456
5 | 0.0044997 | 0.0011258 | -0.0044963 | -0.0011261 | 3.4094e-06 | -2.7626e-07 | 0.0067058 | 0.0067063 | 0.0067063 | 0.99839 | -0.011383 | 0.99761 | -0.016871 | 2.4838
6 | -0.0027478 | -0.00068867 | 0.0027485 | 0.00068808 | 6.8643e-07 | -5.9038e-07 | 0.0040997 | 0.0040994 | 0.0040997 | 0.99735 | -0.018677 | 0.99761 | -0.016871 | 1.5184
7 | -0.010001 | -0.0024967 | 0.010009 | 0.0024993 | 8.7941e-06 | 2.5502e-06 | 0.014895 | 0.014895 | 0.014895 | 0.99883 | -0.008281 | 0.99973 | -0.0018839 | 5.5167
8 | -0.010605 | -0.0026485 | 0.010608 | 0.0026493 | 2.7471e-06 | 8.2474e-07 | 0.015781 | 0.015781 | 0.015781 | 0.99973 | -0.0018839 | 1 | 0 | 5.8449
9 | 0.002142 | 0.00052369 | -0.00214 | -0.00052714 | 2.0402e-06 | -3.4434e-06 | 0.0031828 | 0.0031843 | 0.0031843 | 1 | 0 | 0.99902 | -0.0071687 | 1.1794
10 | 0.00214 | 0.00052714 | -0.0021397 | -0.00052771 | 3.4128e-07 | -5.7482e-07 | 0.0031843 | 0.0031845 | 0.0031845 | 0.99902 | -0.0071687 | 0.99885 | -0.0083587 | 1.1795
11 | 0.0036306 | 0.00090258 | -0.0036301 | -0.00090276 | 5.404e-07 | -1.786e-07 | 0.0054108 | 0.0054109 | 0.0054109 | 0.99798 | -0.0143 | 0.99782 | -0.015392 | 2.004
12 | 0.0018708 | 0.00046472 | -0.0018708 | -0.00046484 | 5.4569e-08 | -1.2568e-07 | 0.0027896 | 0.0027896 | 0.0027896 | 0.99742 | -0.018306 | 0.99739 | -0.018521 | 1.0332
13 | -0.00191 | -0.00047453 | 0.0019101 | 0.00047429 | 1.0841e-07 | -2.3789e-07 | 0.002848 | 0.0028479 | 0.002848 | 0.99742 | -0.018306 | 0.99747 | -0.017889 | 1.0548
14 | 0.0017351 | 0.00043085 | -0.0017351 | -0.00043101 | 5.8962e-08 | -1.6153e-07 | 0.0025873 | 0.0025873 | 0.0025873 | 0.99739 | -0.018521 | 0.99735 | -0.018771 | 0.95828
15 | 0.000537 | 0.00013298 | -0.00053695 | -0.00013448 | 4.662e-08 | -1.5027e-06 | 0.00080053 | 0.00080106 | 0.00080106 | 0.99747 | -0.017889 | 0.99739 | -0.018524 | 0.29669
16 | -0.0024471 | -0.00060727 | 0.0024474 | 0.00060693 | 2.8723e-07 | -3.41e-07 | 0.0036484 | 0.0036483 | 0.0036484 | 0.99747 | -0.017889 | 0.9976 | -0.017024 | 1.3513
17 | 0.0012502 | 0.00030949 | -0.0012502 | -0.00030968 | 3.4547e-08 | -1.9466e-07 | 0.0018639 | 0.001864 | 0.001864 | 0.99735 | -0.018771 | 0.99732 | -0.018975 | 0.69037
18 | 0.00042751 | 0.00010706 | -0.00042751 | -0.00010714 | 1.7325e-09 | -8.8411e-08 | 0.00063778 | 0.00063781 | 0.00063781 | 0.99739 | -0.018524 | 0.99738 | -0.018553 | 0.23623
19 | -0.0026699 | -0.00066269 | 0.00267 | 0.00066258 | 1.2073e-07 | -1.1303e-07 | 0.0039801 | 0.0039801 | 0.0039801 | 0.9976 | -0.017024 | 0.99764 | -0.016691 | 1.4741
20 | 0.00096599 | 0.00023846 | -0.00096587 | -0.00023965 | 1.2242e-07 | -1.1869e-06 | 0.00144 | 0.0014404 | 0.0014404 | 0.99732 | -0.018975 | 0.99719 | -0.019913 | 0.53349
21 | -0.0027549 | -0.00068387 | 0.002755 | 0.00068382 | 5.7642e-08 | -4.935e-08 | 0.0041068 | 0.0041068 | 0.0041068 | 0.99764 | -0.016691 | 0.99766 | -0.016537 | 1.521
22 | 0.00073252 | 0.00018117 | -0.0007325 | -0.0001816 | 2.5103e-08 | -4.302e-07 | 0.0010922 | 0.0010924 | 0.0010924 | 0.99719 | -0.019913 | 0.99716 | -0.020167 | 0.40459
23 | 0.00015881 | 3.7816e-05 | -0.0001588 | -3.83e-05 | 1.2948e-09 | -4.8395e-07 | 0.0002363 | 0.00023646 | 0.00023646 | 0.99716 | -0.020167 | 0.99715 | -0.020231 | 0.087578
24 | 0.0001588 | 3.83e-05 | -0.0001588 | -3.9799e-05 | 4.0228e-09 | -1.4992e-06 | 0.00023646 | 0.00023698 | 0.00023698 | 0.99715 | -0.020231 | 0.99712 | -0.020421 | 0.08777
25 | -0.0032821 | -0.00081594 | 0.0032822 | 0.0008159 | 8.4026e-08 | -4.1129e-08 | 0.004893 | 0.004893 | 0.004893 | 0.99766 | -0.016537 | 0.99769 | -0.016349 | 1.8122
26 | -0.0033235 | -0.00082623 | 0.0033239 | 0.00082603 | 4.3329e-07 | -2.0281e-07 | 0.0049545 | 0.0049543 | 0.0049545 | 0.99769 | -0.016349 | 0.99782 | -0.015392 | 1.835
27 | 0.0020914 | 0.00051562 | -0.0020909 | -0.00051642 | 4.5245e-07 | -8.0525e-07 | 0.0031126 | 0.003113 | 0.003113 | 0.99885 | -0.0083587 | 0.99863 | -0.0099696 | 1.1529
28 | 0.0015926 | 0.00039152 | -0.0015925 | -0.00039158 | 1.7928e-08 | -6.0006e-08 | 0.0023704 | 0.0023704 | 0.0023704 | 0.99863 | -0.0099696 | 0.99862 | -0.010054 | 0.87792
29 | -0.0012868 | -0.00031533 | 0.0012868 | 0.00031496 | 6.8928e-08 | -3.6758e-07 | 0.001915 | 0.0019149 | 0.001915 | 0.99856 | -0.010458 | 0.99862 | -0.010054 | 0.70926
30 | 0.0011592 | 0.00028335 | -0.001159 | -0.00028469 | 2.0019e-07 | -1.3329e-06 | 0.0017249 | 0.0017254 | 0.0017254 | 0.99856 | -0.010458 | 0.99838 | -0.011761 | 0.63903
31 | 0.001159 | 0.00028469 | -0.0011584 | -0.00028878 | 6.1514e-07 | -4.0876e-06 | 0.0017254 | 0.0017269 | 0.0017269 | 0.99838 | -0.011761 | 0.99784 | -0.015693 | 0.63959
32 | 0.0011584 | 0.00028878 | -0.0011582 | -0.00028974 | 1.4548e-07 | -9.6494e-07 | 0.0017269 | 0.0017272 | 0.0017272 | 0.99784 | -0.015693 | 0.99771 | -0.016606 | 0.63972
33 | 0.00035038 | 8.7376e-05 | -0.00035038 | -8.7808e-05 | 5.6566e-09 | -4.3144e-07 | 0.00052242 | 0.00052257 | 0.00052257 | 0.9977 | -0.01664 | 0.99769 | -0.016757 | 0.19355
34 | -0.00041358 | -0.00010321 | 0.00041358 | 0.00010311 | 1.8863e-09 | -1.0309e-07 | 0.00061667 | 0.00061664 | 0.00061667 | 0.9977 | -0.01664 | 0.99771 | -0.016606 | 0.2284
35 | 0.00015157 | 3.7982e-05 | -0.00015157 | -3.7986e-05 | 1.1244e-11 | -4.5939e-09 | 0.00022606 | 0.00022606 | 0.00022606 | 0.99769 | -0.016757 | 0.99769 | -0.016757 | 0.083725

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.013781 | 0.003231

## res_load
| p_mw | q_mvar
0 | 0.001626 | 0.00040752
1 | 0.0027478 | 0.00068867
2 | 0.0017477 | 0.00043803
3 | 0.0001291 | 3.2355e-05
4 | 0.00059551 | 0.00014925
5 | 0.0002309 | 5.7869e-05
6 | 0.00010914 | 2.7353e-05
7 | 3.9135e-05 | 9.8083e-06
8 | 0.00013564 | 3.3995e-05
9 | 0.00048488 | 0.00012152
10 | 0.00010944 | 2.7429e-05
11 | 0.0002225 | 5.5765e-05
12 | 0.00028418 | 7.1221e-05
13 | 0.00042751 | 0.00010714
14 | 8.4943e-05 | 2.1289e-05
15 | 0.00023335 | 5.8482e-05
16 | 0.00057369 | 0.00014378
17 | 0.00052715 | 0.00013212
18 | 4.1232e-05 | 1.0334e-05
19 | 0.00030617 | 7.6734e-05
20 | 4.8265e-05 | 1.2096e-05
21 | 0.00049837 | 0.0001249
22 | 0.0001588 | 3.9799e-05
23 | 0.00012757 | 3.1972e-05
24 | 0.0003057 | 7.6617e-05
25 | 6.3197e-05 | 1.5839e-05
26 | 0.00019881 | 4.9826e-05
27 | 0.00074466 | 0.00018663
28 | 0.00015157 | 3.7986e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1