## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1100-3_2_1_node_128 | 0.4 | n |  | TRUE
1 | bus_LV_1100-3_2_1_node_127 | 0.4 | n |  | TRUE
2 | bus_LV_1100-3_2_1_node_134 | 0.4 | n |  | TRUE
3 | bus_LV_1100-3_2_1_node_129 | 0.4 | n |  | TRUE
4 | bus_LV_1100-3_2_1_node_131 | 0.4 | n |  | TRUE
5 | bus_LV_1100-3_2_1_node_104 | 0.4 | n |  | TRUE
6 | bus_LV_1100-3_2_1_node_132 | 0.4 | n |  | TRUE
7 | bus_LV_1100-3_2_1_node_136 | 0.4 | n |  | TRUE
8 | bus_LV_1100-3_2_1_node_125 | 0.4 | n |  | TRUE
9 | bus_LV_1100-3_2_1_node_133 | 0.4 | n |  | TRUE
10 | bus_LV_1100-3_2_1_node_135 | 0.4 | n |  | TRUE
11 | bus_LV_1100-3_2_1_node_137 | 0.4 | n |  | TRUE
12 | bus_LV_1100-3_2_1_node_138 | 0.4 | n |  | TRUE
13 | bus_LV_1100-3_2_1_node_139 | 0.4 | n |  | TRUE
14 | bus_LV_1100-3_2_1_node_140 | 0.4 | n |  | TRUE
15 | bus_LV_1100-3_2_1_node_141 | 0.4 | n |  | TRUE
16 | bus_LV_1100-3_2_1_node_100 | 0.4 | n |  | TRUE
17 | bus_LV_1100-3_2_1_node_101 | 0.4 | n |  | TRUE
18 | bus_LV_1100-3_2_1_node_102 | 0.4 | n |  | TRUE
19 | bus_LV_1100-3_2_1_node_103 | 0.4 | n |  | TRUE
20 | bus_LV_1100-3_2_1_node_118 | 0.4 | n |  | TRUE
21 | bus_LV_1100-3_2_1_node_113 | 0.4 | n |  | TRUE
22 | bus_LV_1100-3_2_1_node_114 | 0.4 | n |  | TRUE
23 | bus_LV_1100-3_2_1_node_115 | 0.4 | n |  | TRUE
24 | bus_LV_1100-3_2_1_node_117 | 0.4 | n |  | TRUE
25 | bus_LV_1100-3_2_1_node_120 | 0.4 | n |  | TRUE
26 | bus_LV_1100-3_2_1_node_126 | 0.4 | n |  | TRUE
27 | bus_LV_1100-3_2_1_node_119 | 0.4 | n |  | TRUE
28 | bus_LV_1100-3_2_1_node_121 | 0.4 | n |  | TRUE
29 | bus_LV_1100-3_2_1_node_122 | 0.4 | n |  | TRUE
30 | bus_LV_1100-3_2_1_node_123 | 0.4 | n |  | TRUE
31 | bus_LV_1100-3_2_1_node_124 | 0.4 | n |  | TRUE
32 | bus_MV_0_node_131 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1100-3_2_1_load_128 | 0 | 0.00078911 | 0.00019777 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1100-3_2_1_load_129 | 3 | 0.00072468 | 0.00018162 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1100-3_2_1_load_131 | 4 | 0.00048588 | 0.00012177 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1100-3_2_1_load_136 | 7 | 0.0011689 | 0.00029296 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1100-3_2_1_load_133 | 9 | 0.00028266 | 7.084e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1100-3_2_1_load_135 | 10 | 0.0026178 | 0.00065607 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1100-3_2_1_load_137 | 11 | 0.0013417 | 0.00033625 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1100-3_2_1_load_138 | 12 | 0.00056391 | 0.00014133 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1100-3_2_1_load_139 | 13 | 0.00083989 | 0.0002105 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1100-3_2_1_load_140 | 14 | 0.0015706 | 0.00039363 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1100-3_2_1_load_100 | 16 | 0.0014038 | 0.00035182 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1100-3_2_1_load_101 | 17 | 0.00052453 | 0.00013146 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1100-3_2_1_load_102 | 18 | 0.00021371 | 5.3561e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1100-3_2_1_load_118 | 20 | 0.00028529 | 7.1501e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1100-3_2_1_load_113 | 21 | 0.0012845 | 0.00032193 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1100-3_2_1_load_114 | 22 | 0.00042172 | 0.00010569 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1100-3_2_1_load_120 | 25 | 0.00074576 | 0.0001869 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1100-3_2_1_load_126 | 26 | 0.0017308 | 0.00043377 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1100-3_2_1_load_119 | 27 | 0.0019189 | 0.00048093 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1100-3_2_1_load_121 | 28 | 0.0019684 | 0.00049332 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1100-3_2_1_load_122 | 29 | 0.0015855 | 0.00039737 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1100-3_2_1_load_123 | 30 | 0.0019001 | 0.00047621 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1100-3_2_1_load_124 | 31 | 0.0015071 | 0.00037771 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1100-3_2_1_line_0 | NAYY 4x150 SE | 0 | 1 | 0.037726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1100-3_2_1_line_1 | NAYY 4x150 SE | 0 | 2 | 0.099411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1100-3_2_1_line_2 | NAYY 4x150 SE | 1 | 3 | 0.021594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1100-3_2_1_line_3 | NAYY 4x150 SE | 1 | 26 | 0.026089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1100-3_2_1_line_4 | NAYY 4x150 SE | 2 | 9 | 0.12869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1100-3_2_1_line_5 | NAYY 4x150 SE | 4 | 5 | 0.029198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1100-3_2_1_line_6 | NAYY 4x150 SE | 5 | 6 | 0.021142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1100-3_2_1_line_7 | NAYY 4x150 SE | 5 | 18 | 0.031002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1100-3_2_1_line_8 | NAYY 4x150 SE | 6 | 7 | 0.05215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1100-3_2_1_line_9 | NAYY 4x150 SE | 6 | 8 | 0.34992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1100-3_2_1_line_10 | NAYY 4x150 SE | 7 | 10 | 0.011794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1100-3_2_1_line_11 | NAYY 4x150 SE | 8 | 15 | 0.020657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1100-3_2_1_line_12 | NAYY 4x150 SE | 8 | 30 | 0.016885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1100-3_2_1_line_13 | NAYY 4x150 SE | 11 | 12 | 0.029293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1100-3_2_1_line_14 | NAYY 4x150 SE | 11 | 13 | 0.027347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1100-3_2_1_line_15 | NAYY 4x150 SE | 12 | 14 | 0.00081996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1100-3_2_1_line_16 | NAYY 4x150 SE | 13 | 15 | 0.023478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1100-3_2_1_line_17 | NAYY 4x150 SE | 16 | 17 | 0.03599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1100-3_2_1_line_18 | NAYY 4x150 SE | 16 | 18 | 0.013954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1100-3_2_1_line_19 | NAYY 4x150 SE | 17 | 19 | 0.079746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1100-3_2_1_line_20 | NAYY 4x150 SE | 19 | 20 | 0.045363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1100-3_2_1_line_21 | NAYY 4x150 SE | 20 | 23 | 0.010396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1100-3_2_1_line_22 | NAYY 4x150 SE | 21 | 22 | 0.011541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1100-3_2_1_line_23 | NAYY 4x150 SE | 21 | 23 | 0.067594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1100-3_2_1_line_24 | NAYY 4x150 SE | 23 | 24 | 0.021207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1100-3_2_1_line_25 | NAYY 4x150 SE | 24 | 25 | 0.028958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1100-3_2_1_line_26 | NAYY 4x150 SE | 24 | 26 | 0.0014579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1100-3_2_1_line_27 | NAYY 4x150 SE | 25 | 27 | 0.037238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1100-3_2_1_line_28 | NAYY 4x150 SE | 27 | 28 | 0.031502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1100-3_2_1_line_29 | NAYY 4x150 SE | 29 | 30 | 0.019581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1100-3_2_1_line_30 | NAYY 4x150 SE | 29 | 31 | 0.02945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1100-3_2_1_trafo_131 | 0.25 MVA 20/0.4 kV | 32 | 4 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2652498.6353 | 1229676.7504 | 2652495.1883 | 1229670.7606 | 2652464.7773 | 1229665.7863
1 | 2652464.7773 | 1229665.7863 | 2652410.1278 | 1229582.7441
2 | 2652498.6353 | 1229676.7504 | 2652492.414 | 1229679.5417 | 2652481.0715 | 1229686.6573 | 2652480.0266 | 1229687.5666
3 | 2652498.6353 | 1229676.7504 | 2652517.3356 | 1229674.5362 | 2652524.4778 | 1229675.8307
4 | 2652410.1278 | 1229582.7441 | 2652402.2425 | 1229588.6784 | 2652363.9768 | 1229606.1193 | 2652322.7345 | 1229633.0069 | 2652299.578 | 1229647.9128
5 | 2652756.9464 | 1229707.5321 | 2652761.4784 | 1229720.9697 | 2652763.8919 | 1229735.7914
6 | 2652777.5624 | 1229702.8564 | 2652767.0036 | 1229704.4304 | 2652756.9464 | 1229707.5321
7 | 2652756.9464 | 1229707.5321 | 2652751.2498 | 1229701.5556 | 2652740.7975 | 1229697.0935 | 2652731.6987 | 1229697.1907 | 2652729.4568 | 1229697.6131
8 | 2652777.5624 | 1229702.8564 | 2652783.3165 | 1229651.0244
9 | 2652777.5624 | 1229702.8564 | 2653104.1641 | 1229828.4527
10 | 2652784.6178 | 1229639.3023 | 2652783.3165 | 1229651.0244
11 | 2653118.9545 | 1229841.6042 | 2653113.2553 | 1229832.5809 | 2653104.1641 | 1229828.4527
12 | 2653104.1641 | 1229828.4527 | 2653100.9056 | 1229845.0202
13 | 2653118.2199 | 1229892.424 | 2653117.7966 | 1229921.714
14 | 2653118.6152 | 1229865.0798 | 2653118.2199 | 1229892.424
15 | 2653117.7847 | 1229922.5339 | 2653117.7966 | 1229921.714
16 | 2653118.9545 | 1229841.6042 | 2653118.6152 | 1229865.0798
17 | 2652715.7441 | 1229700.1967 | 2652708.0849 | 1229701.6398 | 2652695.5412 | 1229703.2409 | 2652680.015 | 1229704.1138
18 | 2652715.7441 | 1229700.1967 | 2652729.4568 | 1229697.6131
19 | 2652601.5205 | 1229690.7901 | 2652656.9118 | 1229701.8536 | 2652676.5783 | 1229704.307 | 2652680.015 | 1229704.1138
20 | 2652601.5205 | 1229690.7901 | 2652557.0349 | 1229681.9124
21 | 2652546.8398 | 1229679.8778 | 2652557.0349 | 1229681.9124
22 | 2652560.0453 | 1229613.6868 | 2652562.598 | 1229602.432
23 | 2652546.8398 | 1229679.8778 | 2652547.9299 | 1229667.1016 | 2652560.0453 | 1229613.6868
24 | 2652546.8398 | 1229679.8778 | 2652525.9123 | 1229676.0907
25 | 2652525.9123 | 1229676.0907 | 2652515.8589 | 1229703.248
26 | 2652525.9123 | 1229676.0907 | 2652524.4778 | 1229675.8307
27 | 2652510.0815 | 1229737.5242 | 2652515.5065 | 1229730.6889 | 2652517.4343 | 1229719.9769 | 2652513.8759 | 1229708.605 | 2652515.8589 | 1229703.248
28 | 2652510.0815 | 1229737.5242 | 2652508.3209 | 1229739.7424 | 2652494.4028 | 1229751.1712 | 2652487.4101 | 1229759.2187
29 | 2653096.7109 | 1229864.1463 | 2653100.617 | 1229846.488 | 2653100.9056 | 1229845.0202
30 | 2653094.6609 | 1229893.3757 | 2653094.6967 | 1229873.2522 | 2653096.7109 | 1229864.1463

## bus_geodata
| x | y | coords
0 | 2652464.7773 | 1229665.7863
1 | 2652498.6353 | 1229676.7504
2 | 2652410.1278 | 1229582.7441
3 | 2652480.0266 | 1229687.5666
4 | 2652763.8919 | 1229735.7914
5 | 2652756.9464 | 1229707.5321
6 | 2652777.5624 | 1229702.8564
7 | 2652783.3165 | 1229651.0244
8 | 2653104.1641 | 1229828.4527
9 | 2652299.578 | 1229647.9128
10 | 2652784.6178 | 1229639.3023
11 | 2653118.2199 | 1229892.424
12 | 2653117.7966 | 1229921.714
13 | 2653118.6152 | 1229865.0798
14 | 2653117.7847 | 1229922.5339
15 | 2653118.9545 | 1229841.6042
16 | 2652715.7441 | 1229700.1967
17 | 2652680.015 | 1229704.1138
18 | 2652729.4568 | 1229697.6131
19 | 2652601.5205 | 1229690.7901
20 | 2652557.0349 | 1229681.9124
21 | 2652560.0453 | 1229613.6868
22 | 2652562.598 | 1229602.432
23 | 2652546.8398 | 1229679.8778
24 | 2652525.9123 | 1229676.0907
25 | 2652515.8589 | 1229703.248
26 | 2652524.4778 | 1229675.8307
27 | 2652510.0815 | 1229737.5242
28 | 2652487.4101 | 1229759.2187
29 | 2653096.7109 | 1229864.1463
30 | 2653100.9056 | 1229845.0202
31 | 2653094.6609 | 1229893.3757
32 | 2652763.8919 | 1229735.7914

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99526 | -0.033422 | 0.00078911 | 0.00019777
1 | 0.99531 | -0.033005 | 0 | 0
2 | 0.99522 | -0.033722 | 0 | 0
3 | 0.99529 | -0.033163 | 0.00072468 | 0.00018162
4 | 1 | 0 | -0.026306 | -0.0063903
5 | 0.99894 | -0.0074446 | 0 | 0
6 | 0.99854 | -0.010227 | 0 | 0
7 | 0.99826 | -0.012206 | 0.0011689 | 0.00029296
8 | 0.99387 | -0.043101 | 0 | 0
9 | 0.99516 | -0.034097 | 0.00028266 | 7.084e-05
10 | 0.99822 | -0.012515 | 0.0026178 | 0.00065607
11 | 0.99346 | -0.045992 | 0.0013417 | 0.00033625
12 | 0.99337 | -0.046625 | 0.00056391 | 0.00014133
13 | 0.9936 | -0.04503 | 0.00083989 | 0.0002105
14 | 0.99337 | -0.046638 | 0.0015706 | 0.00039363
15 | 0.99374 | -0.044004 | 0 | 0
16 | 0.99815 | -0.012978 | 0.0014038 | 0.00035182
17 | 0.9976 | -0.016852 | 0.00052453 | 0.00013146
18 | 0.99839 | -0.01128 | 0.00021371 | 5.3561e-05
19 | 0.99644 | -0.025028 | 0 | 0
20 | 0.99578 | -0.029684 | 0.00028529 | 7.1501e-05
21 | 0.99547 | -0.031886 | 0.0012845 | 0.00032193
22 | 0.99546 | -0.031935 | 0.00042172 | 0.00010569
23 | 0.99564 | -0.030722 | 0 | 0
24 | 0.99539 | -0.032473 | 0 | 0
25 | 0.9952 | -0.033827 | 0.00074576 | 0.0001869
26 | 0.99538 | -0.032525 | 0.0017308 | 0.00043377
27 | 0.99499 | -0.035288 | 0.0019189 | 0.00048093
28 | 0.9949 | -0.035914 | 0.0019684 | 0.00049332
29 | 0.99366 | -0.044566 | 0.0015855 | 0.00039737
30 | 0.99375 | -0.043954 | 0.0019001 | 0.00047621
31 | 0.9936 | -0.045016 | 0.0015071 | 0.00037771
32 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0010718 | -0.00026566 | 0.0010719 | 0.00026519 | 6.0365e-08 | -4.6706e-07 | 0.0016014 | 0.0016012 | 0.0016014 | 0.99526 | -0.033422 | 0.99531 | -0.033005 | 0.59311
1 | 0.00028268 | 6.7886e-05 | -0.00028267 | -6.9174e-05 | 1.1038e-08 | -1.2876e-06 | 0.00042162 | 0.00042206 | 0.00042206 | 0.99526 | -0.033422 | 0.99522 | -0.033722 | 0.15632
2 | 0.00072469 | 0.00018135 | -0.00072468 | -0.00018162 | 1.5815e-08 | -2.7455e-07 | 0.0010833 | 0.0010834 | 0.0010834 | 0.99531 | -0.033005 | 0.99529 | -0.033163 | 0.40127
3 | -0.0017965 | -0.00044654 | 0.0017967 | 0.00044624 | 1.1732e-07 | -2.9397e-07 | 0.0026846 | 0.0026844 | 0.0026846 | 0.99531 | -0.033005 | 0.99538 | -0.032525 | 0.99428
4 | 0.00028267 | 6.9174e-05 | -0.00028266 | -7.084e-05 | 1.4325e-08 | -1.6667e-06 | 0.00042206 | 0.00042264 | 0.00042264 | 0.99522 | -0.033722 | 0.99516 | -0.034097 | 0.15653
5 | 0.025506 | 0.0063902 | -0.02548 | -0.0063805 | 2.6243e-05 | 9.7109e-06 | 0.037952 | 0.037952 | 0.037952 | 1 | 0 | 0.99894 | -0.0074446 | 14.0564
6 | 0.013147 | 0.003294 | -0.013142 | -0.0032923 | 5.0594e-06 | 1.6693e-06 | 0.019583 | 0.019583 | 0.019583 | 0.99894 | -0.0074446 | 0.99854 | -0.010227 | 7.2531
7 | 0.012333 | 0.0030866 | -0.012326 | -0.0030845 | 6.5277e-06 | 2.105e-06 | 0.018369 | 0.018369 | 0.018369 | 0.99894 | -0.0074446 | 0.99839 | -0.01128 | 6.8034
8 | 0.0037878 | 0.00094864 | -0.0037868 | -0.00094892 | 1.0368e-06 | -2.8322e-07 | 0.0056444 | 0.0056446 | 0.0056446 | 0.99854 | -0.010227 | 0.99826 | -0.012206 | 2.0906
9 | 0.009354 | 0.0023437 | -0.0093115 | -0.0023319 | 4.2429e-05 | 1.1763e-05 | 0.013939 | 0.013941 | 0.013941 | 0.99854 | -0.010227 | 0.99387 | -0.043101 | 5.1632
10 | 0.0026179 | 0.00065596 | -0.0026178 | -0.00065607 | 1.1207e-07 | -1.1108e-07 | 0.0039022 | 0.0039022 | 0.0039022 | 0.99826 | -0.012206 | 0.99822 | -0.012515 | 1.4453
11 | 0.0043179 | 0.0010811 | -0.0043174 | -0.0010812 | 5.3865e-07 | -6.0485e-08 | 0.0064643 | 0.0064644 | 0.0064644 | 0.99387 | -0.043101 | 0.99374 | -0.044004 | 2.3942
12 | 0.0049936 | 0.0012508 | -0.0049931 | -0.0012508 | 5.8891e-07 | 7.7205e-09 | 0.0074762 | 0.0074763 | 0.0074763 | 0.99387 | -0.043101 | 0.99375 | -0.043954 | 2.769
13 | 0.0021347 | 0.00053465 | -0.0021345 | -0.00053495 | 1.8687e-07 | -3.0739e-07 | 0.0031973 | 0.0031974 | 0.0031974 | 0.99346 | -0.045992 | 0.99337 | -0.046625 | 1.1842
14 | -0.0034764 | -0.0008709 | 0.0034769 | 0.00087072 | 4.6263e-07 | -1.7621e-07 | 0.0052068 | 0.0052067 | 0.0052068 | 0.99346 | -0.045992 | 0.9936 | -0.04503 | 1.9285
15 | 0.0015706 | 0.00039362 | -0.0015706 | -0.00039363 | 2.8321e-09 | -9.5258e-09 | 0.0023527 | 0.0023527 | 0.0023527 | 0.99337 | -0.046625 | 0.99337 | -0.046638 | 0.87137
16 | -0.0043167 | -0.0010812 | 0.0043174 | 0.0010812 | 6.1223e-07 | -6.8654e-08 | 0.0064646 | 0.0064644 | 0.0064646 | 0.9936 | -0.04503 | 0.99374 | -0.044004 | 2.3943
17 | 0.010706 | 0.0026782 | -0.0107 | -0.0026764 | 5.7192e-06 | 1.7295e-06 | 0.015958 | 0.015958 | 0.015958 | 0.99815 | -0.012978 | 0.9976 | -0.016852 | 5.9105
18 | -0.01211 | -0.00303 | 0.012112 | 0.0030309 | 2.8371e-06 | 9.0876e-07 | 0.018051 | 0.018051 | 0.018051 | 0.99815 | -0.012978 | 0.99839 | -0.01128 | 6.6855
19 | 0.010176 | 0.002545 | -0.010164 | -0.0025416 | 1.1461e-05 | 3.368e-06 | 0.015176 | 0.015176 | 0.015176 | 0.9976 | -0.016852 | 0.99644 | -0.025028 | 5.6208
20 | 0.010164 | 0.0025416 | -0.010158 | -0.0025397 | 6.5196e-06 | 1.917e-06 | 0.015176 | 0.015176 | 0.015176 | 0.99644 | -0.025028 | 0.99578 | -0.029684 | 5.6209
21 | 0.0098723 | 0.0024682 | -0.0098708 | -0.0024678 | 1.4114e-06 | 4.0762e-07 | 0.01475 | 0.01475 | 0.01475 | 0.99578 | -0.029684 | 0.99564 | -0.030722 | 5.463
22 | 0.00042172 | 0.00010554 | -0.00042172 | -0.00010569 | 2.8615e-09 | -1.4894e-07 | 0.00063033 | 0.00063039 | 0.00063039 | 0.99547 | -0.031886 | 0.99546 | -0.031935 | 0.23348
23 | -0.0017063 | -0.00042748 | 0.0017065 | 0.0004267 | 2.7433e-07 | -7.7341e-07 | 0.0025504 | 0.0025501 | 0.0025504 | 0.99547 | -0.031886 | 0.99564 | -0.030722 | 0.9446
24 | 0.0081643 | 0.0020411 | -0.0081623 | -0.0020406 | 1.9697e-06 | 4.8183e-07 | 0.0122 | 0.0122 | 0.0122 | 0.99564 | -0.030722 | 0.99539 | -0.032473 | 4.5186
25 | 0.0046349 | 0.0011606 | -0.004634 | -0.0011606 | 8.6743e-07 | -4.272e-08 | 0.0069284 | 0.0069285 | 0.0069285 | 0.99539 | -0.032473 | 0.9952 | -0.033827 | 2.5661
26 | 0.0035274 | 0.00088 | -0.0035274 | -0.00088001 | 2.5283e-08 | -9.2264e-09 | 0.0052718 | 0.0052718 | 0.0052718 | 0.99539 | -0.032473 | 0.99538 | -0.032525 | 1.9525
27 | 0.0038883 | 0.00097373 | -0.0038875 | -0.00097391 | 7.8534e-07 | -1.817e-07 | 0.0058135 | 0.0058136 | 0.0058136 | 0.9952 | -0.033827 | 0.99499 | -0.035288 | 2.1532
28 | 0.0019685 | 0.00049298 | -0.0019684 | -0.00049332 | 1.7036e-07 | -3.436e-07 | 0.0029438 | 0.002944 | 0.002944 | 0.99499 | -0.035288 | 0.9949 | -0.035914 | 1.0904
29 | -0.0030927 | -0.00077474 | 0.003093 | 0.00077458 | 2.6206e-07 | -1.5287e-07 | 0.0046312 | 0.0046311 | 0.0046312 | 0.99366 | -0.044566 | 0.99375 | -0.043954 | 1.7153
30 | 0.0015072 | 0.00037737 | -0.0015071 | -0.00037771 | 9.3608e-08 | -3.4545e-07 | 0.0022569 | 0.002257 | 0.002257 | 0.99366 | -0.044566 | 0.9936 | -0.045016 | 0.83594

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.026792 | 0.0065121

## res_load
| p_mw | q_mvar
0 | 0.00078911 | 0.00019777
1 | 0.00072468 | 0.00018162
2 | 0.00048588 | 0.00012177
3 | 0.0011689 | 0.00029296
4 | 0.00028266 | 7.084e-05
5 | 0.0026178 | 0.00065607
6 | 0.0013417 | 0.00033625
7 | 0.00056391 | 0.00014133
8 | 0.00083989 | 0.0002105
9 | 0.0015706 | 0.00039363
10 | 0.0014038 | 0.00035182
11 | 0.00052453 | 0.00013146
12 | 0.00021371 | 5.3561e-05
13 | 0.00028529 | 7.1501e-05
14 | 0.0012845 | 0.00032193
15 | 0.00042172 | 0.00010569
16 | 0.00074576 | 0.0001869
17 | 0.0017308 | 0.00043377
18 | 0.0019189 | 0.00048093
19 | 0.0019684 | 0.00049332
20 | 0.0015855 | 0.00039737
21 | 0.0019001 | 0.00047621
22 | 0.0015071 | 0.00037771

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1