## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1102-14_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1102-14_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1102-14_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1102-14_0_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_1102-14_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1102-14_0_4_node_22 | 0.4 | n |  | TRUE
6 | bus_LV_1102-14_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1102-14_0_4_node_23 | 0.4 | n |  | TRUE
8 | bus_LV_1102-14_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1102-14_0_4_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_1102-14_0_4_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_1102-14_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1102-14_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1102-14_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1102-14_0_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1102-14_0_4_node_17 | 0.4 | n |  | TRUE
16 | bus_LV_1102-14_0_4_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_1102-14_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1102-14_0_4_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_1102-14_0_4_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_1102-14_0_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1102-14_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1102-14_0_4_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_1102-14_0_4_node_51 | 0.4 | n |  | TRUE
24 | bus_LV_1102-14_0_4_node_42 | 0.4 | n |  | TRUE
25 | bus_LV_1102-14_0_4_node_52 | 0.4 | n |  | TRUE
26 | bus_LV_1102-14_0_4_node_39 | 0.4 | n |  | TRUE
27 | bus_LV_1102-14_0_4_node_37 | 0.4 | n |  | TRUE
28 | bus_LV_1102-14_0_4_node_38 | 0.4 | n |  | TRUE
29 | bus_LV_1102-14_0_4_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_1102-14_0_4_node_40 | 0.4 | n |  | TRUE
31 | bus_LV_1102-14_0_4_node_41 | 0.4 | n |  | TRUE
32 | bus_LV_1102-14_0_4_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_1102-14_0_4_node_49 | 0.4 | n |  | TRUE
34 | bus_LV_1102-14_0_4_node_48 | 0.4 | n |  | TRUE
35 | bus_LV_1102-14_0_4_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_1102-14_0_4_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_1102-14_0_4_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_1102-14_0_4_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_1102-14_0_4_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_1102-14_0_4_node_45 | 0.4 | n |  | TRUE
41 | bus_LV_1102-14_0_4_node_46 | 0.4 | n |  | TRUE
42 | bus_LV_1102-14_0_4_node_47 | 0.4 | n |  | TRUE
43 | bus_LV_1102-14_0_4_node_50 | 0.4 | n |  | TRUE
44 | bus_LV_1102-14_0_4_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_1102-14_0_4_node_44 | 0.4 | n |  | TRUE
46 | bus_MV_354_0_node_229 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1102-14_0_4_load_0 | 0 | 0.011513 | 0.0028854 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1102-14_0_4_load_1 | 1 | 0.0032554 | 0.00081588 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1102-14_0_4_load_3 | 2 | 0.0034967 | 0.00087635 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1102-14_0_4_load_5 | 3 | 0.0037055 | 0.00092867 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1102-14_0_4_load_4 | 4 | 0.0023668 | 0.00059317 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1102-14_0_4_load_22 | 5 | 0.012948 | 0.0032451 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1102-14_0_4_load_6 | 6 | 0.0032035 | 0.00080287 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1102-14_0_4_load_7 | 8 | 0.0070265 | 0.001761 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1102-14_0_4_load_12 | 9 | 0.017428 | 0.0043679 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1102-14_0_4_load_13 | 10 | 0.0038526 | 0.00096555 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1102-14_0_4_load_8 | 11 | 0.0057831 | 0.0014494 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1102-14_0_4_load_10 | 13 | 0.0039565 | 0.0009916 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1102-14_0_4_load_11 | 14 | 0.0044743 | 0.0011214 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1102-14_0_4_load_17 | 15 | 0.0089977 | 0.002255 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1102-14_0_4_load_14 | 21 | 0.0087248 | 0.0021866 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1102-14_0_4_load_20 | 22 | 0.0071662 | 0.001796 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1102-14_0_4_load_51 | 23 | 0.017138 | 0.0042952 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1102-14_0_4_load_52 | 25 | 0.0033726 | 0.00084525 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1102-14_0_4_load_38 | 28 | 0.0034161 | 0.00085615 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1102-14_0_4_load_41 | 31 | 0.00087192 | 0.00021852 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1102-14_0_4_load_26 | 32 | 0.0029762 | 0.0007459 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1102-14_0_4_load_49 | 33 | 0.0093513 | 0.0023437 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1102-14_0_4_load_48 | 34 | 0.013005 | 0.0032593 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1102-14_0_4_load_30 | 35 | 0.0032192 | 0.0008068 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1102-14_0_4_load_34 | 38 | 0.0027159 | 0.00068067 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1102-14_0_4_load_33 | 39 | 0.0068711 | 0.0017221 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1102-14_0_4_load_47 | 42 | 0.013077 | 0.0032775 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1102-14_0_4_load_50 | 43 | 0.012903 | 0.0032339 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1102-14_0_4_load_43 | 44 | 0.003199 | 0.00080175 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1102-14_0_4_load_44 | 45 | 0.012642 | 0.0031684 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1102-14_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.015895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1102-14_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.020318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1102-14_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.026232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1102-14_0_4_line_3 | NAYY 4x150 SE | 3 | 6 | 0.0031058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1102-14_0_4_line_4 | NAYY 4x150 SE | 4 | 5 | 0.0099943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1102-14_0_4_line_5 | NAYY 4x150 SE | 5 | 7 | 0.023678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1102-14_0_4_line_6 | NAYY 4x150 SE | 6 | 8 | 0.021681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1102-14_0_4_line_7 | NAYY 4x150 SE | 7 | 16 | 0.018016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1102-14_0_4_line_8 | NAYY 4x150 SE | 7 | 13 | 0.019441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1102-14_0_4_line_9 | NAYY 4x150 SE | 8 | 9 | 0.0093601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1102-14_0_4_line_10 | NAYY 4x150 SE | 9 | 10 | 0.031765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1102-14_0_4_line_11 | NAYY 4x150 SE | 10 | 18 | 0.021007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1102-14_0_4_line_12 | NAYY 4x150 SE | 11 | 12 | 0.014466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1102-14_0_4_line_13 | NAYY 4x150 SE | 12 | 13 | 0.0080625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1102-14_0_4_line_14 | NAYY 4x150 SE | 12 | 14 | 0.016127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1102-14_0_4_line_15 | NAYY 4x150 SE | 14 | 15 | 0.020648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1102-14_0_4_line_16 | NAYY 4x150 SE | 15 | 17 | 0.032451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1102-14_0_4_line_17 | NAYY 4x150 SE | 16 | 33 | 0.019756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1102-14_0_4_line_18 | NAYY 4x150 SE | 16 | 23 | 0.036106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1102-14_0_4_line_19 | NAYY 4x150 SE | 17 | 21 | 0.024562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1102-14_0_4_line_20 | NAYY 4x150 SE | 18 | 19 | 0.095775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1102-14_0_4_line_21 | NAYY 4x150 SE | 18 | 20 | 0.019907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1102-14_0_4_line_22 | NAYY 4x150 SE | 19 | 32 | 0.083091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1102-14_0_4_line_23 | NAYY 4x150 SE | 20 | 22 | 0.019339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1102-14_0_4_line_24 | NAYY 4x150 SE | 20 | 21 | 0.015901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1102-14_0_4_line_25 | NAYY 4x150 SE | 24 | 25 | 0.004753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1102-14_0_4_line_26 | NAYY 4x150 SE | 24 | 26 | 0.073212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1102-14_0_4_line_27 | NAYY 4x150 SE | 26 | 30 | 0.039985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1102-14_0_4_line_28 | NAYY 4x150 SE | 26 | 31 | 0.01669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1102-14_0_4_line_29 | NAYY 4x150 SE | 26 | 28 | 0.021039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1102-14_0_4_line_30 | NAYY 4x150 SE | 27 | 28 | 0.0094189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1102-14_0_4_line_31 | NAYY 4x150 SE | 27 | 29 | 0.087659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1102-14_0_4_line_32 | NAYY 4x150 SE | 29 | 38 | 0.03004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1102-14_0_4_line_33 | NAYY 4x150 SE | 29 | 39 | 0.022848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1102-14_0_4_line_34 | NAYY 4x150 SE | 30 | 45 | 0.027747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1102-14_0_4_line_35 | NAYY 4x150 SE | 30 | 40 | 0.029044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1102-14_0_4_line_36 | NAYY 4x150 SE | 30 | 44 | 0.019023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1102-14_0_4_line_37 | NAYY 4x150 SE | 33 | 34 | 0.037362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1102-14_0_4_line_38 | NAYY 4x150 SE | 34 | 42 | 0.024012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1102-14_0_4_line_39 | NAYY 4x150 SE | 35 | 36 | 0.090347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1102-14_0_4_line_40 | NAYY 4x150 SE | 36 | 37 | 0.026043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1102-14_0_4_line_41 | NAYY 4x150 SE | 37 | 38 | 0.018382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1102-14_0_4_line_42 | NAYY 4x150 SE | 40 | 41 | 0.046566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1102-14_0_4_line_43 | NAYY 4x150 SE | 40 | 42 | 0.016933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1102-14_0_4_line_44 | NAYY 4x150 SE | 41 | 43 | 0.055469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1102-14_0_4_trafo_25 | 0.25 MVA 20/0.4 kV | 46 | 16 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2657354.8316 | 1220119.8625 | 2657354.1176 | 1220120.6228 | 2657347.7875 | 1220128.7113 | 2657345.2062 | 1220132.4957
1 | 2657345.2062 | 1220132.4957 | 2657339.5602 | 1220140.7729 | 2657334.1232 | 1220149.5197
2 | 2657321.551 | 1220172.5227 | 2657323.0568 | 1220169.1873 | 2657331.6529 | 1220153.4936 | 2657334.1232 | 1220149.5197
3 | 2657321.551 | 1220172.5227 | 2657320.273 | 1220175.3534
4 | 2657399.7143 | 1220144.3243 | 2657393.8992 | 1220136.1958
5 | 2657412.9594 | 1220163.9495 | 2657400.9613 | 1220146.0673 | 2657399.7143 | 1220144.3243
6 | 2657312.0971 | 1220195.4107 | 2657315.0404 | 1220186.9434 | 2657320.273 | 1220175.3534
7 | 2657412.9594 | 1220163.9495 | 2657423.7538 | 1220178.3958
8 | 2657412.9594 | 1220163.9495 | 2657399.3506 | 1220177.8335
9 | 2657309.0239 | 1220204.2518 | 2657312.0971 | 1220195.4107
10 | 2657301.0894 | 1220234.9596 | 2657301.5827 | 1220230.8412 | 2657304.6267 | 1220218.8631 | 2657309.0239 | 1220204.2518 | 2657309.0239 | 1220204.2518
11 | 2657308.6808 | 1220253.3123 | 2657304.1351 | 1220248.6657 | 2657303.0566 | 1220247.1988 | 2657301.6907 | 1220244.0615 | 2657300.5679 | 1220239.3145 | 2657301.0894 | 1220234.9596
12 | 2657394.4024 | 1220184.1944 | 2657405.4929 | 1220190.7497 | 2657406.624 | 1220189.6428
13 | 2657394.4024 | 1220184.1944 | 2657398.9899 | 1220178.2015 | 2657399.3506 | 1220177.8335
14 | 2657394.4024 | 1220184.1944 | 2657388.7353 | 1220193.5567 | 2657386.4309 | 1220198.1997
15 | 2657377.2513 | 1220216.6948 | 2657386.4309 | 1220198.1997
16 | 2657368.5232 | 1220247.7957 | 2657370.1103 | 1220237.4157 | 2657373.4523 | 1220226.0297 | 2657376.4555 | 1220218.2983 | 2657377.2513 | 1220216.6948
17 | 2657423.7538 | 1220178.3958 | 2657440.0075 | 1220167.1656
18 | 2657423.7538 | 1220178.3958 | 2657443.3593 | 1220202.0772 | 2657447.0247 | 1220205.9916
19 | 2657368.5232 | 1220247.7957 | 2657350.0519 | 1220248.9297 | 2657344.0704 | 1220249.8749
20 | 2657255.8569 | 1220303.0242 | 2657254.9237 | 1220307.7626 | 2657264.8363 | 1220293.9826 | 2657287.9938 | 1220295.4839 | 2657289.6643 | 1220294.5661 | 2657292.1362 | 1220279.7473 | 2657294.3792 | 1220267.4279 | 2657296.3521 | 1220262.6773 | 2657299.1918 | 1220257.7349 | 2657308.6808 | 1220253.3123
21 | 2657328.3643 | 1220252.3565 | 2657314.876 | 1220254.4948 | 2657308.6808 | 1220253.3123
22 | 2657255.8569 | 1220303.0242 | 2657258.9837 | 1220287.1666 | 2657263.8791 | 1220249.9128 | 2657266.1939 | 1220220.6503
23 | 2657328.3643 | 1220252.3565 | 2657327.0885 | 1220246.952 | 2657319.7411 | 1220238.5651 | 2657321.1889 | 1220236.3443
24 | 2657328.3643 | 1220252.3565 | 2657344.0704 | 1220249.8749
25 | 2657565.0451 | 1220249.5029 | 2657561.5014 | 1220252.6818
26 | 2657531.4364 | 1220204.3393 | 2657532.1315 | 1220212.4955 | 2657535.3993 | 1220210.3924 | 2657536.1092 | 1220224.0855 | 2657532.0128 | 1220231.8508 | 2657549.4489 | 1220238.1341 | 2657552.3175 | 1220238.084 | 2657561.5014 | 1220252.6818
27 | 2657531.4364 | 1220204.3393 | 2657526.7053 | 1220188.2614 | 2657519.4979 | 1220166.1782
28 | 2657531.4364 | 1220204.3393 | 2657515.6156 | 1220209.6555
29 | 2657531.4364 | 1220204.3393 | 2657533.3334 | 1220197.2532 | 2657546.6627 | 1220194.0738
30 | 2657553.5012 | 1220199.605 | 2657548.0264 | 1220193.7485 | 2657546.6627 | 1220194.0738
31 | 2657553.5012 | 1220199.605 | 2657572.2759 | 1220188.2904 | 2657577.1205 | 1220186.336 | 2657633.2594 | 1220163.7424
32 | 2657633.2594 | 1220163.7424 | 2657661.6217 | 1220153.8434
33 | 2657633.2594 | 1220163.7424 | 2657641.8181 | 1220184.9272
34 | 2657519.4979 | 1220166.1782 | 2657516.9807 | 1220173.0582 | 2657497.0921 | 1220177.9359
35 | 2657509.3514 | 1220141.2315 | 2657514.0963 | 1220155.8864 | 2657519.8545 | 1220159.9 | 2657518.5988 | 1220163.4345 | 2657519.4979 | 1220166.1782
36 | 2657519.4979 | 1220166.1782 | 2657525.3619 | 1220159.2416 | 2657532.9508 | 1220152.822
37 | 2657472.6439 | 1220152.1214 | 2657458.0512 | 1220164.073 | 2657441.5438 | 1220166.1041 | 2657440.0075 | 1220167.1656
38 | 2657493.71 | 1220141.6066 | 2657480.8195 | 1220145.4255 | 2657472.6439 | 1220152.1214
39 | 2657690.8245 | 1220170.9928 | 2657698.6699 | 1220164.7426 | 2657711.1345 | 1220165.7195 | 2657718.8659 | 1220174.3664 | 2657716.7503 | 1220185.1859 | 2657704.4862 | 1220207.3809 | 2657686.7268 | 1220216.2078
40 | 2657678.9774 | 1220147.7859 | 2657690.8245 | 1220170.9928
41 | 2657678.9774 | 1220147.7859 | 2657661.6217 | 1220153.8434
42 | 2657509.3514 | 1220141.2315 | 2657510.5957 | 1220128.6691 | 2657505.8939 | 1220109.5452 | 2657497.6599 | 1220097.903
43 | 2657509.3514 | 1220141.2315 | 2657504.6977 | 1220138.3515 | 2657493.71 | 1220141.6066
44 | 2657497.6599 | 1220097.903 | 2657490.3715 | 1220104.6257 | 2657470.2485 | 1220112.5476 | 2657459.3685 | 1220122.6935 | 2657450.3961 | 1220123.8794

## bus_geodata
| x | y | coords
0 | 2657354.8316 | 1220119.8625
1 | 2657345.2062 | 1220132.4957
2 | 2657334.1232 | 1220149.5197
3 | 2657321.551 | 1220172.5227
4 | 2657393.8992 | 1220136.1958
5 | 2657399.7143 | 1220144.3243
6 | 2657320.273 | 1220175.3534
7 | 2657412.9594 | 1220163.9495
8 | 2657312.0971 | 1220195.4107
9 | 2657309.0239 | 1220204.2518
10 | 2657301.0894 | 1220234.9596
11 | 2657406.624 | 1220189.6429
12 | 2657394.4024 | 1220184.1944
13 | 2657399.3506 | 1220177.8335
14 | 2657386.4309 | 1220198.1997
15 | 2657377.2513 | 1220216.6948
16 | 2657423.7538 | 1220178.3958
17 | 2657368.5232 | 1220247.7957
18 | 2657308.6808 | 1220253.3123
19 | 2657255.8569 | 1220303.0242
20 | 2657328.3643 | 1220252.3565
21 | 2657344.0704 | 1220249.8749
22 | 2657321.1889 | 1220236.3443
23 | 2657447.0247 | 1220205.9916
24 | 2657561.5014 | 1220252.6818
25 | 2657565.0451 | 1220249.5029
26 | 2657531.4364 | 1220204.3393
27 | 2657553.5012 | 1220199.605
28 | 2657546.6627 | 1220194.0738
29 | 2657633.2594 | 1220163.7424
30 | 2657519.4979 | 1220166.1782
31 | 2657515.6156 | 1220209.6555
32 | 2657266.1939 | 1220220.6503
33 | 2657440.0075 | 1220167.1656
34 | 2657472.6439 | 1220152.1214
35 | 2657686.7268 | 1220216.2078
36 | 2657690.8245 | 1220170.9928
37 | 2657678.9774 | 1220147.7859
38 | 2657661.6217 | 1220153.8434
39 | 2657641.8181 | 1220184.9272
40 | 2657509.3514 | 1220141.2315
41 | 2657497.6599 | 1220097.903
42 | 2657493.71 | 1220141.6066
43 | 2657450.3961 | 1220123.8794
44 | 2657532.9508 | 1220152.822
45 | 2657497.0921 | 1220177.9359
46 | 2657412.9594 | 1220163.9495

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97451 | -0.17926 | 0.011513 | 0.0028854
1 | 0.97478 | -0.17734 | 0.0032554 | 0.00081588
2 | 0.97521 | -0.17419 | 0.0034967 | 0.00087635
3 | 0.97592 | -0.16916 | 0.0037055 | 0.00092867
4 | 0.998 | -0.013856 | 0.0023668 | 0.00059317
5 | 0.99803 | -0.013619 | 0.012948 | 0.0032451
6 | 0.97602 | -0.16845 | 0.0032035 | 0.00080287
7 | 0.99855 | -0.0099873 | 0 | 0
8 | 0.97681 | -0.16273 | 0.0070265 | 0.001761
9 | 0.97725 | -0.15958 | 0.017428 | 0.0043679
10 | 0.97956 | -0.14314 | 0.0038526 | 0.00096555
11 | 0.99466 | -0.036931 | 0.0057831 | 0.0014494
12 | 0.99478 | -0.036087 | 0 | 0
13 | 0.99585 | -0.028642 | 0.0039565 | 0.0009916
14 | 0.99277 | -0.050081 | 0.0044743 | 0.0011214
15 | 0.99032 | -0.06714 | 0.0089977 | 0.002255
16 | 1 | 0 | -0.21607 | -0.054285
17 | 0.9869 | -0.091128 | 0 | 0
18 | 0.9812 | -0.13147 | 0 | 0
19 | 0.98078 | -0.13444 | 0 | 0
20 | 0.98284 | -0.11984 | 0 | 0
21 | 0.98431 | -0.10939 | 0.0087248 | 0.0021866
22 | 0.98264 | -0.12127 | 0.0071662 | 0.001796
23 | 0.99912 | -0.0061818 | 0.017138 | 0.0042952
24 | 0.98711 | -0.090424 | 0 | 0
25 | 0.98709 | -0.090589 | 0.0033726 | 0.00084525
26 | 0.98747 | -0.087893 | 0 | 0
27 | 0.9868 | -0.092633 | 0 | 0
28 | 0.98698 | -0.091394 | 0.0034161 | 0.00085615
29 | 0.98518 | -0.10418 | 0 | 0
30 | 0.98865 | -0.079511 | 0 | 0
31 | 0.98745 | -0.088042 | 0.00087192 | 0.00021852
32 | 0.98042 | -0.13701 | 0.0029762 | 0.0007459
33 | 0.99759 | -0.016743 | 0.0093513 | 0.0023437
34 | 0.99354 | -0.045094 | 0.013005 | 0.0032593
35 | 0.98429 | -0.11049 | 0.0032192 | 0.0008068
36 | 0.98471 | -0.10749 | 0 | 0
37 | 0.98483 | -0.10663 | 0 | 0
38 | 0.98492 | -0.10602 | 0.0027159 | 0.00068067
39 | 0.98495 | -0.10579 | 0.0068711 | 0.0017221
40 | 0.99018 | -0.068746 | 0 | 0
41 | 0.98931 | -0.074871 | 0 | 0
42 | 0.99138 | -0.060264 | 0.013077 | 0.0032775
43 | 0.98828 | -0.082179 | 0.012903 | 0.0032339
44 | 0.98857 | -0.080133 | 0.003199 | 0.00080175
45 | 0.98815 | -0.083095 | 0.012642 | 0.0031684
46 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.011513 | -0.0028854 | 0.011516 | 0.0028864 | 3.0652e-06 | 9.8082e-07 | 0.017579 | 0.017579 | 0.017579 | 0.97451 | -0.17926 | 0.97478 | -0.17734 | 6.5109
1 | -0.014771 | -0.0037023 | 0.014778 | 0.0037045 | 6.4464e-06 | 2.226e-06 | 0.022549 | 0.022549 | 0.022549 | 0.97478 | -0.17734 | 0.97521 | -0.17419 | 8.3514
2 | -0.018274 | -0.0045808 | 0.018287 | 0.0045854 | 1.2727e-05 | 4.5676e-06 | 0.027884 | 0.027884 | 0.027884 | 0.97521 | -0.17419 | 0.97592 | -0.16916 | 10.3274
3 | -0.021993 | -0.0055141 | 0.021995 | 0.0055149 | 2.1793e-06 | 7.9939e-07 | 0.033534 | 0.033534 | 0.033534 | 0.97592 | -0.16916 | 0.97602 | -0.16845 | 12.4199
4 | -0.0023668 | -0.00059317 | 0.0023669 | 0.00059307 | 7.7661e-08 | -1.0073e-07 | 0.0035289 | 0.0035288 | 0.0035289 | 0.998 | -0.013856 | 0.99803 | -0.013619 | 1.307
5 | -0.015315 | -0.0038382 | 0.015323 | 0.0038408 | 7.7033e-06 | 2.6532e-06 | 0.022834 | 0.022834 | 0.022834 | 0.99803 | -0.013619 | 0.99855 | -0.0099873 | 8.457
6 | -0.025198 | -0.0063177 | 0.025218 | 0.0063252 | 1.9967e-05 | 7.4086e-06 | 0.038418 | 0.038418 | 0.038418 | 0.97602 | -0.16845 | 0.97681 | -0.16273 | 14.2288
7 | -0.11248 | -0.028399 | 0.11264 | 0.028459 | 0.00015806 | 6.0321e-05 | 0.16769 | 0.16769 | 0.16769 | 0.99855 | -0.0099873 | 1 | 0 | 31.0537
8 | 0.097159 | 0.024558 | -0.096904 | -0.02446 | 0.00025456 | 9.7653e-05 | 0.14486 | 0.14486 | 0.14486 | 0.99855 | -0.0099873 | 0.99585 | -0.028642 | 53.6505
9 | -0.032245 | -0.0080862 | 0.032259 | 0.0080915 | 1.4093e-05 | 5.3032e-06 | 0.049121 | 0.049121 | 0.049121 | 0.97681 | -0.16273 | 0.97725 | -0.15958 | 18.1931
10 | -0.049687 | -0.012459 | 0.0498 | 0.012503 | 0.00011346 | 4.324e-05 | 0.075658 | 0.075658 | 0.075658 | 0.97725 | -0.15958 | 0.97956 | -0.14314 | 28.0215
11 | -0.053653 | -0.013468 | 0.05374 | 0.013501 | 8.709e-05 | 3.3231e-05 | 0.08151 | 0.08151 | 0.08151 | 0.97956 | -0.14314 | 0.9812 | -0.13147 | 30.189
12 | -0.0057831 | -0.0014494 | 0.0057838 | 0.0014495 | 6.7563e-07 | 7.2077e-08 | 0.0086516 | 0.0086515 | 0.0086516 | 0.99466 | -0.036931 | 0.99478 | -0.036087 | 3.2043
13 | -0.09285 | -0.023431 | 0.092947 | 0.023469 | 9.7126e-05 | 3.7252e-05 | 0.13894 | 0.13894 | 0.13894 | 0.99478 | -0.036087 | 0.99585 | -0.028642 | 51.461
14 | 0.087067 | 0.021982 | -0.086896 | -0.021916 | 0.00017084 | 6.5498e-05 | 0.13029 | 0.13029 | 0.13029 | 0.99478 | -0.036087 | 0.99277 | -0.050081 | 48.2567
15 | 0.082421 | 0.020795 | -0.082225 | -0.02072 | 0.00019679 | 7.5423e-05 | 0.12359 | 0.12359 | 0.12359 | 0.99277 | -0.050081 | 0.99032 | -0.06714 | 45.773
16 | 0.073227 | 0.018465 | -0.072982 | -0.018371 | 0.00024532 | 9.3938e-05 | 0.11007 | 0.11007 | 0.11007 | 0.99032 | -0.06714 | 0.9869 | -0.091128 | 40.7658
17 | 0.085479 | 0.021526 | -0.085279 | -0.021449 | 0.00019956 | 7.6494e-05 | 0.12723 | 0.12723 | 0.12723 | 1 | 0 | 0.99759 | -0.016743 | 47.1224
18 | 0.017153 | 0.0043003 | -0.017138 | -0.0042952 | 1.4678e-05 | 5.1721e-06 | 0.025524 | 0.025524 | 0.025524 | 1 | 0 | 0.99912 | -0.0061818 | 9.4534
19 | 0.072982 | 0.018371 | -0.072796 | -0.0183 | 0.00018568 | 7.1102e-05 | 0.11007 | 0.11007 | 0.11007 | 0.9869 | -0.091128 | 0.98431 | -0.10939 | 40.7658
20 | 0.0029784 | 0.00074452 | -0.0029772 | -0.00074526 | 1.2191e-06 | -7.4031e-07 | 0.0045162 | 0.0045166 | 0.0045166 | 0.9812 | -0.13147 | 0.98078 | -0.13444 | 1.6728
21 | -0.056718 | -0.014246 | 0.05681 | 0.014281 | 9.1929e-05 | 3.5106e-05 | 0.086026 | 0.086026 | 0.086026 | 0.9812 | -0.13147 | 0.98284 | -0.11984 | 31.8617
22 | 0.0029772 | 0.00074526 | -0.0029762 | -0.0007459 | 1.0578e-06 | -6.4136e-07 | 0.0045166 | 0.004517 | 0.004517 | 0.98078 | -0.13444 | 0.98042 | -0.13701 | 1.673
23 | 0.0071676 | 0.0017963 | -0.0071662 | -0.001796 | 1.4211e-06 | 3.0154e-07 | 0.010852 | 0.010852 | 0.010852 | 0.98284 | -0.11984 | 0.98264 | -0.12127 | 4.0192
24 | -0.063978 | -0.016077 | 0.064071 | 0.016113 | 9.3124e-05 | 3.5615e-05 | 0.096878 | 0.096878 | 0.096878 | 0.98284 | -0.11984 | 0.98431 | -0.10939 | 35.8808
25 | 0.0033727 | 0.00084522 | -0.0033726 | -0.00084525 | 7.6662e-08 | -3.1272e-08 | 0.0050841 | 0.0050841 | 0.0050841 | 0.98711 | -0.090424 | 0.98709 | -0.090589 | 1.883
26 | -0.0033727 | -0.00084522 | 0.0033739 | 0.00084474 | 1.1808e-06 | -4.8209e-07 | 0.0050841 | 0.0050838 | 0.0050841 | 0.98711 | -0.090424 | 0.98747 | -0.087893 | 1.883
27 | -0.020504 | -0.0051385 | 0.020527 | 0.0051472 | 2.3818e-05 | 8.6487e-06 | 0.030897 | 0.030897 | 0.030897 | 0.98747 | -0.087893 | 0.98865 | -0.079511 | 11.4433
28 | 0.00087193 | 0.00021832 | -0.00087192 | -0.00021852 | 1.7979e-08 | -2.0659e-07 | 0.0013138 | 0.0013139 | 0.0013139 | 0.98747 | -0.087893 | 0.98745 | -0.088042 | 0.48664
29 | 0.016258 | 0.0040755 | -0.01625 | -0.0040727 | 7.8797e-06 | 2.7617e-06 | 0.024499 | 0.024499 | 0.024499 | 0.98747 | -0.087893 | 0.98698 | -0.091394 | 9.0738
30 | -0.012832 | -0.0032158 | 0.012834 | 0.0032166 | 2.2004e-06 | 7.2597e-07 | 0.019349 | 0.019349 | 0.019349 | 0.9868 | -0.092633 | 0.98698 | -0.091394 | 7.1663
31 | 0.012832 | 0.0032158 | -0.012811 | -0.0032091 | 2.0479e-05 | 6.7586e-06 | 0.019349 | 0.019349 | 0.019349 | 0.9868 | -0.092633 | 0.98518 | -0.10418 | 7.1665
32 | 0.0059386 | 0.0014867 | -0.0059371 | -0.0014865 | 1.5079e-06 | 1.9757e-07 | 0.0089691 | 0.0089692 | 0.0089692 | 0.98518 | -0.10418 | 0.98492 | -0.10602 | 3.3219
33 | 0.0068726 | 0.0017224 | -0.0068711 | -0.0017221 | 1.5363e-06 | 3.0002e-07 | 0.01038 | 0.010381 | 0.010381 | 0.98518 | -0.10418 | 0.98495 | -0.10579 | 3.8446
34 | 0.012648 | 0.0031705 | -0.012642 | -0.0031684 | 6.2749e-06 | 2.0578e-06 | 0.019037 | 0.019037 | 0.019037 | 0.98865 | -0.079511 | 0.98815 | -0.083095 | 7.0508
35 | -0.036375 | -0.0091192 | 0.036429 | 0.0091398 | 5.4324e-05 | 2.0521e-05 | 0.054749 | 0.054749 | 0.054749 | 0.98865 | -0.079511 | 0.99018 | -0.068746 | 20.2774
36 | 0.0031993 | 0.00080161 | -0.003199 | -0.00080175 | 2.7523e-07 | -1.3806e-07 | 0.0048151 | 0.0048152 | 0.0048152 | 0.98865 | -0.079511 | 0.98857 | -0.080133 | 1.7834
37 | 0.075928 | 0.019106 | -0.075629 | -0.018991 | 0.00029918 | 0.00011458 | 0.11328 | 0.11328 | 0.11328 | 0.99759 | -0.016743 | 0.99354 | -0.045094 | 41.9563
38 | 0.062624 | 0.015732 | -0.062492 | -0.015681 | 0.00013185 | 5.0399e-05 | 0.093805 | 0.093805 | 0.093805 | 0.99354 | -0.045094 | 0.99138 | -0.060264 | 34.7426
39 | -0.0032192 | -0.0008068 | 0.0032205 | 0.00080616 | 1.3351e-06 | -6.3533e-07 | 0.0048666 | 0.0048662 | 0.0048666 | 0.98429 | -0.11049 | 0.98471 | -0.10749 | 1.8025
40 | -0.0032205 | -0.00080616 | 0.0032209 | 0.00080598 | 3.8481e-07 | -1.8334e-07 | 0.0048662 | 0.0048661 | 0.0048662 | 0.98471 | -0.10749 | 0.98483 | -0.10663 | 1.8023
41 | -0.0032209 | -0.00080598 | 0.0032212 | 0.00080585 | 2.7161e-07 | -1.2946e-07 | 0.0048661 | 0.004866 | 0.0048661 | 0.98483 | -0.10663 | 0.98492 | -0.10602 | 1.8023
42 | 0.012928 | 0.0032418 | -0.012917 | -0.0032382 | 1.0967e-05 | 3.6198e-06 | 0.019428 | 0.019428 | 0.019428 | 0.99018 | -0.068746 | 0.98931 | -0.074871 | 7.1956
43 | -0.049357 | -0.012382 | 0.049415 | 0.012404 | 5.8135e-05 | 2.2142e-05 | 0.074177 | 0.074177 | 0.074177 | 0.99018 | -0.068746 | 0.99138 | -0.060264 | 27.4728
44 | 0.012917 | 0.0032382 | -0.012903 | -0.0032339 | 1.3065e-05 | 4.3134e-06 | 0.019428 | 0.019428 | 0.019428 | 0.98931 | -0.074871 | 0.98828 | -0.082179 | 7.1957

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21607 | 0.054285

## res_load
| p_mw | q_mvar
0 | 0.011513 | 0.0028854
1 | 0.0032554 | 0.00081588
2 | 0.0034967 | 0.00087635
3 | 0.0037055 | 0.00092867
4 | 0.0023668 | 0.00059317
5 | 0.012948 | 0.0032451
6 | 0.0032035 | 0.00080287
7 | 0.0070265 | 0.001761
8 | 0.017428 | 0.0043679
9 | 0.0038526 | 0.00096555
10 | 0.0057831 | 0.0014494
11 | 0.0039565 | 0.0009916
12 | 0.0044743 | 0.0011214
13 | 0.0089977 | 0.002255
14 | 0.0087248 | 0.0021866
15 | 0.0071662 | 0.001796
16 | 0.017138 | 0.0042952
17 | 0.0033726 | 0.00084525
18 | 0.0034161 | 0.00085615
19 | 0.00087192 | 0.00021852
20 | 0.0029762 | 0.0007459
21 | 0.0093513 | 0.0023437
22 | 0.013005 | 0.0032593
23 | 0.0032192 | 0.0008068
24 | 0.0027159 | 0.00068067
25 | 0.0068711 | 0.0017221
26 | 0.013077 | 0.0032775
27 | 0.012903 | 0.0032339
28 | 0.003199 | 0.00080175
29 | 0.012642 | 0.0031684

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1