## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1102-16_1_2_node_56 | 0.4 | n |  | TRUE
1 | bus_LV_1102-16_1_2_node_50 | 0.4 | n |  | TRUE
2 | bus_LV_1102-16_1_2_node_54 | 0.4 | n |  | TRUE
3 | bus_LV_1102-16_1_2_node_59 | 0.4 | n |  | TRUE
4 | bus_LV_1102-16_1_2_node_60 | 0.4 | n |  | TRUE
5 | bus_LV_1102-16_1_2_node_77 | 0.4 | n |  | TRUE
6 | bus_LV_1102-16_1_2_node_76 | 0.4 | n |  | TRUE
7 | bus_LV_1102-16_1_2_node_37 | 0.4 | n |  | TRUE
8 | bus_LV_1102-16_1_2_node_38 | 0.4 | n |  | TRUE
9 | bus_LV_1102-16_1_2_node_39 | 0.4 | n |  | TRUE
10 | bus_LV_1102-16_1_2_node_40 | 0.4 | n |  | TRUE
11 | bus_LV_1102-16_1_2_node_41 | 0.4 | n |  | TRUE
12 | bus_LV_1102-16_1_2_node_42 | 0.4 | n |  | TRUE
13 | bus_LV_1102-16_1_2_node_43 | 0.4 | n |  | TRUE
14 | bus_LV_1102-16_1_2_node_45 | 0.4 | n |  | TRUE
15 | bus_LV_1102-16_1_2_node_44 | 0.4 | n |  | TRUE
16 | bus_LV_1102-16_1_2_node_46 | 0.4 | n |  | TRUE
17 | bus_LV_1102-16_1_2_node_69 | 0.4 | n |  | TRUE
18 | bus_LV_1102-16_1_2_node_70 | 0.4 | n |  | TRUE
19 | bus_LV_1102-16_1_2_node_67 | 0.4 | n |  | TRUE
20 | bus_LV_1102-16_1_2_node_47 | 0.4 | n |  | TRUE
21 | bus_LV_1102-16_1_2_node_48 | 0.4 | n |  | TRUE
22 | bus_LV_1102-16_1_2_node_49 | 0.4 | n |  | TRUE
23 | bus_LV_1102-16_1_2_node_51 | 0.4 | n |  | TRUE
24 | bus_LV_1102-16_1_2_node_52 | 0.4 | n |  | TRUE
25 | bus_LV_1102-16_1_2_node_53 | 0.4 | n |  | TRUE
26 | bus_LV_1102-16_1_2_node_55 | 0.4 | n |  | TRUE
27 | bus_LV_1102-16_1_2_node_57 | 0.4 | n |  | TRUE
28 | bus_LV_1102-16_1_2_node_58 | 0.4 | n |  | TRUE
29 | bus_LV_1102-16_1_2_node_71 | 0.4 | n |  | TRUE
30 | bus_LV_1102-16_1_2_node_61 | 0.4 | n |  | TRUE
31 | bus_LV_1102-16_1_2_node_62 | 0.4 | n |  | TRUE
32 | bus_LV_1102-16_1_2_node_73 | 0.4 | n |  | TRUE
33 | bus_LV_1102-16_1_2_node_63 | 0.4 | n |  | TRUE
34 | bus_LV_1102-16_1_2_node_74 | 0.4 | n |  | TRUE
35 | bus_LV_1102-16_1_2_node_64 | 0.4 | n |  | TRUE
36 | bus_LV_1102-16_1_2_node_68 | 0.4 | n |  | TRUE
37 | bus_LV_1102-16_1_2_node_65 | 0.4 | n |  | TRUE
38 | bus_LV_1102-16_1_2_node_72 | 0.4 | n |  | TRUE
39 | bus_LV_1102-16_1_2_node_66 | 0.4 | n |  | TRUE
40 | bus_LV_1102-16_1_2_node_75 | 0.4 | n |  | TRUE
41 | bus_MV_354_0_node_66 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1102-16_1_2_load_50 | 1 | 0.00049606 | 0.00012432 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1102-16_1_2_load_54 | 2 | 0.0042867 | 0.0010744 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1102-16_1_2_load_59 | 3 | 0.0036491 | 0.00091455 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1102-16_1_2_load_77 | 5 | 0.0034097 | 0.00085454 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1102-16_1_2_load_76 | 6 | 0.0028779 | 0.00072128 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1102-16_1_2_load_37 | 7 | 0.0041555 | 0.0010415 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1102-16_1_2_load_38 | 8 | 0.0028725 | 0.00071991 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1102-16_1_2_load_39 | 9 | 0.0040363 | 0.0010116 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1102-16_1_2_load_41 | 11 | 0.0023377 | 0.00058588 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1102-16_1_2_load_42 | 12 | 0.00411 | 0.0010301 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1102-16_1_2_load_43 | 13 | 0.0043655 | 0.0010941 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1102-16_1_2_load_45 | 14 | 0.0057792 | 0.0014484 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1102-16_1_2_load_44 | 15 | 0.0034938 | 0.00087563 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1102-16_1_2_load_46 | 16 | 0.0049653 | 0.0012444 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1102-16_1_2_load_70 | 18 | 0.00066043 | 0.00016552 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1102-16_1_2_load_67 | 19 | 0.00073243 | 0.00018357 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1102-16_1_2_load_47 | 20 | 0.0014708 | 0.00036861 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1102-16_1_2_load_48 | 21 | 0.00049351 | 0.00012369 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1102-16_1_2_load_51 | 23 | 0.00059756 | 0.00014976 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1102-16_1_2_load_52 | 24 | 0.00040438 | 0.00010135 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1102-16_1_2_load_53 | 25 | 0.0015645 | 0.00039211 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1102-16_1_2_load_55 | 26 | 0.0017375 | 0.00043547 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1102-16_1_2_load_57 | 27 | 0.00069831 | 0.00017501 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1102-16_1_2_load_71 | 29 | 0.0010829 | 0.00027141 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1102-16_1_2_load_62 | 31 | 0.0026948 | 0.00067538 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1102-16_1_2_load_73 | 32 | 0.0049695 | 0.0012455 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1102-16_1_2_load_63 | 33 | 0.0034571 | 0.00086644 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1102-16_1_2_load_74 | 34 | 0.0022023 | 0.00055195 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1102-16_1_2_load_68 | 36 | 0.0035004 | 0.00087728 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1102-16_1_2_load_65 | 37 | 0.0036816 | 0.00092271 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1102-16_1_2_load_72 | 38 | 0.0047966 | 0.0012021 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1102-16_1_2_load_66 | 39 | 0.00092771 | 0.00023251 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1102-16_1_2_load_75 | 40 | 0.0025761 | 0.00064563 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 36 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1102-16_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.02447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1102-16_1_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.03499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1102-16_1_2_line_2 | NAYY 4x150 SE | 1 | 21 | 0.022027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1102-16_1_2_line_3 | NAYY 4x150 SE | 2 | 25 | 0.015924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1102-16_1_2_line_4 | NAYY 4x150 SE | 3 | 4 | 0.017493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1102-16_1_2_line_5 | NAYY 4x150 SE | 4 | 30 | 0.009636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1102-16_1_2_line_6 | NAYY 4x150 SE | 4 | 31 | 0.028731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1102-16_1_2_line_7 | NAYY 4x150 SE | 5 | 6 | 0.016153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1102-16_1_2_line_8 | NAYY 4x150 SE | 6 | 30 | 0.031215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1102-16_1_2_line_9 | NAYY 4x150 SE | 7 | 8 | 0.004715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1102-16_1_2_line_10 | NAYY 4x150 SE | 8 | 9 | 0.0059418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1102-16_1_2_line_11 | NAYY 4x150 SE | 9 | 10 | 0.015241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1102-16_1_2_line_12 | NAYY 4x150 SE | 10 | 11 | 0.023387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1102-16_1_2_line_13 | NAYY 4x150 SE | 10 | 12 | 0.011147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1102-16_1_2_line_14 | NAYY 4x150 SE | 11 | 13 | 0.024219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1102-16_1_2_line_15 | NAYY 4x150 SE | 12 | 14 | 0.013966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1102-16_1_2_line_16 | NAYY 4x150 SE | 13 | 15 | 0.027036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1102-16_1_2_line_17 | NAYY 4x150 SE | 14 | 16 | 0.046252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1102-16_1_2_line_18 | NAYY 4x150 SE | 15 | 17 | 0.014992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1102-16_1_2_line_19 | NAYY 4x150 SE | 17 | 18 | 0.010171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1102-16_1_2_line_20 | NAYY 4x150 SE | 17 | 19 | 0.01321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1102-16_1_2_line_21 | NAYY 4x150 SE | 18 | 28 | 0.02798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1102-16_1_2_line_22 | NAYY 4x150 SE | 19 | 39 | 0.0018637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1102-16_1_2_line_23 | NAYY 4x150 SE | 20 | 21 | 0.12135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1102-16_1_2_line_24 | NAYY 4x150 SE | 20 | 22 | 0.039995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1102-16_1_2_line_25 | NAYY 4x150 SE | 22 | 23 | 0.025722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1102-16_1_2_line_26 | NAYY 4x150 SE | 23 | 24 | 0.028895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1102-16_1_2_line_27 | NAYY 4x150 SE | 25 | 26 | 0.041276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1102-16_1_2_line_28 | NAYY 4x150 SE | 26 | 27 | 0.08126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1102-16_1_2_line_29 | NAYY 4x150 SE | 27 | 28 | 0.018763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1102-16_1_2_line_30 | NAYY 4x150 SE | 28 | 29 | 0.037277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1102-16_1_2_line_31 | NAYY 4x150 SE | 30 | 32 | 0.0055382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1102-16_1_2_line_32 | NAYY 4x150 SE | 31 | 33 | 0.0033036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1102-16_1_2_line_33 | NAYY 4x150 SE | 32 | 34 | 0.015634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1102-16_1_2_line_34 | NAYY 4x150 SE | 33 | 35 | 0.014896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1102-16_1_2_line_35 | NAYY 4x150 SE | 34 | 40 | 0.0088231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1102-16_1_2_line_36 | NAYY 4x150 SE | 35 | 36 | 0.013919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1102-16_1_2_line_37 | NAYY 4x150 SE | 35 | 37 | 0.0025717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1102-16_1_2_line_38 | NAYY 4x150 SE | 36 | 38 | 0.019884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1102-16_1_2_line_39 | NAYY 4x150 SE | 37 | 39 | 0.023227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1102-16_1_2_trafo_68 | 0.25 MVA 20/0.4 kV | 41 | 36 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2657890.5916 | 1220067.8327 | 2657914.8706 | 1220064.7835
1 | 2657890.5916 | 1220067.8327 | 2657874.26 | 1220036.8882
2 | 2657914.8706 | 1220064.7835 | 2657928.4702 | 1220063.0756 | 2657936.7261 | 1220062.0409
3 | 2657882.6172 | 1220023.3331 | 2657874.26 | 1220036.8882 | 2657874.26 | 1220036.8882
4 | 2657744.293 | 1219957.4672 | 2657752.2147 | 1219973.0638
5 | 2657739.5332 | 1219949.0826 | 2657744.293 | 1219957.4672
6 | 2657744.293 | 1219957.4672 | 2657768.9539 | 1219942.7254
7 | 2657694.4034 | 1219963.4599 | 2657709.836 | 1219958.6902
8 | 2657739.5332 | 1219949.0826 | 2657733.938 | 1219950.9518 | 2657723.0215 | 1219954.615 | 2657709.836 | 1219958.6902
9 | 2657765.3231 | 1219815.4758 | 2657767.998 | 1219816.5875 | 2657769.2727 | 1219817.8842
10 | 2657773.438 | 1219822.1214 | 2657769.2727 | 1219817.8842
11 | 2657773.0876 | 1219837.1273 | 2657774.5907 | 1219829.237 | 2657773.438 | 1219822.1214
12 | 2657773.0876 | 1219837.1273 | 2657786.0905 | 1219853.0744 | 2657787.4989 | 1219855.5062
13 | 2657773.0876 | 1219837.1273 | 2657766.9227 | 1219842.9601 | 2657764.6073 | 1219844.2689
14 | 2657787.4989 | 1219855.5062 | 2657793.0908 | 1219865.1609 | 2657799.495 | 1219876.5453
15 | 2657752.4476 | 1219851.1376 | 2657753.4255 | 1219850.5896 | 2657764.6073 | 1219844.2689
16 | 2657812.7505 | 1219900.1087 | 2657799.495 | 1219876.5453
17 | 2657752.4476 | 1219851.1376 | 2657712.0992 | 1219873.7495
18 | 2657820.1007 | 1219913.1748 | 2657812.7505 | 1219900.1087
19 | 2657820.1007 | 1219913.1748 | 2657828.9909 | 1219908.2341
20 | 2657820.1007 | 1219913.1748 | 2657808.6187 | 1219919.7076
21 | 2657853.4475 | 1219894.6425 | 2657828.9909 | 1219908.2341
22 | 2657806.9988 | 1219920.6292 | 2657808.6187 | 1219919.7076
23 | 2658055.1061 | 1220037.2563 | 2658051.3931 | 1220038.7677 | 2658024.7358 | 1220047.4913 | 2657985.6832 | 1220055.9053 | 2657936.7261 | 1220062.0409
24 | 2658092.1495 | 1220022.1768 | 2658055.1061 | 1220037.2563
25 | 2658092.1495 | 1220022.1768 | 2658099.7874 | 1220034.1475 | 2658106.2326 | 1220043.6986
26 | 2658106.2326 | 1220043.6986 | 2658116.0855 | 1220058.2992 | 2658121.9797 | 1220067.9175
27 | 2657882.6172 | 1220023.3331 | 2657895.5531 | 1220002.3514 | 2657893.9083 | 1219985.8063
28 | 2657893.9083 | 1219985.8063 | 2657893.5141 | 1219981.8411 | 2657885.9782 | 1219961.6665 | 2657864.9821 | 1219917.98 | 2657861.7611 | 1219911.4631
29 | 2657853.4475 | 1219894.6425 | 2657861.7611 | 1219911.4631
30 | 2657853.4475 | 1219894.6425 | 2657858.4588 | 1219886.4972 | 2657861.1452 | 1219877.0952 | 2657867.2223 | 1219860.2209
31 | 2657739.5332 | 1219949.0826 | 2657736.8087 | 1219944.2609
32 | 2657768.9539 | 1219942.7254 | 2657771.7895 | 1219941.0303
33 | 2657736.8087 | 1219944.2609 | 2657729.1179 | 1219930.6496
34 | 2657784.5753 | 1219933.3872 | 2657771.7895 | 1219941.0303
35 | 2657724.7775 | 1219922.9679 | 2657729.1179 | 1219930.6496
36 | 2657784.5753 | 1219933.3872 | 2657777.7316 | 1219921.2668
37 | 2657784.5753 | 1219933.3872 | 2657786.8105 | 1219932.1155
38 | 2657767.955 | 1219903.9523 | 2657777.7316 | 1219921.2668
39 | 2657786.8105 | 1219932.1155 | 2657806.9988 | 1219920.6292

## bus_geodata
| x | y | coords
0 | 2657890.5916 | 1220067.8327
1 | 2657914.8706 | 1220064.7835
2 | 2657874.26 | 1220036.8882
3 | 2657752.2147 | 1219973.0638
4 | 2657744.293 | 1219957.4672
5 | 2657694.4034 | 1219963.4599
6 | 2657709.836 | 1219958.6902
7 | 2657765.3231 | 1219815.4758
8 | 2657769.2727 | 1219817.8842
9 | 2657773.438 | 1219822.1214
10 | 2657773.0876 | 1219837.1273
11 | 2657787.4989 | 1219855.5062
12 | 2657764.6073 | 1219844.2689
13 | 2657799.495 | 1219876.5453
14 | 2657752.4476 | 1219851.1376
15 | 2657812.7505 | 1219900.1087
16 | 2657712.0992 | 1219873.7495
17 | 2657820.1007 | 1219913.1748
18 | 2657828.9909 | 1219908.2341
19 | 2657808.6187 | 1219919.7076
20 | 2658055.1061 | 1220037.2563
21 | 2657936.7261 | 1220062.0409
22 | 2658092.1495 | 1220022.1768
23 | 2658106.2326 | 1220043.6986
24 | 2658121.9797 | 1220067.9175
25 | 2657882.6172 | 1220023.3331
26 | 2657893.9083 | 1219985.8063
27 | 2657861.7611 | 1219911.4631
28 | 2657853.4475 | 1219894.6425
29 | 2657867.2223 | 1219860.2209
30 | 2657739.5332 | 1219949.0826
31 | 2657768.9539 | 1219942.7254
32 | 2657736.8087 | 1219944.2609
33 | 2657771.7895 | 1219941.0303
34 | 2657729.1179 | 1219930.6496
35 | 2657784.5753 | 1219933.3872
36 | 2657777.7316 | 1219921.2668
37 | 2657786.8105 | 1219932.1155
38 | 2657767.955 | 1219903.9523
39 | 2657806.9988 | 1219920.6292
40 | 2657724.7775 | 1219922.9679
41 | 2657784.5753 | 1219933.3872

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99218 | -0.054944 | 0 | 0
1 | 0.99205 | -0.055809 | 0.00049606 | 0.00012432
2 | 0.99235 | -0.053707 | 0.0042867 | 0.0010744
3 | 0.99683 | -0.022172 | 0.0036491 | 0.00091455
4 | 0.99692 | -0.02153 | 0 | 0
5 | 0.99634 | -0.02561 | 0.0034097 | 0.00085454
6 | 0.99642 | -0.025057 | 0.0028779 | 0.00072128
7 | 0.99116 | -0.061977 | 0.0041555 | 0.0010415
8 | 0.99119 | -0.061778 | 0.0028725 | 0.00071991
9 | 0.99125 | -0.061353 | 0.0040363 | 0.0010116
10 | 0.9915 | -0.059641 | 0 | 0
11 | 0.99237 | -0.05349 | 0.0023377 | 0.00058588
12 | 0.99126 | -0.061323 | 0.00411 | 0.0010301
13 | 0.99335 | -0.046558 | 0.0043655 | 0.0010941
14 | 0.99104 | -0.062848 | 0.0057792 | 0.0014484
15 | 0.99462 | -0.037645 | 0.0034938 | 0.00087563
16 | 0.99071 | -0.065183 | 0.0049653 | 0.0012444
17 | 0.9954 | -0.032184 | 0 | 0
18 | 0.9952 | -0.033572 | 0.00066043 | 0.00016552
19 | 0.99634 | -0.02558 | 0.00073243 | 0.00018357
20 | 0.99153 | -0.05954 | 0.0014708 | 0.00036861
21 | 0.99196 | -0.056477 | 0.00049351 | 0.00012369
22 | 0.99147 | -0.059949 | 0 | 0
23 | 0.99143 | -0.060212 | 0.00059756 | 0.00014976
24 | 0.99142 | -0.060331 | 0.00040438 | 0.00010135
25 | 0.99253 | -0.052451 | 0.0015645 | 0.00039211
26 | 0.99308 | -0.048545 | 0.0017375 | 0.00043547
27 | 0.99437 | -0.039438 | 0.00069831 | 0.00017501
28 | 0.99468 | -0.037206 | 0 | 0
29 | 0.99463 | -0.037613 | 0.0010829 | 0.00027141
30 | 0.9967 | -0.023083 | 0 | 0
31 | 0.99773 | -0.015852 | 0.0026948 | 0.00067538
32 | 0.99662 | -0.023626 | 0.0049695 | 0.0012455
33 | 0.99784 | -0.015111 | 0.0034571 | 0.00086644
34 | 0.99652 | -0.024377 | 0.0022023 | 0.00055195
35 | 0.99839 | -0.011253 | 0 | 0
36 | 1 | 0 | -0.086862 | -0.021621
37 | 0.99818 | -0.01267 | 0.0036816 | 0.00092271
38 | 0.99986 | -0.00095219 | 0.0047966 | 0.0012021
39 | 0.99647 | -0.024635 | 0.00092771 | 0.00023251
40 | 0.99648 | -0.024605 | 0.0025761 | 0.00064563
41 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0034641 | 0.00086504 | -0.0034637 | -0.0008652 | 4.1196e-07 | -1.5754e-07 | 0.0051942 | 0.0051943 | 0.0051943 | 0.99218 | -0.054944 | 0.99205 | -0.055809 | 1.9238
1 | -0.0034641 | -0.00086504 | 0.0034647 | 0.00086482 | 5.8904e-07 | -2.2541e-07 | 0.0051942 | 0.005194 | 0.0051942 | 0.99218 | -0.054944 | 0.99235 | -0.053707 | 1.9238
2 | 0.0029676 | 0.00074087 | -0.0029674 | -0.00074105 | 2.7222e-07 | -1.7968e-07 | 0.0044502 | 0.0044503 | 0.0044503 | 0.99205 | -0.055809 | 0.99196 | -0.056477 | 1.6483
3 | -0.0077514 | -0.0019392 | 0.0077528 | 0.0019395 | 1.3421e-06 | 3.1044e-07 | 0.011622 | 0.011622 | 0.011622 | 0.99235 | -0.053707 | 0.99253 | -0.052451 | 4.3044
4 | -0.0036491 | -0.00091455 | 0.0036494 | 0.00091445 | 3.2388e-07 | -1.0349e-07 | 0.0054472 | 0.0054471 | 0.0054472 | 0.99683 | -0.022172 | 0.99692 | -0.02153 | 2.0175
5 | 0.016042 | 0.0040203 | -0.016039 | -0.0040191 | 3.4475e-06 | 1.2003e-06 | 0.023945 | 0.023945 | 0.023945 | 0.99692 | -0.02153 | 0.9967 | -0.023083 | 8.8684
6 | -0.019692 | -0.0049348 | 0.019707 | 0.0049404 | 1.5488e-05 | 5.5819e-06 | 0.029392 | 0.029392 | 0.029392 | 0.99692 | -0.02153 | 0.99773 | -0.015852 | 10.8859
7 | -0.0034097 | -0.00085454 | 0.0034099 | 0.00085443 | 2.6137e-07 | -1.0986e-07 | 0.0050923 | 0.0050922 | 0.0050923 | 0.99634 | -0.02561 | 0.99642 | -0.025057 | 1.886
8 | -0.0062879 | -0.0015757 | 0.0062896 | 0.001576 | 1.7174e-06 | 2.5383e-07 | 0.00939 | 0.0093898 | 0.00939 | 0.99642 | -0.025057 | 0.9967 | -0.023083 | 3.4778
9 | -0.0041555 | -0.0010415 | 0.0041556 | 0.0010414 | 1.145e-07 | -1.673e-08 | 0.0062385 | 0.0062385 | 0.0062385 | 0.99116 | -0.061977 | 0.99119 | -0.061778 | 2.3106
10 | -0.0070281 | -0.0017613 | 0.0070285 | 0.0017614 | 4.1273e-07 | 8.2153e-08 | 0.010551 | 0.010551 | 0.010551 | 0.99119 | -0.061778 | 0.99125 | -0.061353 | 3.9077
11 | -0.011065 | -0.002773 | 0.011067 | 0.0027738 | 2.6237e-06 | 8.126e-07 | 0.01661 | 0.01661 | 0.01661 | 0.99125 | -0.061353 | 0.9915 | -0.059641 | 6.1518
12 | -0.025929 | -0.0064986 | 0.025951 | 0.0065068 | 2.2098e-05 | 8.1975e-06 | 0.038914 | 0.038914 | 0.038914 | 0.9915 | -0.059641 | 0.99237 | -0.05349 | 14.4126
13 | 0.014862 | 0.0037248 | -0.014858 | -0.0037236 | 3.4602e-06 | 1.1871e-06 | 0.022304 | 0.022304 | 0.022304 | 0.9915 | -0.059641 | 0.99126 | -0.061323 | 8.2609
14 | -0.028289 | -0.0070927 | 0.028316 | 0.0071028 | 2.7194e-05 | 1.0146e-05 | 0.042419 | 0.042419 | 0.042419 | 0.99237 | -0.05349 | 0.99335 | -0.046558 | 15.7108
15 | 0.010748 | 0.0026935 | -0.010746 | -0.0026928 | 2.2686e-06 | 6.9256e-07 | 0.016135 | 0.016135 | 0.016135 | 0.99126 | -0.061323 | 0.99104 | -0.062848 | 5.9758
16 | -0.032682 | -0.0081969 | 0.032722 | 0.0082121 | 4.0437e-05 | 1.5202e-05 | 0.048959 | 0.048958 | 0.048959 | 0.99335 | -0.046558 | 0.99462 | -0.037645 | 18.1328
17 | 0.0049669 | 0.0012444 | -0.0049653 | -0.0012444 | 1.6051e-06 | 2.1584e-08 | 0.0074575 | 0.0074577 | 0.0074577 | 0.99104 | -0.062848 | 0.99071 | -0.065183 | 2.7621
18 | -0.036216 | -0.0090878 | 0.036243 | 0.0090981 | 2.7466e-05 | 1.0369e-05 | 0.054185 | 0.054185 | 0.054185 | 0.99462 | -0.037645 | 0.9954 | -0.032184 | 20.0686
19 | 0.013528 | 0.0033884 | -0.013526 | -0.0033875 | 2.5954e-06 | 8.6607e-07 | 0.020223 | 0.020223 | 0.020223 | 0.9954 | -0.032184 | 0.9952 | -0.033572 | 7.4898
20 | -0.049772 | -0.012487 | 0.049817 | 0.012504 | 4.5639e-05 | 1.7382e-05 | 0.074408 | 0.074408 | 0.074408 | 0.9954 | -0.032184 | 0.99634 | -0.02558 | 27.5584
21 | 0.012865 | 0.003222 | -0.012859 | -0.0032199 | 6.4598e-06 | 2.1212e-06 | 0.019235 | 0.019235 | 0.019235 | 0.9952 | -0.033572 | 0.99468 | -0.037206 | 7.1242
22 | -0.05055 | -0.012687 | 0.050556 | 0.01269 | 6.6295e-06 | 2.5255e-06 | 0.075502 | 0.075502 | 0.075502 | 0.99634 | -0.02558 | 0.99647 | -0.024635 | 27.9636
23 | -0.0024728 | -0.00061853 | 0.0024738 | 0.00061737 | 1.0424e-06 | -1.1649e-06 | 0.0037106 | 0.00371 | 0.0037106 | 0.99153 | -0.05954 | 0.99196 | -0.056477 | 1.3743
24 | 0.001002 | 0.00024993 | -0.001002 | -0.00025042 | 5.6412e-08 | -4.9413e-07 | 0.0015034 | 0.0015035 | 0.0015035 | 0.99153 | -0.05954 | 0.99147 | -0.059949 | 0.55687
25 | 0.001002 | 0.00025042 | -0.0010019 | -0.00025074 | 3.6287e-08 | -3.1776e-07 | 0.0015035 | 0.0015037 | 0.0015037 | 0.99147 | -0.059949 | 0.99143 | -0.060212 | 0.55691
26 | 0.00040438 | 0.00010098 | -0.00040438 | -0.00010135 | 6.6403e-09 | -3.7005e-07 | 0.0006068 | 0.00060693 | 0.00060693 | 0.99143 | -0.060212 | 0.99142 | -0.060331 | 0.22479
27 | -0.0093173 | -0.0023316 | 0.0093223 | 0.002333 | 5.0247e-06 | 1.3988e-06 | 0.013967 | 0.013967 | 0.013967 | 0.99253 | -0.052451 | 0.99308 | -0.048545 | 5.1731
28 | -0.01106 | -0.0027685 | 0.011074 | 0.0027728 | 1.3923e-05 | 4.3023e-06 | 0.016571 | 0.01657 | 0.016571 | 0.99308 | -0.048545 | 0.99437 | -0.039438 | 6.1373
29 | -0.011772 | -0.0029478 | 0.011776 | 0.0029489 | 3.633e-06 | 1.1538e-06 | 0.017615 | 0.017615 | 0.017615 | 0.99437 | -0.039438 | 0.99468 | -0.037206 | 6.5242
30 | 0.001083 | 0.00027095 | -0.0010829 | -0.00027141 | 6.1049e-08 | -4.6035e-07 | 0.00162 | 0.0016201 | 0.0016201 | 0.99468 | -0.037206 | 0.99463 | -0.037613 | 0.60005
31 | 0.0097492 | 0.0024432 | -0.0097485 | -0.002443 | 7.3211e-07 | 2.0941e-07 | 0.014555 | 0.014555 | 0.014555 | 0.9967 | -0.023083 | 0.99662 | -0.023626 | 5.3907
32 | -0.022402 | -0.0056157 | 0.022404 | 0.0056166 | 2.3011e-06 | 8.419e-07 | 0.033411 | 0.033411 | 0.033411 | 0.99773 | -0.015852 | 0.99784 | -0.015111 | 12.3743
33 | 0.004779 | 0.0011975 | -0.0047785 | -0.0011975 | 4.9667e-07 | -1.2674e-08 | 0.0071352 | 0.0071353 | 0.0071353 | 0.99662 | -0.023626 | 0.99652 | -0.024377 | 2.6427
34 | -0.025861 | -0.006483 | 0.025875 | 0.0064881 | 1.3825e-05 | 5.1227e-06 | 0.038566 | 0.038566 | 0.038566 | 0.99784 | -0.015111 | 0.99839 | -0.011253 | 14.2838
35 | 0.0025762 | 0.00064555 | -0.0025761 | -0.00064563 | 8.147e-08 | -8.361e-08 | 0.0038468 | 0.0038468 | 0.0038468 | 0.99652 | -0.024377 | 0.99648 | -0.024605 | 1.4247
36 | -0.081137 | -0.02037 | 0.081264 | 0.020419 | 0.00012704 | 4.8679e-05 | 0.12094 | 0.12094 | 0.12094 | 0.99839 | -0.011253 | 1 | 0 | 44.793
37 | 0.055262 | 0.013882 | -0.055251 | -0.013878 | 1.0889e-05 | 4.1545e-06 | 0.082375 | 0.082375 | 0.082375 | 0.99839 | -0.011253 | 0.99818 | -0.01267 | 30.5093
38 | 0.0047972 | 0.0012021 | -0.0047966 | -0.0012021 | 6.3223e-07 | -1.7664e-08 | 0.0071382 | 0.0071383 | 0.0071383 | 1 | 0 | 0.99986 | -0.00095219 | 2.6438
39 | 0.05157 | 0.012955 | -0.051484 | -0.012922 | 8.5681e-05 | 3.2651e-05 | 0.076887 | 0.076887 | 0.076887 | 0.99818 | -0.01267 | 0.99647 | -0.024635 | 28.4766

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.090362 | 0.022498

## res_load
| p_mw | q_mvar
0 | 0.00049606 | 0.00012432
1 | 0.0042867 | 0.0010744
2 | 0.0036491 | 0.00091455
3 | 0.0034097 | 0.00085454
4 | 0.0028779 | 0.00072128
5 | 0.0041555 | 0.0010415
6 | 0.0028725 | 0.00071991
7 | 0.0040363 | 0.0010116
8 | 0.0023377 | 0.00058588
9 | 0.00411 | 0.0010301
10 | 0.0043655 | 0.0010941
11 | 0.0057792 | 0.0014484
12 | 0.0034938 | 0.00087563
13 | 0.0049653 | 0.0012444
14 | 0.00066043 | 0.00016552
15 | 0.00073243 | 0.00018357
16 | 0.0014708 | 0.00036861
17 | 0.00049351 | 0.00012369
18 | 0.00059756 | 0.00014976
19 | 0.00040438 | 0.00010135
20 | 0.0015645 | 0.00039211
21 | 0.0017375 | 0.00043547
22 | 0.00069831 | 0.00017501
23 | 0.0010829 | 0.00027141
24 | 0.0026948 | 0.00067538
25 | 0.0049695 | 0.0012455
26 | 0.0034571 | 0.00086644
27 | 0.0022023 | 0.00055195
28 | 0.0035004 | 0.00087728
29 | 0.0036816 | 0.00092271
30 | 0.0047966 | 0.0012021
31 | 0.00092771 | 0.00023251
32 | 0.0025761 | 0.00064563

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1