## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1102-21_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1102-21_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1102-21_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1102-21_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1102-21_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1102-21_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1102-21_0_4_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_1102-21_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_1102-21_0_4_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_1102-21_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1102-21_0_4_node_40 | 0.4 | n |  | TRUE
11 | bus_LV_1102-21_0_4_node_45 | 0.4 | n |  | TRUE
12 | bus_LV_1102-21_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1102-21_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1102-21_0_4_node_41 | 0.4 | n |  | TRUE
15 | bus_LV_1102-21_0_4_node_44 | 0.4 | n |  | TRUE
16 | bus_LV_1102-21_0_4_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_1102-21_0_4_node_39 | 0.4 | n |  | TRUE
18 | bus_LV_1102-21_0_4_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_1102-21_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1102-21_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1102-21_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1102-21_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1102-21_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1102-21_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1102-21_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1102-21_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1102-21_0_4_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_1102-21_0_4_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_1102-21_0_4_node_47 | 0.4 | n |  | TRUE
30 | bus_LV_1102-21_0_4_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_1102-21_0_4_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_1102-21_0_4_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_1102-21_0_4_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_1102-21_0_4_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_1102-21_0_4_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_1102-21_0_4_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_1102-21_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_1102-21_0_4_node_49 | 0.4 | n |  | TRUE
39 | bus_LV_1102-21_0_4_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_1102-21_0_4_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_1102-21_0_4_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_1102-21_0_4_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_1102-21_0_4_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_1102-21_0_4_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_1102-21_0_4_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_1102-21_0_4_node_42 | 0.4 | n |  | TRUE
47 | bus_LV_1102-21_0_4_node_37 | 0.4 | n |  | TRUE
48 | bus_MV_354_0_node_84 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1102-21_0_4_load_0 | 0 | 0.003919 | 0.0009822 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1102-21_0_4_load_1 | 1 | 0.0033144 | 0.00083066 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1102-21_0_4_load_3 | 3 | 0.0032858 | 0.00082351 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1102-21_0_4_load_5 | 5 | 0.003934 | 0.00098596 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1102-21_0_4_load_8 | 6 | 0.0079314 | 0.0019878 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1102-21_0_4_load_9 | 7 | 0.0075094 | 0.001882 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1102-21_0_4_load_10 | 8 | 0.0070468 | 0.0017661 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1102-21_0_4_load_6 | 9 | 0.0033124 | 0.00083015 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1102-21_0_4_load_40 | 10 | 0.007627 | 0.0019115 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1102-21_0_4_load_45 | 11 | 0.0051809 | 0.0012984 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1102-21_0_4_load_7 | 12 | 0.0034134 | 0.00085547 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1102-21_0_4_load_11 | 13 | 0.0062046 | 0.001555 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1102-21_0_4_load_44 | 15 | 0.0087797 | 0.0022004 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1102-21_0_4_load_38 | 16 | 0.0052211 | 0.0013085 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1102-21_0_4_load_39 | 17 | 0.0037744 | 0.00094596 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1102-21_0_4_load_34 | 18 | 0.0099549 | 0.0024949 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1102-21_0_4_load_13 | 19 | 0.0034362 | 0.0008612 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1102-21_0_4_load_14 | 20 | 0.0063871 | 0.0016008 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1102-21_0_4_load_15 | 22 | 0.0025791 | 0.00064638 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1102-21_0_4_load_18 | 25 | 0.005045 | 0.0012644 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1102-21_0_4_load_20 | 27 | 0.0030679 | 0.00076888 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1102-21_0_4_load_21 | 28 | 0.0098802 | 0.0024762 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1102-21_0_4_load_47 | 29 | 0.0050401 | 0.0012632 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1102-21_0_4_load_22 | 30 | 0.0029059 | 0.00072829 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1102-21_0_4_load_29 | 31 | 0.0091373 | 0.00229 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1102-21_0_4_load_23 | 32 | 0.002794 | 0.00070023 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1102-21_0_4_load_30 | 33 | 0.010689 | 0.0026789 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1102-21_0_4_load_25 | 35 | 0.0086879 | 0.0021774 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1102-21_0_4_load_27 | 37 | 0.0087582 | 0.002195 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1102-21_0_4_load_49 | 38 | 0.009076 | 0.0022747 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1102-21_0_4_load_31 | 40 | 0.012256 | 0.0030717 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1102-21_0_4_load_33 | 42 | 0.0032276 | 0.00080891 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1102-21_0_4_load_35 | 43 | 0.012195 | 0.0030564 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1102-21_0_4_load_43 | 44 | 0.0055773 | 0.0013978 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1102-21_0_4_load_42 | 46 | 0.0068523 | 0.0017173 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1102-21_0_4_load_37 | 47 | 0.0038615 | 0.00096778 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1102-21_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.012789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1102-21_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0051129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1102-21_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.019469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1102-21_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.039516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1102-21_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.018986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1102-21_0_4_line_5 | NAYY 4x150 SE | 3 | 9 | 0.018869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1102-21_0_4_line_6 | NAYY 4x150 SE | 4 | 10 | 0.028159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1102-21_0_4_line_7 | NAYY 4x150 SE | 5 | 11 | 0.026008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1102-21_0_4_line_8 | NAYY 4x150 SE | 6 | 7 | 0.017781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1102-21_0_4_line_9 | NAYY 4x150 SE | 6 | 8 | 0.0078065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1102-21_0_4_line_10 | NAYY 4x150 SE | 7 | 13 | 0.004039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1102-21_0_4_line_11 | NAYY 4x150 SE | 8 | 21 | 0.017103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_1102-21_0_4_line_12 | NAYY 4x150 SE | 9 | 12 | 0.021612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1102-21_0_4_line_13 | NAYY 4x150 SE | 10 | 14 | 0.013314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1102-21_0_4_line_14 | NAYY 4x150 SE | 11 | 15 | 0.02296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1102-21_0_4_line_15 | NAYY 4x150 SE | 13 | 19 | 0.021468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1102-21_0_4_line_16 | NAYY 4x150 SE | 14 | 46 | 0.020067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1102-21_0_4_line_17 | NAYY 4x150 SE | 15 | 44 | 0.02889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1102-21_0_4_line_18 | NAYY 4x150 SE | 16 | 17 | 0.020943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_1102-21_0_4_line_19 | NAYY 4x150 SE | 16 | 18 | 0.024256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_1102-21_0_4_line_20 | NAYY 4x150 SE | 17 | 21 | 0.043216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_1102-21_0_4_line_21 | NAYY 4x150 SE | 18 | 41 | 0.063588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_1102-21_0_4_line_22 | NAYY 4x150 SE | 19 | 20 | 0.0081033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1102-21_0_4_line_23 | NAYY 4x150 SE | 22 | 23 | 0.023101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1102-21_0_4_line_24 | NAYY 4x150 SE | 22 | 24 | 0.028487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1102-21_0_4_line_25 | NAYY 4x150 SE | 23 | 25 | 0.027578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1102-21_0_4_line_26 | NAYY 4x150 SE | 23 | 26 | 0.046819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1102-21_0_4_line_27 | NAYY 4x150 SE | 24 | 27 | 0.019821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_1102-21_0_4_line_28 | NAYY 4x150 SE | 24 | 28 | 0.046447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
29 | LV_1102-21_0_4_line_29 | NAYY 4x150 SE | 26 | 29 | 0.021652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1102-21_0_4_line_30 | NAYY 4x150 SE | 27 | 30 | 0.015333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_1102-21_0_4_line_31 | NAYY 4x150 SE | 28 | 31 | 0.041949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_1102-21_0_4_line_32 | NAYY 4x150 SE | 30 | 32 | 0.0083856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_1102-21_0_4_line_33 | NAYY 4x150 SE | 31 | 33 | 0.037461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_1102-21_0_4_line_34 | NAYY 4x150 SE | 32 | 34 | 0.023445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1102-21_0_4_line_35 | NAYY 4x150 SE | 33 | 39 | 0.026176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_1102-21_0_4_line_36 | NAYY 4x150 SE | 34 | 35 | 0.015123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1102-21_0_4_line_37 | NAYY 4x150 SE | 34 | 36 | 0.04676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1102-21_0_4_line_38 | NAYY 4x150 SE | 36 | 37 | 0.01411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1102-21_0_4_line_39 | NAYY 4x150 SE | 37 | 38 | 0.041779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1102-21_0_4_line_40 | NAYY 4x150 SE | 39 | 40 | 0.025174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_1102-21_0_4_line_41 | NAYY 4x150 SE | 40 | 41 | 0.1292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_1102-21_0_4_line_42 | NAYY 4x150 SE | 41 | 42 | 0.027663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1102-21_0_4_line_43 | NAYY 4x150 SE | 42 | 43 | 0.021531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1102-21_0_4_line_44 | NAYY 4x150 SE | 42 | 44 | 0.043642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1102-21_0_4_line_45 | NAYY 4x150 SE | 43 | 45 | 0.031218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1102-21_0_4_line_46 | NAYY 4x150 SE | 45 | 47 | 0.018186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1102-21_0_4_trafo_10 | 0.25 MVA 20/0.4 kV | 48 | 8 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2657519.9855 | 1220044.4351 | 2657530.6687 | 1220037.4043
1 | 2657515.7145 | 1220047.2458 | 2657519.9855 | 1220044.4351
2 | 2657530.6687 | 1220037.4043 | 2657546.9319 | 1220026.7013
3 | 2657532.8984 | 1220082.8337 | 2657532.0261 | 1220080.446 | 2657515.7145 | 1220047.2458
4 | 2657515.7145 | 1220047.2458 | 2657499.6381 | 1220057.3457
5 | 2657546.9319 | 1220026.7013 | 2657562.6941 | 1220016.328
6 | 2657532.8984 | 1220082.8337 | 2657518.2093 | 1220088.262 | 2657505.8823 | 1220090.3307
7 | 2657477.6151 | 1220071.1813 | 2657499.6381 | 1220057.3457
8 | 2657507.1247 | 1219963.2109 | 2657510.4102 | 1219962.431 | 2657516.574 | 1219959.8111 | 2657523.3458 | 1219956.1315
9 | 2657499.9048 | 1219960.4618 | 2657503.6262 | 1219962.4767 | 2657507.1247 | 1219963.2109 | 2657507.1247 | 1219963.2109
10 | 2657526.8947 | 1219954.2031 | 2657523.3458 | 1219956.1315
11 | 2657487.7974 | 1219948.3819 | 2657499.9048 | 1219960.4618 | 2657499.9048 | 1219960.4618
12 | 2657562.6941 | 1220016.328 | 2657580.7476 | 1220004.4468
13 | 2657497.6599 | 1220097.903 | 2657499.3537 | 1220091.4264 | 2657505.8823 | 1220090.3307
14 | 2657458.173 | 1220083.3956 | 2657477.6151 | 1220071.1813
15 | 2657526.8947 | 1219954.2031 | 2657545.7581 | 1219943.9533
16 | 2657497.6599 | 1220097.903 | 2657490.3715 | 1220104.6257 | 2657480.9258 | 1220108.3443
17 | 2657433.6988 | 1220098.746 | 2657439.6876 | 1220095.0088 | 2657458.173 | 1220083.3956
18 | 2657441.8965 | 1219993.2102 | 2657456.8798 | 1219978.5771
19 | 2657424.433 | 1220010.0446 | 2657436.7435 | 1219998.2428 | 2657441.8965 | 1219993.2102
20 | 2657487.7974 | 1219948.3819 | 2657456.8798 | 1219978.5771
21 | 2657378.531 | 1220054.0499 | 2657424.433 | 1220010.0446
22 | 2657545.7581 | 1219943.9533 | 2657552.8782 | 1219940.0845
23 | 2657559.6766 | 1219786.6979 | 2657570.7267 | 1219796.7108 | 2657574.7802 | 1219801.2639 | 2657575.88 | 1219803.0447
24 | 2657583.2228 | 1219829.8187 | 2657582.9746 | 1219819.3876 | 2657581.1904 | 1219811.6434 | 2657575.88 | 1219803.0447
25 | 2657559.6766 | 1219786.6979 | 2657538.7729 | 1219768.7098
26 | 2657529.2544 | 1219756.2298 | 2657562.2349 | 1219784.2211 | 2657559.6766 | 1219786.6979
27 | 2657583.2228 | 1219829.8187 | 2657573.6864 | 1219828.0699 | 2657570.3455 | 1219827.5151 | 2657563.6954 | 1219828.6071
28 | 2657583.2228 | 1219829.8187 | 2657581.4387 | 1219836.9837 | 2657579.5128 | 1219843.8916 | 2657572.9316 | 1219857.4919 | 2657562.5061 | 1219870.6442
29 | 2657529.2544 | 1219756.2298 | 2657543.127 | 1219739.5756
30 | 2657563.6954 | 1219828.6071 | 2657558.5201 | 1219830.9919 | 2657551.157 | 1219837.2062
31 | 2657562.5061 | 1219870.6442 | 2657561.3169 | 1219872.1444 | 2657532.7666 | 1219900.2093
32 | 2657551.157 | 1219837.2062 | 2657544.7488 | 1219842.6147
33 | 2657532.7666 | 1219900.2093 | 2657506.0516 | 1219926.4701
34 | 2657526.8322 | 1219857.7358 | 2657544.7488 | 1219842.6147
35 | 2657487.3841 | 1219944.8202 | 2657506.0516 | 1219926.4701
36 | 2657526.8322 | 1219857.7358 | 2657523.5489 | 1219853.5794 | 2657513.7261 | 1219853.3049
37 | 2657526.8322 | 1219857.7358 | 2657490.5715 | 1219887.3821
38 | 2657490.5715 | 1219887.3821 | 2657486.3097 | 1219884.7504 | 2657477.2133 | 1219885.0452
39 | 2657477.2133 | 1219885.0452 | 2657442.9315 | 1219908.9249
40 | 2657487.3841 | 1219944.8202 | 2657469.305 | 1219962.3381
41 | 2657378.531 | 1220054.0499 | 2657390.5083 | 1220038.6891 | 2657469.305 | 1219962.3381
42 | 2657378.531 | 1220054.0499 | 2657391.4635 | 1220067.9163 | 2657393.8028 | 1220070.0402 | 2657397.9405 | 1220073.7268
43 | 2657381.5828 | 1220087.7279 | 2657397.9405 | 1220073.7268 | 2657397.9405 | 1220073.7268
44 | 2657397.9405 | 1220073.7268 | 2657433.6988 | 1220098.746
45 | 2657364.3715 | 1220112.4386 | 2657369.1812 | 1220098.3429 | 2657381.5828 | 1220087.7279
46 | 2657364.3715 | 1220112.4386 | 2657368.0999 | 1220112.141 | 2657373.8109 | 1220113.1855 | 2657377.0523 | 1220114.6065 | 2657380.8899 | 1220117.9662

## bus_geodata
| x | y | coords
0 | 2657519.9855 | 1220044.4351
1 | 2657530.6687 | 1220037.4043
2 | 2657515.7145 | 1220047.2458
3 | 2657546.9319 | 1220026.7013
4 | 2657532.8984 | 1220082.8337
5 | 2657499.6381 | 1220057.3457
6 | 2657507.1247 | 1219963.2109
7 | 2657523.3458 | 1219956.1315
8 | 2657499.9048 | 1219960.4618
9 | 2657562.6941 | 1220016.328
10 | 2657505.8823 | 1220090.3307
11 | 2657477.6151 | 1220071.1813
12 | 2657580.7476 | 1220004.4468
13 | 2657526.8947 | 1219954.2031
14 | 2657497.6599 | 1220097.903
15 | 2657458.173 | 1220083.3956
16 | 2657441.8965 | 1219993.2102
17 | 2657456.8798 | 1219978.5771
18 | 2657424.433 | 1220010.0446
19 | 2657545.7581 | 1219943.9533
20 | 2657552.8782 | 1219940.0845
21 | 2657487.7974 | 1219948.3819
22 | 2657575.88 | 1219803.0447
23 | 2657559.6766 | 1219786.6979
24 | 2657583.2228 | 1219829.8187
25 | 2657538.7729 | 1219768.7098
26 | 2657529.2544 | 1219756.2298
27 | 2657563.6954 | 1219828.6071
28 | 2657562.5061 | 1219870.6442
29 | 2657543.127 | 1219739.5756
30 | 2657551.157 | 1219837.2062
31 | 2657532.7666 | 1219900.2093
32 | 2657544.7488 | 1219842.6147
33 | 2657506.0516 | 1219926.4701
34 | 2657526.8322 | 1219857.7358
35 | 2657513.7261 | 1219853.3049
36 | 2657490.5715 | 1219887.3821
37 | 2657477.2133 | 1219885.0452
38 | 2657442.9315 | 1219908.9249
39 | 2657487.3841 | 1219944.8202
40 | 2657469.305 | 1219962.3381
41 | 2657378.531 | 1220054.0499
42 | 2657397.9405 | 1220073.7268
43 | 2657381.5828 | 1220087.7279
44 | 2657433.6988 | 1220098.746
45 | 2657364.3715 | 1220112.4386
46 | 2657480.9258 | 1220108.3443
47 | 2657380.8899 | 1220117.9662
48 | 2657487.7974 | 1219948.3819

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97327 | -0.18773 | 0.003919 | 0.0009822
1 | 0.97302 | -0.18953 | 0.0033144 | 0.00083066
2 | 0.9734 | -0.1868 | 0 | 0
3 | 0.97273 | -0.19158 | 0.0032858 | 0.00082351
4 | 0.97256 | -0.19283 | 0 | 0
5 | 0.97428 | -0.18046 | 0.003934 | 0.00098596
6 | 0.99965 | -0.0024531 | 0.0079314 | 0.0019878
7 | 0.99905 | -0.0066362 | 0.0075094 | 0.001882
8 | 1 | 0 | -0.21979 | -0.055413
9 | 0.97254 | -0.19292 | 0.0033124 | 0.00083015
10 | 0.97196 | -0.19714 | 0.007627 | 0.0019115
11 | 0.97564 | -0.17071 | 0.0051809 | 0.0012984
12 | 0.97244 | -0.1937 | 0.0034134 | 0.00085547
13 | 0.99896 | -0.0072837 | 0.0062046 | 0.001555
14 | 0.97182 | -0.19811 | 0 | 0
15 | 0.97701 | -0.16089 | 0.0087797 | 0.0022004
16 | 0.99279 | -0.049716 | 0.0052211 | 0.0013085
17 | 0.99462 | -0.037032 | 0.0037744 | 0.00094596
18 | 0.99073 | -0.064036 | 0.0099549 | 0.0024949
19 | 0.99866 | -0.0093939 | 0.0034362 | 0.0008612
20 | 0.99859 | -0.0099119 | 0.0063871 | 0.0016008
21 | 0.99848 | -0.01046 | 0 | 0
22 | 0.97401 | -0.18242 | 0.0025791 | 0.00064638
23 | 0.97367 | -0.18488 | 0 | 0
24 | 0.97454 | -0.17862 | 0 | 0
25 | 0.97347 | -0.18634 | 0.005045 | 0.0012644
26 | 0.97332 | -0.18736 | 0 | 0
27 | 0.9742 | -0.18108 | 0.0030679 | 0.00076888
28 | 0.97563 | -0.17082 | 0.0098802 | 0.0024762
29 | 0.97316 | -0.18851 | 0.0050401 | 0.0012632
30 | 0.97396 | -0.18281 | 0.0029059 | 0.00072829
31 | 0.97681 | -0.16235 | 0.0091373 | 0.00229
32 | 0.97377 | -0.1841 | 0.002794 | 0.00070023
33 | 0.97804 | -0.1536 | 0.010689 | 0.0026789
34 | 0.97286 | -0.19066 | 0 | 0
35 | 0.97267 | -0.19204 | 0.0086879 | 0.0021774
36 | 0.97164 | -0.19947 | 0 | 0
37 | 0.97127 | -0.20213 | 0.0087582 | 0.002195
38 | 0.97071 | -0.20614 | 0.009076 | 0.0022747
39 | 0.97903 | -0.14653 | 0 | 0
40 | 0.97998 | -0.13975 | 0.012256 | 0.0030717
41 | 0.98564 | -0.099687 | 0 | 0
42 | 0.98263 | -0.12093 | 0.0032276 | 0.00080891
43 | 0.98213 | -0.1245 | 0.012195 | 0.0030564
44 | 0.97911 | -0.14593 | 0.0055773 | 0.0013978
45 | 0.98196 | -0.12575 | 0 | 0
46 | 0.97162 | -0.19956 | 0.0068523 | 0.0017173
47 | 0.98186 | -0.12648 | 0.0038615 | 0.00096778
48 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.013334 | 0.0033419 | -0.01333 | -0.0033408 | 3.3165e-06 | 1.1167e-06 | 0.020386 | 0.020386 | 0.020386 | 0.97327 | -0.18773 | 0.97302 | -0.18953 | 7.5503
1 | -0.017253 | -0.0043241 | 0.017255 | 0.0043249 | 2.2198e-06 | 7.9023e-07 | 0.026378 | 0.026378 | 0.026378 | 0.97327 | -0.18773 | 0.9734 | -0.1868 | 9.7695
2 | 0.010016 | 0.0025101 | -0.010013 | -0.0025092 | 2.8503e-06 | 8.5453e-07 | 0.015317 | 0.015317 | 0.015317 | 0.97302 | -0.18953 | 0.97273 | -0.19158 | 5.6731
3 | 0.014502 | 0.0036365 | -0.01449 | -0.0036323 | 1.212e-05 | 4.1707e-06 | 0.02217 | 0.02217 | 0.02217 | 0.9734 | -0.1868 | 0.97256 | -0.19283 | 8.2112
4 | -0.031757 | -0.0079613 | 0.031785 | 0.0079718 | 2.7922e-05 | 1.0503e-05 | 0.048548 | 0.048548 | 0.048548 | 0.9734 | -0.1868 | 0.97428 | -0.18046 | 17.9806
5 | 0.0067273 | 0.0016857 | -0.0067261 | -0.0016855 | 1.247e-06 | 2.4541e-07 | 0.010291 | 0.010291 | 0.010291 | 0.97273 | -0.19158 | 0.97254 | -0.19292 | 3.8115
6 | 0.01449 | 0.0036323 | -0.014482 | -0.0036293 | 8.6368e-06 | 2.9726e-06 | 0.02217 | 0.02217 | 0.02217 | 0.97256 | -0.19283 | 0.97196 | -0.19714 | 8.2113
7 | -0.035719 | -0.0089578 | 0.035768 | 0.008976 | 4.8304e-05 | 1.8254e-05 | 0.054556 | 0.054556 | 0.054556 | 0.97428 | -0.18046 | 0.97564 | -0.17071 | 20.2059
8 | 0.023556 | 0.0059054 | -0.023542 | -0.0059004 | 1.3642e-05 | 5.0139e-06 | 0.035064 | 0.035064 | 0.035064 | 0.99965 | -0.0024531 | 0.99905 | -0.0066362 | 12.9868
9 | -0.031487 | -0.0078932 | 0.031498 | 0.0078972 | 1.0701e-05 | 4.0135e-06 | 0.04687 | 0.04687 | 0.04687 | 0.99965 | -0.0024531 | 1 | 0 | 17.3594
10 | 0.016033 | 0.0040184 | -0.016031 | -0.0040179 | 1.4372e-06 | 4.9988e-07 | 0.02388 | 0.02388 | 0.02388 | 0.99905 | -0.0066362 | 0.99896 | -0.0072837 | 8.8443
11 | 0.18749 | 0.047516 | -0.18721 | -0.04741 | 0.00027726 | 0.00010597 | 0.27917 | 0.27917 | 0.27917 | 1 | 0 | 0.99848 | -0.01046 | 34.4658
12 | 0.0034137 | 0.00085534 | -0.0034134 | -0.00085547 | 3.679e-07 | -1.2665e-07 | 0.005223 | 0.0052231 | 0.0052231 | 0.97254 | -0.19292 | 0.97244 | -0.1937 | 1.9345
13 | 0.0068546 | 0.0017178 | -0.0068536 | -0.0017176 | 9.1492e-07 | 1.869e-07 | 0.010494 | 0.010494 | 0.010494 | 0.97196 | -0.19714 | 0.97182 | -0.19811 | 3.8867
14 | -0.040948 | -0.010274 | 0.041004 | 0.010296 | 5.589e-05 | 2.1209e-05 | 0.062458 | 0.062458 | 0.062458 | 0.97564 | -0.17071 | 0.97701 | -0.16089 | 23.1325
15 | 0.0098266 | 0.0024628 | -0.0098238 | -0.002462 | 2.8702e-06 | 8.2295e-07 | 0.014637 | 0.014638 | 0.014638 | 0.99896 | -0.0072837 | 0.99866 | -0.0093939 | 5.4213
16 | 0.0068536 | 0.0017176 | -0.0068523 | -0.0017173 | 1.3789e-06 | 2.8178e-07 | 0.010494 | 0.010494 | 0.010494 | 0.97182 | -0.19811 | 0.97162 | -0.19956 | 3.8867
17 | -0.049784 | -0.012496 | 0.049888 | 0.012536 | 0.00010366 | 3.9506e-05 | 0.075829 | 0.075829 | 0.075829 | 0.97701 | -0.16089 | 0.97911 | -0.14593 | 28.0849
18 | -0.18241 | -0.046072 | 0.18274 | 0.046196 | 0.00032592 | 0.00012454 | 0.27353 | 0.27353 | 0.27353 | 0.99279 | -0.049716 | 0.99462 | -0.037032 | 33.7688
19 | 0.17719 | 0.044763 | -0.17683 | -0.044627 | 0.00035619 | 0.00013606 | 0.2657 | 0.2657 | 0.2657 | 0.99279 | -0.049716 | 0.99073 | -0.064036 | 32.8027
20 | -0.18651 | -0.047142 | 0.18721 | 0.04741 | 0.00070058 | 0.00026777 | 0.27917 | 0.27917 | 0.27917 | 0.99462 | -0.037032 | 0.99848 | -0.01046 | 34.4659
21 | 0.16688 | 0.042132 | -0.16605 | -0.041815 | 0.00083162 | 0.00031741 | 0.25075 | 0.25075 | 0.25075 | 0.99073 | -0.064036 | 0.98564 | -0.099687 | 30.957
22 | 0.0063875 | 0.0016008 | -0.0063871 | -0.0016008 | 4.5803e-07 | 7.0148e-08 | 0.0095175 | 0.0095175 | 0.0095175 | 0.99866 | -0.0093939 | 0.99859 | -0.0099119 | 3.525
23 | 0.010092 | 0.0025288 | -0.010089 | -0.0025278 | 3.4266e-06 | 1.0305e-06 | 0.015418 | 0.015418 | 0.015418 | 0.97401 | -0.18242 | 0.97367 | -0.18488 | 5.7103
24 | -0.012671 | -0.0031752 | 0.012678 | 0.0031774 | 6.6612e-06 | 2.2072e-06 | 0.019358 | 0.019358 | 0.019358 | 0.97401 | -0.18242 | 0.97454 | -0.17862 | 7.1696
25 | 0.0050461 | 0.0012645 | -0.005045 | -0.0012644 | 1.0234e-06 | 5.0683e-08 | 0.0077116 | 0.0077117 | 0.0077117 | 0.97367 | -0.18488 | 0.97347 | -0.18634 | 2.8562
26 | 0.0050427 | 0.0012633 | -0.0050409 | -0.0012632 | 1.735e-06 | 8.5219e-08 | 0.0077063 | 0.0077065 | 0.0077065 | 0.97367 | -0.18488 | 0.97332 | -0.18736 | 2.8543
27 | 0.035374 | 0.0088736 | -0.035362 | -0.0088697 | 1.2029e-05 | 3.8859e-06 | 0.054015 | 0.054016 | 0.054016 | 0.97454 | -0.17862 | 0.9742 | -0.18108 | 6.6686
28 | -0.048052 | -0.012051 | 0.048104 | 0.012069 | 5.2011e-05 | 1.8266e-05 | 0.073373 | 0.073373 | 0.073373 | 0.97454 | -0.17862 | 0.97563 | -0.17082 | 9.0584
29 | 0.0050409 | 0.0012632 | -0.0050401 | -0.0012632 | 8.0242e-07 | 3.9563e-08 | 0.0077065 | 0.0077066 | 0.0077066 | 0.97332 | -0.18736 | 0.97316 | -0.18851 | 2.8543
30 | 0.032294 | 0.0081008 | -0.032286 | -0.0080984 | 7.761e-06 | 2.4124e-06 | 0.04933 | 0.04933 | 0.04933 | 0.9742 | -0.18108 | 0.97396 | -0.18281 | 6.0901
31 | -0.057984 | -0.014545 | 0.058052 | 0.01457 | 6.8249e-05 | 2.4676e-05 | 0.088442 | 0.088441 | 0.088442 | 0.97563 | -0.17082 | 0.97681 | -0.16235 | 10.9187
32 | 0.029381 | 0.0073701 | -0.029375 | -0.0073683 | 5.2722e-06 | 1.8191e-06 | 0.04489 | 0.04489 | 0.04489 | 0.97396 | -0.18281 | 0.97377 | -0.1841 | 8.313
33 | -0.06719 | -0.01686 | 0.067271 | 0.01689 | 8.164e-05 | 2.9992e-05 | 0.10236 | 0.10236 | 0.10236 | 0.97681 | -0.16235 | 0.97804 | -0.1536 | 12.6371
34 | 0.026581 | 0.0066681 | -0.026557 | -0.0066591 | 2.414e-05 | 8.993e-06 | 0.040621 | 0.040621 | 0.040621 | 0.97377 | -0.1841 | 0.97286 | -0.19066 | 15.0448
35 | -0.07796 | -0.019569 | 0.078037 | 0.019598 | 7.6614e-05 | 2.848e-05 | 0.11862 | 0.11862 | 0.11862 | 0.97804 | -0.1536 | 0.97903 | -0.14653 | 14.6448
36 | 0.0086896 | 0.0021779 | -0.0086879 | -0.0021774 | 1.6671e-06 | 4.5343e-07 | 0.013291 | 0.013291 | 0.013291 | 0.97286 | -0.19066 | 0.97267 | -0.19204 | 4.9226
37 | 0.017868 | 0.0044812 | -0.017846 | -0.0044734 | 2.1794e-05 | 7.8025e-06 | 0.02733 | 0.02733 | 0.02733 | 0.97286 | -0.19066 | 0.97164 | -0.19947 | 10.1223
38 | 0.017846 | 0.0044734 | -0.017839 | -0.0044711 | 6.5766e-06 | 2.3548e-06 | 0.02733 | 0.02733 | 0.02733 | 0.97164 | -0.19947 | 0.97127 | -0.20213 | 10.1223
39 | 0.009081 | 0.0022761 | -0.009076 | -0.0022747 | 5.0461e-06 | 1.424e-06 | 0.013913 | 0.013913 | 0.013913 | 0.97127 | -0.20213 | 0.97071 | -0.20614 | 5.1528
40 | -0.078037 | -0.019598 | 0.078111 | 0.019625 | 7.368e-05 | 2.7388e-05 | 0.11862 | 0.11862 | 0.11862 | 0.97903 | -0.14653 | 0.97998 | -0.13975 | 14.6447
41 | -0.090367 | -0.022697 | 0.090873 | 0.022886 | 0.00050609 | 0.00018974 | 0.13723 | 0.13723 | 0.13723 | 0.97998 | -0.13975 | 0.98564 | -0.099687 | 16.9422
42 | 0.075174 | 0.018928 | -0.074952 | -0.018843 | 0.00022245 | 8.5206e-05 | 0.11352 | 0.11352 | 0.11352 | 0.98564 | -0.099687 | 0.98263 | -0.12093 | 42.045
43 | 0.016066 | 0.0040268 | -0.016058 | -0.004024 | 7.9524e-06 | 2.786e-06 | 0.024329 | 0.024329 | 0.024329 | 0.98263 | -0.12093 | 0.98213 | -0.1245 | 9.0107
44 | 0.055658 | 0.014007 | -0.055465 | -0.013933 | 0.00019355 | 7.3892e-05 | 0.084305 | 0.084305 | 0.084305 | 0.98263 | -0.12093 | 0.97911 | -0.14593 | 31.2242
45 | 0.0038626 | 0.00096756 | -0.0038619 | -0.0009677 | 6.6711e-07 | -1.384e-07 | 0.0058519 | 0.0058521 | 0.0058521 | 0.98213 | -0.1245 | 0.98196 | -0.12575 | 2.1674
46 | 0.0038619 | 0.0009677 | -0.0038615 | -0.00096778 | 3.8863e-07 | -8.0554e-08 | 0.0058521 | 0.0058522 | 0.0058522 | 0.98196 | -0.12575 | 0.98186 | -0.12648 | 2.1675

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22683 | 0.057179

## res_load
| p_mw | q_mvar
0 | 0.003919 | 0.0009822
1 | 0.0033144 | 0.00083066
2 | 0.0032858 | 0.00082351
3 | 0.003934 | 0.00098596
4 | 0.0079314 | 0.0019878
5 | 0.0075094 | 0.001882
6 | 0.0070468 | 0.0017661
7 | 0.0033124 | 0.00083015
8 | 0.007627 | 0.0019115
9 | 0.0051809 | 0.0012984
10 | 0.0034134 | 0.00085547
11 | 0.0062046 | 0.001555
12 | 0.0087797 | 0.0022004
13 | 0.0052211 | 0.0013085
14 | 0.0037744 | 0.00094596
15 | 0.0099549 | 0.0024949
16 | 0.0034362 | 0.0008612
17 | 0.0063871 | 0.0016008
18 | 0.0025791 | 0.00064638
19 | 0.005045 | 0.0012644
20 | 0.0030679 | 0.00076888
21 | 0.0098802 | 0.0024762
22 | 0.0050401 | 0.0012632
23 | 0.0029059 | 0.00072829
24 | 0.0091373 | 0.00229
25 | 0.002794 | 0.00070023
26 | 0.010689 | 0.0026789
27 | 0.0086879 | 0.0021774
28 | 0.0087582 | 0.002195
29 | 0.009076 | 0.0022747
30 | 0.012256 | 0.0030717
31 | 0.0032276 | 0.00080891
32 | 0.012195 | 0.0030564
33 | 0.0055773 | 0.0013978
34 | 0.0068523 | 0.0017173
35 | 0.0038615 | 0.00096778

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1