## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1102-25_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1102-25_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1102-25_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1102-25_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1102-25_0_4_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_1102-25_0_4_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_1102-25_0_4_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_1102-25_0_4_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_1102-25_0_4_node_87 | 0.4 | n |  | TRUE
9 | bus_LV_1102-25_0_4_node_86 | 0.4 | n |  | TRUE
10 | bus_LV_1102-25_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1102-25_0_4_node_90 | 0.4 | n |  | TRUE
12 | bus_LV_1102-25_0_4_node_89 | 0.4 | n |  | TRUE
13 | bus_LV_1102-25_0_4_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1102-25_0_4_node_28 | 0.4 | n |  | TRUE
15 | bus_LV_1102-25_0_4_node_37 | 0.4 | n |  | TRUE
16 | bus_LV_1102-25_0_4_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_1102-25_0_4_node_62 | 0.4 | n |  | TRUE
18 | bus_LV_1102-25_0_4_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_1102-25_0_4_node_74 | 0.4 | n |  | TRUE
20 | bus_LV_1102-25_0_4_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1102-25_0_4_node_88 | 0.4 | n |  | TRUE
22 | bus_LV_1102-25_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1102-25_0_4_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_1102-25_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1102-25_0_4_node_32 | 0.4 | n |  | TRUE
26 | bus_LV_1102-25_0_4_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_1102-25_0_4_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_1102-25_0_4_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_1102-25_0_4_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_1102-25_0_4_node_38 | 0.4 | n |  | TRUE
31 | bus_LV_1102-25_0_4_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_1102-25_0_4_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_1102-25_0_4_node_34 | 0.4 | n |  | TRUE
34 | bus_LV_1102-25_0_4_node_73 | 0.4 | n |  | TRUE
35 | bus_LV_1102-25_0_4_node_80 | 0.4 | n |  | TRUE
36 | bus_LV_1102-25_0_4_node_78 | 0.4 | n |  | TRUE
37 | bus_LV_1102-25_0_4_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_1102-25_0_4_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_1102-25_0_4_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_1102-25_0_4_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_1102-25_0_4_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_1102-25_0_4_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_1102-25_0_4_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_1102-25_0_4_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_1102-25_0_4_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_1102-25_0_4_node_43 | 0.4 | n |  | TRUE
47 | bus_LV_1102-25_0_4_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_1102-25_0_4_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_1102-25_0_4_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_1102-25_0_4_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_1102-25_0_4_node_64 | 0.4 | n |  | TRUE
52 | bus_LV_1102-25_0_4_node_48 | 0.4 | n |  | TRUE
53 | bus_LV_1102-25_0_4_node_65 | 0.4 | n |  | TRUE
54 | bus_LV_1102-25_0_4_node_49 | 0.4 | n |  | TRUE
55 | bus_LV_1102-25_0_4_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_1102-25_0_4_node_54 | 0.4 | n |  | TRUE
57 | bus_LV_1102-25_0_4_node_51 | 0.4 | n |  | TRUE
58 | bus_LV_1102-25_0_4_node_57 | 0.4 | n |  | TRUE
59 | bus_LV_1102-25_0_4_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_1102-25_0_4_node_52 | 0.4 | n |  | TRUE
61 | bus_LV_1102-25_0_4_node_53 | 0.4 | n |  | TRUE
62 | bus_LV_1102-25_0_4_node_75 | 0.4 | n |  | TRUE
63 | bus_LV_1102-25_0_4_node_56 | 0.4 | n |  | TRUE
64 | bus_LV_1102-25_0_4_node_58 | 0.4 | n |  | TRUE
65 | bus_LV_1102-25_0_4_node_59 | 0.4 | n |  | TRUE
66 | bus_LV_1102-25_0_4_node_60 | 0.4 | n |  | TRUE
67 | bus_LV_1102-25_0_4_node_82 | 0.4 | n |  | TRUE
68 | bus_LV_1102-25_0_4_node_76 | 0.4 | n |  | TRUE
69 | bus_LV_1102-25_0_4_node_61 | 0.4 | n |  | TRUE
70 | bus_LV_1102-25_0_4_node_84 | 0.4 | n |  | TRUE
71 | bus_LV_1102-25_0_4_node_81 | 0.4 | n |  | TRUE
72 | bus_LV_1102-25_0_4_node_63 | 0.4 | n |  | TRUE
73 | bus_LV_1102-25_0_4_node_66 | 0.4 | n |  | TRUE
74 | bus_LV_1102-25_0_4_node_67 | 0.4 | n |  | TRUE
75 | bus_LV_1102-25_0_4_node_68 | 0.4 | n |  | TRUE
76 | bus_LV_1102-25_0_4_node_69 | 0.4 | n |  | TRUE
77 | bus_LV_1102-25_0_4_node_70 | 0.4 | n |  | TRUE
78 | bus_LV_1102-25_0_4_node_71 | 0.4 | n |  | TRUE
79 | bus_LV_1102-25_0_4_node_72 | 0.4 | n |  | TRUE
80 | bus_LV_1102-25_0_4_node_77 | 0.4 | n |  | TRUE
81 | bus_LV_1102-25_0_4_node_79 | 0.4 | n |  | TRUE
82 | bus_LV_1102-25_0_4_node_83 | 0.4 | n |  | TRUE
83 | bus_LV_1102-25_0_4_node_85 | 0.4 | n |  | TRUE
84 | bus_MV_354_0_node_95 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1102-25_0_4_load_0 | 0 | 0.0013341 | 0.00033435 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1102-25_0_4_load_10 | 4 | 0.0057734 | 0.001447 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1102-25_0_4_load_22 | 6 | 0.0029488 | 0.00073903 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1102-25_0_4_load_87 | 8 | 0.0031364 | 0.00078607 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1102-25_0_4_load_86 | 9 | 0.010779 | 0.0027015 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1102-25_0_4_load_90 | 11 | 0.0040051 | 0.0010038 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1102-25_0_4_load_89 | 12 | 0.001773 | 0.00044434 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1102-25_0_4_load_14 | 13 | 0.0084881 | 0.0021273 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1102-25_0_4_load_37 | 15 | 0.0037629 | 0.00094308 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1102-25_0_4_load_23 | 16 | 0.0015606 | 0.00039113 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1102-25_0_4_load_74 | 19 | 0.0017649 | 0.00044232 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1102-25_0_4_load_88 | 21 | 0.0027546 | 0.00069037 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1102-25_0_4_load_13 | 22 | 0.00039536 | 9.9086e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1102-25_0_4_load_11 | 23 | 0.0069774 | 0.0017487 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1102-25_0_4_load_24 | 24 | 0.0011001 | 0.00027571 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1102-25_0_4_load_32 | 25 | 0.0011244 | 0.0002818 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1102-25_0_4_load_31 | 26 | 0.0014952 | 0.00037473 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1102-25_0_4_load_12 | 27 | 0.0014852 | 0.00037224 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1102-25_0_4_load_15 | 28 | 0.001993 | 0.0004995 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1102-25_0_4_load_16 | 29 | 0.0016991 | 0.00042584 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1102-25_0_4_load_38 | 30 | 0.0063655 | 0.0015953 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1102-25_0_4_load_33 | 32 | 0.0057442 | 0.0014396 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1102-25_0_4_load_34 | 33 | 0.0044126 | 0.0011059 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1102-25_0_4_load_73 | 34 | 0.0020006 | 0.0005014 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1102-25_0_4_load_80 | 35 | 0.0030283 | 0.00075896 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1102-25_0_4_load_26 | 38 | 0.0033021 | 0.00082758 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1102-25_0_4_load_36 | 39 | 0.0039929 | 0.0010007 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1102-25_0_4_load_27 | 40 | 0.0041168 | 0.0010318 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1102-25_0_4_load_29 | 41 | 0.0012644 | 0.00031689 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1102-25_0_4_load_39 | 42 | 0.0025305 | 0.0006342 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1102-25_0_4_load_40 | 43 | 0.0026096 | 0.00065403 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1102-25_0_4_load_41 | 44 | 0.0049949 | 0.0012518 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1102-25_0_4_load_42 | 45 | 0.0038193 | 0.00095721 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1102-25_0_4_load_43 | 46 | 0.0016169 | 0.00040523 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1102-25_0_4_load_45 | 48 | 0.0063242 | 0.001585 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1102-25_0_4_load_46 | 49 | 0.0022292 | 0.0005587 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1102-25_0_4_load_47 | 50 | 0.0035837 | 0.00089815 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1102-25_0_4_load_64 | 51 | 0.0029157 | 0.00073074 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1102-25_0_4_load_48 | 52 | 0.0065473 | 0.0016409 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1102-25_0_4_load_65 | 53 | 0.0024115 | 0.00060439 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1102-25_0_4_load_49 | 54 | 0.0041772 | 0.0010469 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1102-25_0_4_load_51 | 57 | 0.0032532 | 0.00081532 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1102-25_0_4_load_57 | 58 | 0.0015452 | 0.00038726 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1102-25_0_4_load_55 | 59 | 0.0039772 | 0.00099678 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1102-25_0_4_load_52 | 60 | 0.0041435 | 0.0010385 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1102-25_0_4_load_53 | 61 | 0.0033647 | 0.00084328 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1102-25_0_4_load_75 | 62 | 0.0034528 | 0.00086535 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1102-25_0_4_load_59 | 65 | 0.0057168 | 0.0014328 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1102-25_0_4_load_60 | 66 | 0.014615 | 0.0036628 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1102-25_0_4_load_76 | 68 | 0.0037884 | 0.00094946 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1102-25_0_4_load_61 | 69 | 0.0088024 | 0.0022061 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1102-25_0_4_load_84 | 70 | 0.0040464 | 0.0010141 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1102-25_0_4_load_81 | 71 | 0.0032645 | 0.00081817 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1102-25_0_4_load_63 | 72 | 0.010293 | 0.0025796 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1102-25_0_4_load_66 | 73 | 0.0024153 | 0.00060533 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1102-25_0_4_load_67 | 74 | 0.0025227 | 0.00063224 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1102-25_0_4_load_68 | 75 | 0.0025563 | 0.00064066 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1102-25_0_4_load_69 | 76 | 0.0030668 | 0.00076861 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1102-25_0_4_load_70 | 77 | 0.0013178 | 0.00033026 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1102-25_0_4_load_71 | 78 | 0.0013449 | 0.00033706 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1102-25_0_4_load_72 | 79 | 0.0024182 | 0.00060605 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1102-25_0_4_load_77 | 80 | 0.0023052 | 0.00057774 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1102-25_0_4_load_79 | 81 | 0.0047076 | 0.0011798 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1102-25_0_4_load_83 | 82 | 0.0035023 | 0.00087776 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1102-25_0_4_load_85 | 83 | 0.002864 | 0.0007178 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 54 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1102-25_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.06106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1102-25_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.12213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1102-25_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.03559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1102-25_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.024187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1102-25_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.019594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1102-25_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.014613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1102-25_0_4_line_6 | NAYY 4x150 SE | 4 | 13 | 0.0028805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1102-25_0_4_line_7 | NAYY 4x150 SE | 5 | 14 | 0.024983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1102-25_0_4_line_8 | NAYY 4x150 SE | 5 | 15 | 0.023345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1102-25_0_4_line_9 | NAYY 4x150 SE | 6 | 16 | 0.023855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1102-25_0_4_line_10 | NAYY 4x150 SE | 7 | 8 | 0.024275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1102-25_0_4_line_11 | NAYY 4x150 SE | 7 | 9 | 0.019756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1102-25_0_4_line_12 | NAYY 4x150 SE | 8 | 11 | 0.035817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1102-25_0_4_line_13 | NAYY 4x150 SE | 9 | 17 | 0.0038385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1102-25_0_4_line_14 | NAYY 4x150 SE | 10 | 11 | 0.022574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1102-25_0_4_line_15 | NAYY 4x150 SE | 10 | 12 | 0.027963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1102-25_0_4_line_16 | NAYY 4x150 SE | 12 | 21 | 0.031627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1102-25_0_4_line_17 | NAYY 4x150 SE | 13 | 27 | 0.017512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1102-25_0_4_line_18 | NAYY 4x150 SE | 14 | 37 | 0.05392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1102-25_0_4_line_19 | NAYY 4x150 SE | 14 | 38 | 0.01901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1102-25_0_4_line_20 | NAYY 4x150 SE | 15 | 39 | 0.014069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1102-25_0_4_line_21 | NAYY 4x150 SE | 16 | 24 | 0.021976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1102-25_0_4_line_22 | NAYY 4x150 SE | 17 | 69 | 0.034055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1102-25_0_4_line_23 | NAYY 4x150 SE | 18 | 19 | 0.021463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1102-25_0_4_line_24 | NAYY 4x150 SE | 18 | 20 | 0.084001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1102-25_0_4_line_25 | NAYY 4x150 SE | 19 | 34 | 0.0075937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1102-25_0_4_line_26 | NAYY 4x150 SE | 20 | 28 | 0.010779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1102-25_0_4_line_27 | NAYY 4x150 SE | 22 | 23 | 0.026143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1102-25_0_4_line_28 | NAYY 4x150 SE | 23 | 27 | 0.0088435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1102-25_0_4_line_29 | NAYY 4x150 SE | 25 | 26 | 0.0088849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1102-25_0_4_line_30 | NAYY 4x150 SE | 26 | 41 | 0.014254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1102-25_0_4_line_31 | NAYY 4x150 SE | 28 | 29 | 0.0080051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1102-25_0_4_line_32 | NAYY 4x150 SE | 30 | 31 | 0.024229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1102-25_0_4_line_33 | NAYY 4x150 SE | 31 | 42 | 0.020507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1102-25_0_4_line_34 | NAYY 4x150 SE | 31 | 43 | 0.020767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1102-25_0_4_line_35 | NAYY 4x150 SE | 31 | 37 | 0.010427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1102-25_0_4_line_36 | NAYY 4x150 SE | 32 | 33 | 0.0042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1102-25_0_4_line_37 | NAYY 4x150 SE | 33 | 37 | 0.027368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1102-25_0_4_line_38 | NAYY 4x150 SE | 34 | 79 | 0.013149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1102-25_0_4_line_39 | NAYY 4x150 SE | 35 | 36 | 0.0073129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1102-25_0_4_line_40 | NAYY 4x150 SE | 36 | 81 | 0.046472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1102-25_0_4_line_41 | NAYY 4x150 SE | 36 | 80 | 0.014555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1102-25_0_4_line_42 | NAYY 4x150 SE | 38 | 40 | 5.652e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1102-25_0_4_line_43 | NAYY 4x150 SE | 40 | 41 | 0.009338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1102-25_0_4_line_44 | NAYY 4x150 SE | 42 | 44 | 0.017886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1102-25_0_4_line_45 | NAYY 4x150 SE | 43 | 45 | 0.0057875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1102-25_0_4_line_46 | NAYY 4x150 SE | 45 | 46 | 0.0060758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1102-25_0_4_line_47 | NAYY 4x150 SE | 46 | 47 | 0.044976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1102-25_0_4_line_48 | NAYY 4x150 SE | 47 | 48 | 0.0038761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_1102-25_0_4_line_49 | NAYY 4x150 SE | 47 | 49 | 0.017783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1102-25_0_4_line_50 | NAYY 4x150 SE | 48 | 50 | 0.016887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
51 | LV_1102-25_0_4_line_51 | NAYY 4x150 SE | 49 | 51 | 0.00033616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1102-25_0_4_line_52 | NAYY 4x150 SE | 50 | 52 | 0.016176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_1102-25_0_4_line_53 | NAYY 4x150 SE | 51 | 53 | 0.0065905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1102-25_0_4_line_54 | NAYY 4x150 SE | 52 | 54 | 0.013556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_1102-25_0_4_line_55 | NAYY 4x150 SE | 53 | 73 | 0.016008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1102-25_0_4_line_56 | NAYY 4x150 SE | 54 | 55 | 0.0041294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
57 | LV_1102-25_0_4_line_57 | NAYY 4x150 SE | 55 | 56 | 0.017518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1102-25_0_4_line_58 | NAYY 4x150 SE | 55 | 57 | 0.026795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1102-25_0_4_line_59 | NAYY 4x150 SE | 56 | 58 | 0.011727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1102-25_0_4_line_60 | NAYY 4x150 SE | 56 | 59 | 0.0032651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1102-25_0_4_line_61 | NAYY 4x150 SE | 57 | 60 | 0.0028549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1102-25_0_4_line_62 | NAYY 4x150 SE | 58 | 62 | 0.032245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1102-25_0_4_line_63 | NAYY 4x150 SE | 59 | 63 | 0.027021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1102-25_0_4_line_64 | NAYY 4x150 SE | 60 | 61 | 0.0058654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1102-25_0_4_line_65 | NAYY 4x150 SE | 62 | 68 | 0.020171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1102-25_0_4_line_66 | NAYY 4x150 SE | 63 | 64 | 0.002909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1102-25_0_4_line_67 | NAYY 4x150 SE | 63 | 65 | 0.012888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1102-25_0_4_line_68 | NAYY 4x150 SE | 64 | 66 | 0.00037635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1102-25_0_4_line_69 | NAYY 4x150 SE | 65 | 67 | 0.024496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1102-25_0_4_line_70 | NAYY 4x150 SE | 66 | 69 | 0.020871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1102-25_0_4_line_71 | NAYY 4x150 SE | 67 | 70 | 0.029941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1102-25_0_4_line_72 | NAYY 4x150 SE | 67 | 71 | 0.0074104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1102-25_0_4_line_73 | NAYY 4x150 SE | 68 | 80 | 0.0091547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1102-25_0_4_line_74 | NAYY 4x150 SE | 69 | 72 | 0.018175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1102-25_0_4_line_75 | NAYY 4x150 SE | 70 | 83 | 0.0045662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1102-25_0_4_line_76 | NAYY 4x150 SE | 71 | 82 | 0.001302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1102-25_0_4_line_77 | NAYY 4x150 SE | 73 | 74 | 0.0040427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1102-25_0_4_line_78 | NAYY 4x150 SE | 74 | 75 | 0.0033411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1102-25_0_4_line_79 | NAYY 4x150 SE | 75 | 76 | 0.004583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1102-25_0_4_line_80 | NAYY 4x150 SE | 76 | 77 | 0.011263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1102-25_0_4_line_81 | NAYY 4x150 SE | 77 | 78 | 0.0068388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1102-25_0_4_line_82 | NAYY 4x150 SE | 78 | 79 | 0.0037313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1102-25_0_4_trafo_49 | 0.25 MVA 20/0.4 kV | 84 | 54 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2657490.8853 | 1220699.844 | 2657519.854 | 1220682.3682 | 2657535.4123 | 1220673.991 | 2657544.0479 | 1220669.8951
1 | 2657661.7315 | 1220693.9243 | 2657649.464 | 1220691.5153 | 2657620.9308 | 1220683.5455 | 2657592.5759 | 1220673.6096 | 2657577.5068 | 1220669.0501 | 2657568.6187 | 1220667.0963 | 2657560.2874 | 1220666.3932 | 2657553.4538 | 1220666.9498 | 2657546.8756 | 1220668.5539 | 2657544.0479 | 1220669.8951
2 | 2657476.6759 | 1220719.4079 | 2657487.6367 | 1220718.8578 | 2657493.6749 | 1220718.1711 | 2657490.8853 | 1220699.844
3 | 2657661.7315 | 1220693.9243 | 2657673.212 | 1220672.6359
4 | 2657457.15 | 1220721.4876 | 2657470.7325 | 1220719.7063 | 2657476.6759 | 1220719.4079
5 | 2657476.6759 | 1220719.4079 | 2657475.2662 | 1220704.8632
6 | 2657673.212 | 1220672.6359 | 2657674.5792 | 1220670.1006
7 | 2657457.15 | 1220721.4876 | 2657443.6198 | 1220724.9259 | 2657433.2486 | 1220728.8506
8 | 2657457.15 | 1220721.4876 | 2657459.8373 | 1220738.6241 | 2657462.942 | 1220743.7573
9 | 2657475.2662 | 1220704.8632 | 2657473.9298 | 1220691.075 | 2657473.0738 | 1220681.1095
10 | 2657588.1992 | 1220904.1771 | 2657580.2731 | 1220918.0981 | 2657574.0119 | 1220923.4798
11 | 2657588.1992 | 1220904.1771 | 2657583.9746 | 1220900.912 | 2657575.9602 | 1220888.9286
12 | 2657574.0119 | 1220923.4798 | 2657546.8497 | 1220946.8273
13 | 2657573.8263 | 1220885.7379 | 2657575.9602 | 1220888.9286
14 | 2657528.7323 | 1220960.2264 | 2657540.0332 | 1220952.6864 | 2657546.8497 | 1220946.8273
15 | 2657528.7323 | 1220960.2264 | 2657513.6119 | 1220938.2668 | 2657514.5855 | 1220937.4042
16 | 2657514.5855 | 1220937.4042 | 2657520.2156 | 1220932.4158 | 2657519.5019 | 1220929.3292 | 2657536.8111 | 1220917.551
17 | 2657674.5792 | 1220670.1006 | 2657670.6703 | 1220653.0299 | 2657670.6703 | 1220653.0299
18 | 2657433.2486 | 1220728.8506 | 2657419.6932 | 1220737.2697 | 2657411.3112 | 1220741.0468 | 2657386.6091 | 1220744.9113 | 2657382.9112 | 1220743.6638
19 | 2657433.2486 | 1220728.8506 | 2657430.5039 | 1220722.3757 | 2657429.114 | 1220710.479
20 | 2657472.3005 | 1220754.1596 | 2657464.6465 | 1220746.5754 | 2657462.942 | 1220743.7573
21 | 2657470.7935 | 1220659.2611 | 2657471.7335 | 1220665.5046 | 2657473.0738 | 1220681.1095
22 | 2657547.2333 | 1220864.7124 | 2657571.62 | 1220882.4479 | 2657573.8263 | 1220885.7379
23 | 2657349.5468 | 1220857.6355 | 2657357.4714 | 1220853.2646 | 2657367.946 | 1220846.6043
24 | 2657324.5272 | 1220802.3271 | 2657310.5364 | 1220812.6545 | 2657305.5316 | 1220816.342 | 2657313.1669 | 1220823.909 | 2657333.9033 | 1220841.8418 | 2657349.5468 | 1220857.6355
25 | 2657374.3539 | 1220842.5297 | 2657367.946 | 1220846.6043
26 | 2657324.5272 | 1220802.3271 | 2657330.8194 | 1220811.0787
27 | 2657664.6933 | 1220646.5121 | 2657648.5226 | 1220628.8784 | 2657648.0119 | 1220626.7209
28 | 2657664.6933 | 1220646.5121 | 2657670.6703 | 1220653.0299
29 | 2657425.3388 | 1220678.1654 | 2657426.3698 | 1220686.9903
30 | 2657428.0238 | 1220701.1479 | 2657426.3698 | 1220686.9903
31 | 2657330.8194 | 1220811.0787 | 2657335.4924 | 1220817.5783
32 | 2657377.2806 | 1220752.4483 | 2657365.0382 | 1220749.0061 | 2657353.5994 | 1220747.7087
33 | 2657377.2806 | 1220752.4483 | 2657374.6879 | 1220761.6847 | 2657369.3585 | 1220771.209
34 | 2657377.2806 | 1220752.4483 | 2657396.1629 | 1220761.0926
35 | 2657377.2806 | 1220752.4483 | 2657382.9112 | 1220743.6638
36 | 2657376.6657 | 1220713.1467 | 2657377.1702 | 1220717.3162
37 | 2657382.9112 | 1220743.6638 | 2657379.6871 | 1220738.1182 | 2657377.1702 | 1220717.3162
38 | 2657374.3539 | 1220842.5297 | 2657385.4493 | 1220835.4745
39 | 2657431.0153 | 1220882.5467 | 2657424.8895 | 1220886.5408
40 | 2657431.0153 | 1220882.5467 | 2657460.6689 | 1220908.7711 | 2657466.6288 | 1220905.1708
41 | 2657431.0153 | 1220882.5467 | 2657443.2077 | 1220874.5968
42 | 2657429.114 | 1220710.479 | 2657429.1074 | 1220710.4228
43 | 2657428.0238 | 1220701.1479 | 2657429.1074 | 1220710.4228
44 | 2657356.9007 | 1220783.4011 | 2657365.9878 | 1220777.2328 | 2657369.3585 | 1220771.209
45 | 2657401.3842 | 1220763.5823 | 2657400.4018 | 1220763.0331 | 2657396.1629 | 1220761.0926
46 | 2657401.3842 | 1220763.5823 | 2657406.6876 | 1220766.5471
47 | 2657443.9798 | 1220791.4262 | 2657426.8511 | 1220777.8194 | 2657406.6876 | 1220766.5471
48 | 2657443.9798 | 1220791.4262 | 2657447.16 | 1220793.6422
49 | 2657443.9798 | 1220791.4262 | 2657440.8067 | 1220798.689 | 2657436.2188 | 1220803.192 | 2657433.3251 | 1220805.0321
50 | 2657447.16 | 1220793.6422 | 2657461.0153 | 1220803.2969
51 | 2657433.0414 | 1220805.2125 | 2657433.3251 | 1220805.0321
52 | 2657474.2867 | 1220812.5446 | 2657461.0153 | 1220803.2969
53 | 2657427.48 | 1220808.7488 | 2657433.0414 | 1220805.2125
54 | 2657474.2867 | 1220812.5446 | 2657485.4089 | 1220820.2948
55 | 2657427.48 | 1220808.7488 | 2657413.9715 | 1220817.3383
56 | 2657488.7969 | 1220822.6556 | 2657485.4089 | 1220820.2948
57 | 2657503.1983 | 1220832.6897 | 2657488.7969 | 1220822.6556
58 | 2657488.7969 | 1220822.6556 | 2657498.1451 | 1220807.592 | 2657501.8619 | 1220803.7366 | 2657504.7272 | 1220801.3777
59 | 2657503.1983 | 1220832.6897 | 2657494.3169 | 1220840.3481
60 | 2657503.1983 | 1220832.6897 | 2657505.8388 | 1220834.6102
61 | 2657504.7272 | 1220801.3777 | 2657506.9313 | 1220799.5633
62 | 2657494.3169 | 1220840.3481 | 2657489.9248 | 1220844.1354 | 2657467.7724 | 1220858.5796
63 | 2657527.6907 | 1220850.5038 | 2657505.8388 | 1220834.6102
64 | 2657511.4596 | 1220795.8354 | 2657506.9313 | 1220799.5633
65 | 2657467.7724 | 1220858.5796 | 2657450.8762 | 1220869.5966
66 | 2657530.0488 | 1220852.2165 | 2657527.6907 | 1220850.5038
67 | 2657527.6907 | 1220850.5038 | 2657523.3468 | 1220856.4433 | 2657519.2463 | 1220860.1534
68 | 2657530.3532 | 1220852.4378 | 2657530.0488 | 1220852.2165
69 | 2657503.6996 | 1220878.9899 | 2657515.2493 | 1220863.7697 | 2657519.2463 | 1220860.1534
70 | 2657547.2333 | 1220864.7124 | 2657530.3532 | 1220852.4378
71 | 2657503.6996 | 1220878.9899 | 2657505.0803 | 1220883.7062 | 2657511.1971 | 1220887.4342 | 2657510.7991 | 1220897.2253 | 2657508.9529 | 1220902.2106 | 2657506.9338 | 1220904.0751
72 | 2657503.6996 | 1220878.9899 | 2657496.9146 | 1220881.9694
73 | 2657450.8762 | 1220869.5966 | 2657443.2077 | 1220874.5968
74 | 2657547.2333 | 1220864.7124 | 2657557.7117 | 1220849.862
75 | 2657503.5792 | 1220907.1729 | 2657506.9338 | 1220904.0751
76 | 2657495.7225 | 1220882.4929 | 2657496.9146 | 1220881.9694
77 | 2657413.9715 | 1220817.3383 | 2657410.5601 | 1220819.5075
78 | 2657407.7407 | 1220821.3003 | 2657410.5601 | 1220819.5075
79 | 2657407.7407 | 1220821.3003 | 2657403.8733 | 1220823.7594
80 | 2657394.3689 | 1220829.8029 | 2657403.8733 | 1220823.7594
81 | 2657394.3689 | 1220829.8029 | 2657388.598 | 1220833.4724
82 | 2657388.598 | 1220833.4724 | 2657385.4493 | 1220835.4745

## bus_geodata
| x | y | coords
0 | 2657544.0479 | 1220669.8951
1 | 2657490.8853 | 1220699.844
2 | 2657661.7315 | 1220693.9243
3 | 2657476.6759 | 1220719.4079
4 | 2657673.212 | 1220672.6359
5 | 2657457.15 | 1220721.4876
6 | 2657475.2662 | 1220704.8632
7 | 2657588.1992 | 1220904.1771
8 | 2657574.0119 | 1220923.4798
9 | 2657575.9602 | 1220888.9286
10 | 2657528.7323 | 1220960.2264
11 | 2657546.8497 | 1220946.8273
12 | 2657514.5854 | 1220937.4042
13 | 2657674.5792 | 1220670.1006
14 | 2657433.2486 | 1220728.8506
15 | 2657462.942 | 1220743.7573
16 | 2657473.0738 | 1220681.1095
17 | 2657573.8263 | 1220885.7379
18 | 2657349.5468 | 1220857.6355
19 | 2657367.946 | 1220846.6043
20 | 2657324.5272 | 1220802.3271
21 | 2657536.8111 | 1220917.551
22 | 2657648.0119 | 1220626.7209
23 | 2657664.6933 | 1220646.5121
24 | 2657470.7935 | 1220659.2611
25 | 2657425.3388 | 1220678.1654
26 | 2657426.3698 | 1220686.9903
27 | 2657670.6703 | 1220653.0299
28 | 2657330.8194 | 1220811.0787
29 | 2657335.4924 | 1220817.5783
30 | 2657353.5994 | 1220747.7087
31 | 2657377.2806 | 1220752.4483
32 | 2657376.6657 | 1220713.1467
33 | 2657377.1702 | 1220717.3162
34 | 2657374.3539 | 1220842.5297
35 | 2657424.8895 | 1220886.5408
36 | 2657431.0153 | 1220882.5467
37 | 2657382.9112 | 1220743.6638
38 | 2657429.114 | 1220710.479
39 | 2657472.3005 | 1220754.1596
40 | 2657429.1074 | 1220710.4228
41 | 2657428.0238 | 1220701.1479
42 | 2657369.3585 | 1220771.209
43 | 2657396.1629 | 1220761.0926
44 | 2657356.9007 | 1220783.4011
45 | 2657401.3842 | 1220763.5823
46 | 2657406.6876 | 1220766.5471
47 | 2657443.9798 | 1220791.4262
48 | 2657447.16 | 1220793.6422
49 | 2657433.3251 | 1220805.0321
50 | 2657461.0153 | 1220803.2969
51 | 2657433.0414 | 1220805.2125
52 | 2657474.2867 | 1220812.5446
53 | 2657427.48 | 1220808.7488
54 | 2657485.4089 | 1220820.2948
55 | 2657488.7969 | 1220822.6556
56 | 2657503.1983 | 1220832.6897
57 | 2657504.7272 | 1220801.3777
58 | 2657494.3169 | 1220840.3481
59 | 2657505.8388 | 1220834.6102
60 | 2657506.9313 | 1220799.5633
61 | 2657511.4596 | 1220795.8354
62 | 2657467.7724 | 1220858.5796
63 | 2657527.6907 | 1220850.5038
64 | 2657530.0488 | 1220852.2165
65 | 2657519.2463 | 1220860.1534
66 | 2657530.3532 | 1220852.4378
67 | 2657503.6996 | 1220878.9899
68 | 2657450.8762 | 1220869.5966
69 | 2657547.2333 | 1220864.7124
70 | 2657506.9338 | 1220904.0751
71 | 2657496.9146 | 1220881.9694
72 | 2657557.7117 | 1220849.862
73 | 2657413.9715 | 1220817.3383
74 | 2657410.5601 | 1220819.5075
75 | 2657407.7407 | 1220821.3003
76 | 2657403.8733 | 1220823.7594
77 | 2657394.3689 | 1220829.8029
78 | 2657388.598 | 1220833.4724
79 | 2657385.4493 | 1220835.4745
80 | 2657443.2077 | 1220874.5968
81 | 2657466.6288 | 1220905.1708
82 | 2657495.7225 | 1220882.4929
83 | 2657503.5792 | 1220907.1729
84 | 2657488.7969 | 1220822.6556

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97621 | -0.16707 | 0.0013341 | 0.00033435
1 | 0.9784 | -0.15145 | 0 | 0
2 | 0.97206 | -0.19678 | 0 | 0
3 | 0.97968 | -0.14238 | 0 | 0
4 | 0.97124 | -0.2027 | 0.0057734 | 0.001447
5 | 0.98054 | -0.13625 | 0 | 0
6 | 0.97956 | -0.14324 | 0.0029488 | 0.00073903
7 | 0.99083 | -0.06432 | 0 | 0
8 | 0.99042 | -0.067204 | 0.0031364 | 0.00078607
9 | 0.99116 | -0.061974 | 0.010779 | 0.0027015
10 | 0.98984 | -0.071361 | 0 | 0
11 | 0.98998 | -0.070318 | 0.0040051 | 0.0010038
12 | 0.98965 | -0.072652 | 0.001773 | 0.00044434
13 | 0.97117 | -0.20323 | 0.0084881 | 0.0021273
14 | 0.98192 | -0.12645 | 0 | 0
15 | 0.98028 | -0.13814 | 0.0037629 | 0.00094308
16 | 0.97947 | -0.1439 | 0.0015606 | 0.00039113
17 | 0.99129 | -0.061098 | 0 | 0
18 | 0.993 | -0.048804 | 0 | 0
19 | 0.99311 | -0.048 | 0.0017649 | 0.00044232
20 | 0.99256 | -0.05195 | 0 | 0
21 | 0.98953 | -0.07354 | 0.0027546 | 0.00069037
22 | 0.97083 | -0.20567 | 0.00039536 | 9.9086e-05
23 | 0.97085 | -0.20556 | 0.0069774 | 0.0017487
24 | 0.97943 | -0.14415 | 0.0011001 | 0.00027571
25 | 0.98149 | -0.12955 | 0.0011244 | 0.0002818
26 | 0.9815 | -0.12944 | 0.0014952 | 0.00037473
27 | 0.97094 | -0.20487 | 0.0014852 | 0.00037224
28 | 0.9925 | -0.052353 | 0.001993 | 0.0004995
29 | 0.99248 | -0.052491 | 0.0016991 | 0.00042584
30 | 0.98647 | -0.094348 | 0.0063655 | 0.0015953
31 | 0.98669 | -0.092767 | 0 | 0
32 | 0.98535 | -0.10222 | 0.0057442 | 0.0014396
33 | 0.98539 | -0.10197 | 0.0044126 | 0.0011059
34 | 0.99317 | -0.04758 | 0.0020006 | 0.0005014
35 | 0.99537 | -0.032425 | 0.0030283 | 0.00075896
36 | 0.9954 | -0.032201 | 0 | 0
37 | 0.98579 | -0.099115 | 0 | 0
38 | 0.98161 | -0.12868 | 0.0033021 | 0.00082758
39 | 0.9802 | -0.13872 | 0.0039929 | 0.0010007
40 | 0.98161 | -0.12868 | 0.0041168 | 0.0010318
41 | 0.98156 | -0.12906 | 0.0012644 | 0.00031689
42 | 0.98647 | -0.09435 | 0.0025305 | 0.0006342
43 | 0.9889 | -0.077211 | 0.0026096 | 0.00065403
44 | 0.98634 | -0.095266 | 0.0049949 | 0.0012518
45 | 0.98954 | -0.072735 | 0.0038193 | 0.00095721
46 | 0.99025 | -0.067805 | 0.0016169 | 0.00040523
47 | 0.99556 | -0.030796 | 0 | 0
48 | 0.99587 | -0.028611 | 0.0063242 | 0.001585
49 | 0.99478 | -0.036293 | 0.0022292 | 0.0005587
50 | 0.99732 | -0.018575 | 0.0035837 | 0.00089815
51 | 0.99476 | -0.03639 | 0.0029157 | 0.00073074
52 | 0.99874 | -0.0086985 | 0.0065473 | 0.0016409
53 | 0.99452 | -0.038087 | 0.0024115 | 0.00060439
54 | 1 | 0 | -0.24073 | -0.060446
55 | 0.99968 | -0.0022504 | 0 | 0
56 | 0.9972 | -0.019509 | 0 | 0
57 | 0.99927 | -0.0051318 | 0.0032532 | 0.00081532
58 | 0.99689 | -0.021727 | 0.0015452 | 0.00038726
59 | 0.99683 | -0.022117 | 0.0039772 | 0.00099678
60 | 0.99923 | -0.0053461 | 0.0041435 | 0.0010385
61 | 0.99921 | -0.0055434 | 0.0033647 | 0.00084328
62 | 0.99609 | -0.027332 | 0.0034528 | 0.00086535
63 | 0.9939 | -0.042691 | 0 | 0
64 | 0.99366 | -0.044342 | 0 | 0
65 | 0.99354 | -0.045218 | 0.0057168 | 0.0014328
66 | 0.99363 | -0.044556 | 0.014615 | 0.0036628
67 | 0.99306 | -0.048608 | 0 | 0
68 | 0.99569 | -0.03014 | 0.0037884 | 0.00094946
69 | 0.99239 | -0.053336 | 0.0088024 | 0.0022061
70 | 0.99276 | -0.050703 | 0.0040464 | 0.0010141
71 | 0.99299 | -0.049116 | 0.0032645 | 0.00081817
72 | 0.99212 | -0.055233 | 0.010293 | 0.0025796
73 | 0.99399 | -0.041823 | 0.0024153 | 0.00060533
74 | 0.99387 | -0.042669 | 0.0025227 | 0.00063224
75 | 0.99378 | -0.043282 | 0.0025563 | 0.00064066
76 | 0.99368 | -0.044006 | 0.0030668 | 0.00076861
77 | 0.99348 | -0.045436 | 0.0013178 | 0.00033026
78 | 0.99337 | -0.046213 | 0.0013449 | 0.00033706
79 | 0.99331 | -0.046586 | 0.0024182 | 0.00060605
80 | 0.99556 | -0.031067 | 0.0023052 | 0.00057774
81 | 0.99508 | -0.034407 | 0.0047076 | 0.0011798
82 | 0.99298 | -0.049162 | 0.0035023 | 0.00087776
83 | 0.99274 | -0.050836 | 0.002864 | 0.0007178
84 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.024572 | -0.0061718 | 0.024626 | 0.0061916 | 5.3465e-05 | 1.9798e-05 | 0.03746 | 0.03746 | 0.03746 | 0.97621 | -0.16707 | 0.9784 | -0.15145 | 13.874
1 | 0.023238 | 0.0058374 | -0.023143 | -0.0058022 | 9.5649e-05 | 3.5268e-05 | 0.035426 | 0.035427 | 0.035427 | 0.97621 | -0.16707 | 0.97206 | -0.19678 | 13.1211
2 | -0.024626 | -0.0061916 | 0.024657 | 0.0062031 | 3.1163e-05 | 1.1538e-05 | 0.03746 | 0.037459 | 0.03746 | 0.9784 | -0.15145 | 0.97968 | -0.14238 | 13.8739
3 | 0.023143 | 0.0058022 | -0.023124 | -0.0057952 | 1.8942e-05 | 6.9859e-06 | 0.035427 | 0.035427 | 0.035427 | 0.97206 | -0.19678 | 0.97124 | -0.2027 | 13.1211
4 | -0.030267 | -0.0076086 | 0.030293 | 0.0076183 | 2.585e-05 | 9.6953e-06 | 0.045981 | 0.045981 | 0.045981 | 0.97968 | -0.14238 | 0.98054 | -0.13625 | 17.0299
5 | 0.0056104 | 0.0014055 | -0.0056098 | -0.0014054 | 6.6213e-07 | 7.069e-08 | 0.0085214 | 0.0085214 | 0.0085214 | 0.97968 | -0.14238 | 0.97956 | -0.14324 | 3.1561
6 | 0.01735 | 0.0043482 | -0.017349 | -0.0043478 | 1.27e-06 | 4.5283e-07 | 0.026582 | 0.026582 | 0.026582 | 0.97124 | -0.2027 | 0.97117 | -0.20323 | 9.8451
7 | -0.038051 | -0.0095625 | 0.038103 | 0.0095822 | 5.1999e-05 | 1.9684e-05 | 0.057754 | 0.057754 | 0.057754 | 0.98054 | -0.13625 | 0.98192 | -0.12645 | 21.3904
8 | 0.0077582 | 0.0019442 | -0.0077561 | -0.0019437 | 2.0192e-06 | 4.8223e-07 | 0.011773 | 0.011773 | 0.011773 | 0.98054 | -0.13625 | 0.98028 | -0.13814 | 4.3605
9 | 0.002661 | 0.00066637 | -0.0026607 | -0.00066657 | 2.4321e-07 | -2.0673e-07 | 0.004042 | 0.0040421 | 0.0040421 | 0.97956 | -0.14324 | 0.97947 | -0.1439 | 1.4971
10 | 0.011679 | 0.0029266 | -0.011675 | -0.0029252 | 4.6601e-06 | 1.4798e-06 | 0.01754 | 0.01754 | 0.01754 | 0.99083 | -0.06432 | 0.99042 | -0.067204 | 6.4962
11 | -0.011679 | -0.0029266 | 0.011683 | 0.0029278 | 3.7924e-06 | 1.2041e-06 | 0.01754 | 0.01754 | 0.01754 | 0.99083 | -0.06432 | 0.99116 | -0.061974 | 6.4962
12 | 0.0085382 | 0.0021391 | -0.0085345 | -0.0021381 | 3.6777e-06 | 9.5375e-07 | 0.012828 | 0.012828 | 0.012828 | 0.99042 | -0.067204 | 0.98998 | -0.070318 | 4.751
13 | -0.022462 | -0.0056293 | 0.022465 | 0.0056303 | 2.7238e-06 | 9.9813e-07 | 0.033722 | 0.033722 | 0.033722 | 0.99116 | -0.061974 | 0.99129 | -0.061098 | 12.4896
14 | -0.0045287 | -0.0011344 | 0.0045294 | 0.0011344 | 6.5283e-07 | -3.9119e-08 | 0.0068078 | 0.0068077 | 0.0068078 | 0.98984 | -0.071361 | 0.98998 | -0.070318 | 2.5214
15 | 0.0045287 | 0.0011344 | -0.0045279 | -0.0011344 | 8.0869e-07 | -4.8327e-08 | 0.0068078 | 0.0068079 | 0.0068079 | 0.98984 | -0.071361 | 0.98965 | -0.072652 | 2.5215
16 | 0.002755 | 0.0006901 | -0.0027546 | -0.00069037 | 3.3862e-07 | -2.7609e-07 | 0.0041422 | 0.0041423 | 0.0041423 | 0.98965 | -0.072652 | 0.98953 | -0.07354 | 1.5342
17 | 0.0088607 | 0.0022204 | -0.0088587 | -0.0022199 | 2.0142e-06 | 5.5803e-07 | 0.013576 | 0.013576 | 0.013576 | 0.97117 | -0.20323 | 0.97094 | -0.20487 | 5.0283
18 | -0.04941 | -0.012416 | 0.049599 | 0.012488 | 0.00018869 | 7.189e-05 | 0.074888 | 0.074888 | 0.074888 | 0.98192 | -0.12645 | 0.98579 | -0.099115 | 27.7363
19 | 0.011307 | 0.0028336 | -0.011303 | -0.0028325 | 3.4826e-06 | 1.0991e-06 | 0.017134 | 0.017134 | 0.017134 | 0.98192 | -0.12645 | 0.98161 | -0.12868 | 6.346
20 | 0.0039932 | 0.0010007 | -0.0039929 | -0.0010007 | 3.2255e-07 | -5.3289e-08 | 0.0060615 | 0.0060615 | 0.0060615 | 0.98028 | -0.13814 | 0.9802 | -0.13872 | 2.245
21 | 0.0011001 | 0.00027545 | -0.0011001 | -0.00027571 | 3.8303e-08 | -2.6185e-07 | 0.0016712 | 0.0016713 | 0.0016713 | 0.97947 | -0.1439 | 0.97943 | -0.14415 | 0.61901
22 | -0.022465 | -0.0056303 | 0.022489 | 0.0056392 | 2.4165e-05 | 8.8548e-06 | 0.033722 | 0.033722 | 0.033722 | 0.99129 | -0.061098 | 0.99239 | -0.053336 | 12.4896
23 | -0.003694 | -0.00092472 | 0.0036944 | 0.0009246 | 4.1031e-07 | -1.1987e-07 | 0.0055351 | 0.005535 | 0.0055351 | 0.993 | -0.048804 | 0.99311 | -0.048 | 2.05
24 | 0.003694 | 0.00092472 | -0.0036924 | -0.00092519 | 1.606e-06 | -4.6848e-07 | 0.0055351 | 0.0055355 | 0.0055355 | 0.993 | -0.048804 | 0.99256 | -0.05195 | 2.0502
25 | -0.0054593 | -0.0013669 | 0.0054596 | 0.0013669 | 3.1701e-07 | 2.3664e-08 | 0.0081793 | 0.0081793 | 0.0081793 | 0.99311 | -0.048 | 0.99317 | -0.04758 | 3.0294
26 | 0.0036924 | 0.00092519 | -0.0036922 | -0.00092525 | 2.061e-07 | -6.0037e-08 | 0.0055355 | 0.0055355 | 0.0055355 | 0.99256 | -0.05195 | 0.9925 | -0.052353 | 2.0502
27 | -0.00039536 | -9.9086e-05 | 0.00039537 | 9.8765e-05 | 5.9891e-09 | -3.2096e-07 | 0.00060598 | 0.00060586 | 0.00060598 | 0.97083 | -0.20567 | 0.97085 | -0.20556 | 0.22444
28 | -0.0073728 | -0.0018475 | 0.0073735 | 0.0018476 | 7.0465e-07 | 1.6165e-07 | 0.0113 | 0.0113 | 0.0113 | 0.97085 | -0.20556 | 0.97094 | -0.20487 | 4.1852
29 | -0.0011244 | -0.0002818 | 0.0011244 | 0.00028169 | 1.611e-08 | -1.0609e-07 | 0.0017047 | 0.0017046 | 0.0017047 | 0.98149 | -0.12955 | 0.9815 | -0.12944 | 0.63136
30 | -0.0026196 | -0.00065642 | 0.0026197 | 0.0006563 | 1.4028e-07 | -1.262e-07 | 0.0039714 | 0.0039714 | 0.0039714 | 0.9815 | -0.12944 | 0.98156 | -0.12906 | 1.4709
31 | 0.0016992 | 0.00042575 | -0.0016991 | -0.00042584 | 3.2417e-08 | -9.0981e-08 | 0.0025475 | 0.0025475 | 0.0025475 | 0.9925 | -0.052353 | 0.99248 | -0.052491 | 0.94352
32 | -0.0063655 | -0.0015953 | 0.0063669 | 0.0015956 | 1.3939e-06 | 2.2672e-07 | 0.0096019 | 0.0096018 | 0.0096019 | 0.98647 | -0.094348 | 0.98669 | -0.092767 | 3.5563
33 | 0.0075277 | 0.0018864 | -0.007526 | -0.0018861 | 1.6492e-06 | 3.7243e-07 | 0.011352 | 0.011352 | 0.011352 | 0.98669 | -0.092767 | 0.98647 | -0.09435 | 4.2046
34 | -0.073707 | -0.018537 | 0.073867 | 0.018598 | 0.00016018 | 6.1342e-05 | 0.11118 | 0.11118 | 0.11118 | 0.98669 | -0.092767 | 0.9889 | -0.077211 | 41.1777
35 | 0.059813 | 0.015055 | -0.05976 | -0.015034 | 5.2967e-05 | 2.0239e-05 | 0.090226 | 0.090226 | 0.090226 | 0.98669 | -0.092767 | 0.98579 | -0.099115 | 33.4169
36 | -0.0057442 | -0.0014396 | 0.0057444 | 0.0014397 | 1.972e-07 | 2.2348e-08 | 0.0086745 | 0.0086745 | 0.0086745 | 0.98535 | -0.10222 | 0.98539 | -0.10197 | 3.2128
37 | -0.010157 | -0.0025456 | 0.010161 | 0.0025468 | 4.0176e-06 | 1.1964e-06 | 0.015338 | 0.015338 | 0.015338 | 0.98539 | -0.10197 | 0.98579 | -0.099115 | 5.6807
38 | -0.0074602 | -0.0018683 | 0.0074612 | 0.0018686 | 1.0249e-06 | 2.2402e-07 | 0.011177 | 0.011177 | 0.011177 | 0.99317 | -0.04758 | 0.99331 | -0.046586 | 4.1395
39 | -0.0030283 | -0.00075896 | 0.0030284 | 0.0007589 | 9.3523e-08 | -5.9085e-08 | 0.0045271 | 0.0045271 | 0.0045271 | 0.99537 | -0.032425 | 0.9954 | -0.032201 | 1.6767
40 | 0.0047091 | 0.0011798 | -0.0047076 | -0.0011798 | 1.437e-06 | -5.1187e-08 | 0.0070394 | 0.0070397 | 0.0070397 | 0.9954 | -0.032201 | 0.99508 | -0.034407 | 2.6073
41 | -0.0077375 | -0.0019387 | 0.0077387 | 0.001939 | 1.2151e-06 | 2.7811e-07 | 0.011567 | 0.011566 | 0.011567 | 0.9954 | -0.032201 | 0.99556 | -0.031067 | 4.2839
42 | 0.0080011 | 0.0020049 | -0.0080011 | -0.0020049 | 5.1884e-09 | 1.2803e-09 | 0.012129 | 0.012129 | 0.012129 | 0.98161 | -0.12868 | 0.98161 | -0.12868 | 4.4921
43 | 0.0038843 | 0.00097315 | -0.0038841 | -0.00097319 | 2.0202e-07 | -4.0337e-08 | 0.0058881 | 0.0058882 | 0.0058882 | 0.98161 | -0.12868 | 0.98156 | -0.12906 | 2.1808
44 | 0.0049955 | 0.0012519 | -0.0049949 | -0.0012518 | 6.3373e-07 | 1.5431e-08 | 0.0075354 | 0.0075354 | 0.0075354 | 0.98647 | -0.09435 | 0.98634 | -0.095266 | 2.7909
45 | -0.076477 | -0.019252 | 0.076525 | 0.01927 | 4.7849e-05 | 1.8329e-05 | 0.11511 | 0.11511 | 0.11511 | 0.9889 | -0.077211 | 0.98954 | -0.072735 | 42.632
46 | -0.080344 | -0.020228 | 0.0804 | 0.020249 | 5.537e-05 | 2.1218e-05 | 0.12085 | 0.12085 | 0.12085 | 0.98954 | -0.072735 | 0.99025 | -0.067805 | 44.7591
47 | -0.082017 | -0.020654 | 0.082443 | 0.020817 | 0.00042652 | 0.00016347 | 0.12328 | 0.12328 | 0.12328 | 0.99025 | -0.067805 | 0.99556 | -0.030796 | 45.6589
48 | -0.11315 | -0.028519 | 0.11319 | 0.028532 | 3.4615e-05 | 1.3213e-05 | 0.16918 | 0.16918 | 0.16918 | 0.99556 | -0.030796 | 0.99587 | -0.028611 | 31.3302
49 | 0.030711 | 0.0077014 | -0.030688 | -0.0076927 | 2.3383e-05 | 8.7624e-06 | 0.045904 | 0.045904 | 0.045904 | 0.99556 | -0.030796 | 0.99478 | -0.036293 | 17.0015
50 | -0.11951 | -0.030117 | 0.11968 | 0.030181 | 0.00016813 | 6.4224e-05 | 0.17863 | 0.17863 | 0.17863 | 0.99587 | -0.028611 | 0.99732 | -0.018575 | 33.0801
51 | 0.028458 | 0.007134 | -0.028458 | -0.0071338 | 3.8013e-07 | 1.4184e-07 | 0.042569 | 0.042569 | 0.042569 | 0.99478 | -0.036293 | 0.99476 | -0.03639 | 15.7665
52 | -0.12326 | -0.03108 | 0.12344 | 0.031145 | 0.00017083 | 6.5279e-05 | 0.18398 | 0.18398 | 0.18398 | 0.99732 | -0.018575 | 0.99874 | -0.0086985 | 34.0702
53 | 0.025542 | 0.0064031 | -0.025536 | -0.0064009 | 6.0036e-06 | 2.2236e-06 | 0.038208 | 0.038208 | 0.038208 | 0.99476 | -0.03639 | 0.99452 | -0.038087 | 14.1511
54 | -0.12998 | -0.032786 | 0.13014 | 0.032846 | 0.00015875 | 6.0701e-05 | 0.19373 | 0.19373 | 0.19373 | 0.99874 | -0.0086985 | 1 | 0 | 35.8766
55 | 0.023125 | 0.0057965 | -0.023113 | -0.0057921 | 1.1958e-05 | 4.3918e-06 | 0.0346 | 0.0346 | 0.0346 | 0.99452 | -0.038087 | 0.99399 | -0.041823 | 12.8148
56 | 0.10979 | 0.0276 | -0.10976 | -0.027587 | 3.44e-05 | 1.3123e-05 | 0.1634 | 0.1634 | 0.1634 | 1 | 0 | 0.99968 | -0.0022504 | 30.2598
57 | 0.098993 | 0.024888 | -0.098755 | -0.024797 | 0.00023743 | 9.109e-05 | 0.14738 | 0.14738 | 0.14738 | 0.99968 | -0.0022504 | 0.9972 | -0.019509 | 54.5844
58 | 0.010766 | 0.0026984 | -0.010762 | -0.0026971 | 4.2939e-06 | 1.3003e-06 | 0.016025 | 0.016025 | 0.016025 | 0.99968 | -0.0022504 | 0.99927 | -0.0051318 | 5.9353
59 | 0.018856 | 0.0047278 | -0.01885 | -0.0047257 | 5.7937e-06 | 2.0754e-06 | 0.028138 | 0.028138 | 0.028138 | 0.9972 | -0.019509 | 0.99689 | -0.021727 | 10.4214
60 | 0.079899 | 0.02007 | -0.07987 | -0.020058 | 2.8968e-05 | 1.1099e-05 | 0.11924 | 0.11924 | 0.11924 | 0.9972 | -0.019509 | 0.99683 | -0.022117 | 44.1631
61 | 0.0075085 | 0.0018817 | -0.0075083 | -0.0018817 | 2.2271e-07 | 4.8258e-08 | 0.011181 | 0.011181 | 0.011181 | 0.99927 | -0.0051318 | 0.99923 | -0.0053461 | 4.1411
62 | 0.017305 | 0.0043385 | -0.017292 | -0.0043337 | 1.3426e-05 | 4.7437e-06 | 0.025831 | 0.025831 | 0.025831 | 0.99689 | -0.021727 | 0.99609 | -0.027332 | 9.5672
63 | 0.075893 | 0.019062 | -0.075676 | -0.018979 | 0.00021645 | 8.29e-05 | 0.1133 | 0.1133 | 0.1133 | 0.99683 | -0.022117 | 0.9939 | -0.042691 | 41.9643
64 | 0.0033648 | 0.00084323 | -0.0033647 | -0.00084328 | 9.1892e-08 | -4.1487e-08 | 0.0050107 | 0.0050107 | 0.0050107 | 0.99923 | -0.0053461 | 0.99921 | -0.0055434 | 1.8558
65 | 0.013839 | 0.0034684 | -0.013834 | -0.0034666 | 5.3794e-06 | 1.8065e-06 | 0.020673 | 0.020674 | 0.020674 | 0.99609 | -0.027332 | 0.99569 | -0.03014 | 7.6569
66 | 0.056267 | 0.014113 | -0.056254 | -0.014108 | 1.2883e-05 | 4.9171e-06 | 0.084244 | 0.084244 | 0.084244 | 0.9939 | -0.042691 | 0.99366 | -0.044342 | 31.2013
67 | 0.01941 | 0.0048656 | -0.019403 | -0.0048632 | 6.7916e-06 | 2.4452e-06 | 0.02906 | 0.02906 | 0.02906 | 0.9939 | -0.042691 | 0.99354 | -0.045218 | 10.763
68 | 0.056254 | 0.014108 | -0.056252 | -0.014108 | 1.6667e-06 | 6.3616e-07 | 0.084244 | 0.084244 | 0.084244 | 0.99366 | -0.044342 | 0.99363 | -0.044556 | 31.2013
69 | 0.013686 | 0.0034304 | -0.01368 | -0.0034283 | 6.4226e-06 | 2.1531e-06 | 0.020498 | 0.020498 | 0.020498 | 0.99354 | -0.045218 | 0.99306 | -0.048608 | 7.5919
70 | 0.041637 | 0.010445 | -0.041587 | -0.010426 | 5.0642e-05 | 1.9208e-05 | 0.062358 | 0.062358 | 0.062358 | 0.99363 | -0.044556 | 0.99239 | -0.053336 | 23.0954
71 | 0.0069125 | 0.0017323 | -0.0069105 | -0.0017319 | 2.0044e-06 | 3.8368e-07 | 0.010358 | 0.010358 | 0.010358 | 0.99306 | -0.048608 | 0.99276 | -0.050703 | 3.8363
72 | 0.0067673 | 0.001696 | -0.0067668 | -0.0016959 | 4.7547e-07 | 8.7006e-08 | 0.01014 | 0.01014 | 0.01014 | 0.99306 | -0.048608 | 0.99299 | -0.049116 | 3.7557
73 | 0.010045 | 0.0025171 | -0.010044 | -0.0025167 | 1.2874e-06 | 3.7609e-07 | 0.015012 | 0.015012 | 0.015012 | 0.99569 | -0.03014 | 0.99556 | -0.031067 | 5.56
74 | 0.010295 | 0.0025804 | -0.010293 | -0.0025796 | 2.7027e-06 | 8.0473e-07 | 0.015437 | 0.015437 | 0.015437 | 0.99239 | -0.053336 | 0.99212 | -0.055233 | 5.7175
75 | 0.0028641 | 0.00071776 | -0.002864 | -0.0007178 | 5.251e-08 | -3.8844e-08 | 0.0042929 | 0.0042929 | 0.0042929 | 0.99276 | -0.050703 | 0.99274 | -0.050836 | 1.59
76 | 0.0035023 | 0.00087775 | -0.0035023 | -0.00087776 | 2.2378e-08 | -8.2349e-09 | 0.0052483 | 0.0052483 | 0.0052483 | 0.99299 | -0.049116 | 0.99298 | -0.049162 | 1.9438
77 | 0.020697 | 0.0051868 | -0.020695 | -0.0051859 | 2.4218e-06 | 8.7906e-07 | 0.030984 | 0.030984 | 0.030984 | 0.99399 | -0.041823 | 0.99387 | -0.042669 | 11.4756
78 | 0.018172 | 0.0045536 | -0.018171 | -0.0045531 | 1.5433e-06 | 5.5028e-07 | 0.027207 | 0.027207 | 0.027207 | 0.99387 | -0.042669 | 0.99378 | -0.043282 | 10.0768
79 | 0.015615 | 0.0039124 | -0.015613 | -0.0039119 | 1.5632e-06 | 5.4186e-07 | 0.02338 | 0.02338 | 0.02338 | 0.99378 | -0.043282 | 0.99368 | -0.044006 | 8.6592
80 | 0.012546 | 0.0031433 | -0.012544 | -0.0031425 | 2.4807e-06 | 8.0824e-07 | 0.018787 | 0.018787 | 0.018787 | 0.99368 | -0.044006 | 0.99348 | -0.045436 | 6.9583
81 | 0.011226 | 0.0028122 | -0.011225 | -0.0028118 | 1.2064e-06 | 3.7545e-07 | 0.016814 | 0.016814 | 0.016814 | 0.99348 | -0.045436 | 0.99337 | -0.046213 | 6.2273
82 | 0.0098799 | 0.0024748 | -0.0098794 | -0.0024746 | 5.0994e-07 | 1.4783e-07 | 0.014799 | 0.014799 | 0.014799 | 0.99337 | -0.046213 | 0.99331 | -0.046586 | 5.4812

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24491 | 0.061493

## res_load
| p_mw | q_mvar
0 | 0.0013341 | 0.00033435
1 | 0.0057734 | 0.001447
2 | 0.0029488 | 0.00073903
3 | 0.0031364 | 0.00078607
4 | 0.010779 | 0.0027015
5 | 0.0040051 | 0.0010038
6 | 0.001773 | 0.00044434
7 | 0.0084881 | 0.0021273
8 | 0.0037629 | 0.00094308
9 | 0.0015606 | 0.00039113
10 | 0.0017649 | 0.00044232
11 | 0.0027546 | 0.00069037
12 | 0.00039536 | 9.9086e-05
13 | 0.0069774 | 0.0017487
14 | 0.0011001 | 0.00027571
15 | 0.0011244 | 0.0002818
16 | 0.0014952 | 0.00037473
17 | 0.0014852 | 0.00037224
18 | 0.001993 | 0.0004995
19 | 0.0016991 | 0.00042584
20 | 0.0063655 | 0.0015953
21 | 0.0057442 | 0.0014396
22 | 0.0044126 | 0.0011059
23 | 0.0020006 | 0.0005014
24 | 0.0030283 | 0.00075896
25 | 0.0033021 | 0.00082758
26 | 0.0039929 | 0.0010007
27 | 0.0041168 | 0.0010318
28 | 0.0012644 | 0.00031689
29 | 0.0025305 | 0.0006342
30 | 0.0026096 | 0.00065403
31 | 0.0049949 | 0.0012518
32 | 0.0038193 | 0.00095721
33 | 0.0016169 | 0.00040523
34 | 0.0063242 | 0.001585
35 | 0.0022292 | 0.0005587
36 | 0.0035837 | 0.00089815
37 | 0.0029157 | 0.00073074
38 | 0.0065473 | 0.0016409
39 | 0.0024115 | 0.00060439
40 | 0.0041772 | 0.0010469
41 | 0.0032532 | 0.00081532
42 | 0.0015452 | 0.00038726
43 | 0.0039772 | 0.00099678
44 | 0.0041435 | 0.0010385
45 | 0.0033647 | 0.00084328
46 | 0.0034528 | 0.00086535
47 | 0.0057168 | 0.0014328
48 | 0.014615 | 0.0036628
49 | 0.0037884 | 0.00094946
50 | 0.0088024 | 0.0022061
51 | 0.0040464 | 0.0010141
52 | 0.0032645 | 0.00081817
53 | 0.010293 | 0.0025796
54 | 0.0024153 | 0.00060533
55 | 0.0025227 | 0.00063224
56 | 0.0025563 | 0.00064066
57 | 0.0030668 | 0.00076861
58 | 0.0013178 | 0.00033026
59 | 0.0013449 | 0.00033706
60 | 0.0024182 | 0.00060605
61 | 0.0023052 | 0.00057774
62 | 0.0047076 | 0.0011798
63 | 0.0035023 | 0.00087776
64 | 0.002864 | 0.0007178

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1