## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1104-19_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1104-19_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1104-19_0_4_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_1104-19_0_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_1104-19_0_4_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1104-19_0_4_node_52 | 0.4 | n |  | TRUE
6 | bus_LV_1104-19_0_4_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_1104-19_0_4_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_1104-19_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1104-19_0_4_node_49 | 0.4 | n |  | TRUE
10 | bus_LV_1104-19_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1104-19_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1104-19_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1104-19_0_4_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_1104-19_0_4_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_1104-19_0_4_node_35 | 0.4 | n |  | TRUE
16 | bus_LV_1104-19_0_4_node_34 | 0.4 | n |  | TRUE
17 | bus_LV_1104-19_0_4_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_1104-19_0_4_node_32 | 0.4 | n |  | TRUE
19 | bus_LV_1104-19_0_4_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_1104-19_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1104-19_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1104-19_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1104-19_0_4_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1104-19_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1104-19_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1104-19_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1104-19_0_4_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_1104-19_0_4_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_1104-19_0_4_node_33 | 0.4 | n |  | TRUE
30 | bus_LV_1104-19_0_4_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_1104-19_0_4_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_1104-19_0_4_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_1104-19_0_4_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_1104-19_0_4_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_1104-19_0_4_node_42 | 0.4 | n |  | TRUE
36 | bus_LV_1104-19_0_4_node_39 | 0.4 | n |  | TRUE
37 | bus_LV_1104-19_0_4_node_43 | 0.4 | n |  | TRUE
38 | bus_LV_1104-19_0_4_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_1104-19_0_4_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_1104-19_0_4_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_1104-19_0_4_node_40 | 0.4 | n |  | TRUE
42 | bus_LV_1104-19_0_4_node_48 | 0.4 | n |  | TRUE
43 | bus_LV_1104-19_0_4_node_50 | 0.4 | n |  | TRUE
44 | bus_LV_1104-19_0_4_node_46 | 0.4 | n |  | TRUE
45 | bus_LV_1104-19_0_4_node_44 | 0.4 | n |  | TRUE
46 | bus_LV_1104-19_0_4_node_54 | 0.4 | n |  | TRUE
47 | bus_LV_1104-19_0_4_node_53 | 0.4 | n |  | TRUE
48 | bus_LV_1104-19_0_4_node_55 | 0.4 | n |  | TRUE
49 | bus_LV_1104-19_0_4_node_45 | 0.4 | n |  | TRUE
50 | bus_LV_1104-19_0_4_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_1104-19_0_4_node_51 | 0.4 | n |  | TRUE
52 | bus_LV_1104-19_0_4_node_56 | 0.4 | n |  | TRUE
53 | bus_LV_1104-19_0_4_node_58 | 0.4 | n |  | TRUE
54 | bus_LV_1104-19_0_4_node_57 | 0.4 | n |  | TRUE
55 | bus_MV_472_0_node_62 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1104-19_0_4_load_0 | 0 | 0.0082393 | 0.002065 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1104-19_0_4_load_2 | 1 | 0.0022864 | 0.00057302 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1104-19_0_4_load_4 | 2 | 0.0077986 | 0.0019545 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1104-19_0_4_load_6 | 4 | 0.0066634 | 0.00167 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1104-19_0_4_load_52 | 5 | 0.016272 | 0.0040781 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1104-19_0_4_load_12 | 6 | 0.009262 | 0.0023213 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1104-19_0_4_load_7 | 8 | 0.0017466 | 0.00043773 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1104-19_0_4_load_49 | 9 | 0.0014646 | 0.00036706 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1104-19_0_4_load_8 | 10 | 0.0024549 | 0.00061525 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1104-19_0_4_load_9 | 11 | 0.0028586 | 0.00071644 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1104-19_0_4_load_10 | 12 | 0.007475 | 0.0018734 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1104-19_0_4_load_14 | 14 | 0.0042917 | 0.0010756 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1104-19_0_4_load_35 | 15 | 0.00204 | 0.00051127 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1104-19_0_4_load_34 | 16 | 0.0051332 | 0.0012865 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1104-19_0_4_load_23 | 17 | 0.0036214 | 0.00090761 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1104-19_0_4_load_32 | 18 | 0.0013967 | 0.00035004 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1104-19_0_4_load_15 | 20 | 0.032834 | 0.0082289 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1104-19_0_4_load_18 | 22 | 0.0050434 | 0.001264 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1104-19_0_4_load_19 | 23 | 0.0035889 | 0.00089945 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1104-19_0_4_load_20 | 24 | 0.0012306 | 0.00030841 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1104-19_0_4_load_22 | 26 | 0.0015232 | 0.00038176 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1104-19_0_4_load_31 | 27 | 0.0029082 | 0.00072886 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1104-19_0_4_load_24 | 28 | 0.0038848 | 0.00097363 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1104-19_0_4_load_33 | 29 | 0.0070585 | 0.001769 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1104-19_0_4_load_26 | 30 | 0.002685 | 0.00067293 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1104-19_0_4_load_27 | 31 | 0.0064992 | 0.0016289 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1104-19_0_4_load_29 | 32 | 0.0020778 | 0.00052075 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1104-19_0_4_load_41 | 34 | 0.0069337 | 0.0017378 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1104-19_0_4_load_42 | 35 | 0.0099276 | 0.0024881 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1104-19_0_4_load_39 | 36 | 0.0027204 | 0.0006818 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1104-19_0_4_load_36 | 38 | 0.0025722 | 0.00064464 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1104-19_0_4_load_37 | 39 | 0.0023596 | 0.00059138 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1104-19_0_4_load_40 | 41 | 0.0027255 | 0.00068307 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1104-19_0_4_load_50 | 43 | 0.0022621 | 0.00056694 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1104-19_0_4_load_46 | 44 | 0.0043366 | 0.0010869 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1104-19_0_4_load_54 | 46 | 0.0068412 | 0.0017146 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1104-19_0_4_load_53 | 47 | 0.0073618 | 0.001845 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1104-19_0_4_load_55 | 48 | 0.0072095 | 0.0018069 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1104-19_0_4_load_45 | 49 | 0.0039246 | 0.0009836 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1104-19_0_4_load_47 | 50 | 0.0016936 | 0.00042446 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1104-19_0_4_load_51 | 51 | 0.0022725 | 0.00056955 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1104-19_0_4_load_56 | 52 | 0.0059884 | 0.0015008 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1104-19_0_4_load_58 | 53 | 0.0096404 | 0.0024161 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1104-19_0_4_load_57 | 54 | 0.0030739 | 0.0007704 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 44 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1104-19_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.015191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1104-19_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.016353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
2 | LV_1104-19_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.030017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_1104-19_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0059507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_1104-19_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.014559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1104-19_0_4_line_5 | NAYY 4x150 SE | 4 | 8 | 0.017829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1104-19_0_4_line_6 | NAYY 4x150 SE | 5 | 9 | 0.03939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1104-19_0_4_line_7 | NAYY 4x150 SE | 6 | 7 | 0.025345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1104-19_0_4_line_8 | NAYY 4x150 SE | 7 | 13 | 0.013349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1104-19_0_4_line_9 | NAYY 4x150 SE | 7 | 14 | 0.042905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1104-19_0_4_line_10 | NAYY 4x150 SE | 7 | 12 | 0.017819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1104-19_0_4_line_11 | NAYY 4x150 SE | 8 | 10 | 0.0054918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_1104-19_0_4_line_12 | NAYY 4x150 SE | 9 | 50 | 0.015123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1104-19_0_4_line_13 | NAYY 4x150 SE | 10 | 11 | 1.5315e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1104-19_0_4_line_14 | NAYY 4x150 SE | 11 | 12 | 0.021814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1104-19_0_4_line_15 | NAYY 4x150 SE | 13 | 15 | 0.016964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1104-19_0_4_line_16 | NAYY 4x150 SE | 13 | 16 | 0.031084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_1104-19_0_4_line_17 | NAYY 4x150 SE | 14 | 17 | 0.022277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1104-19_0_4_line_18 | NAYY 4x150 SE | 16 | 18 | 0.011555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1104-19_0_4_line_19 | NAYY 4x150 SE | 17 | 19 | 0.0056968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1104-19_0_4_line_20 | NAYY 4x150 SE | 18 | 25 | 0.036744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1104-19_0_4_line_21 | NAYY 4x150 SE | 19 | 21 | 0.014752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1104-19_0_4_line_22 | NAYY 4x150 SE | 20 | 21 | 0.015494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1104-19_0_4_line_23 | NAYY 4x150 SE | 22 | 23 | 0.003542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1104-19_0_4_line_24 | NAYY 4x150 SE | 22 | 24 | 0.009215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1104-19_0_4_line_25 | NAYY 4x150 SE | 23 | 25 | 0.039549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1104-19_0_4_line_26 | NAYY 4x150 SE | 24 | 26 | 0.018753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1104-19_0_4_line_27 | NAYY 4x150 SE | 25 | 27 | 0.016495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1104-19_0_4_line_28 | NAYY 4x150 SE | 26 | 28 | 0.01501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1104-19_0_4_line_29 | NAYY 4x150 SE | 27 | 29 | 0.0084866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1104-19_0_4_line_30 | NAYY 4x150 SE | 29 | 32 | 0.0049909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1104-19_0_4_line_31 | NAYY 4x150 SE | 30 | 31 | 0.017575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1104-19_0_4_line_32 | NAYY 4x150 SE | 31 | 32 | 0.04205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1104-19_0_4_line_33 | NAYY 4x150 SE | 33 | 34 | 0.059762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1104-19_0_4_line_34 | NAYY 4x150 SE | 33 | 35 | 0.10677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1104-19_0_4_line_35 | NAYY 4x150 SE | 34 | 36 | 0.0093922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1104-19_0_4_line_36 | NAYY 4x150 SE | 35 | 37 | 0.05414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1104-19_0_4_line_37 | NAYY 4x150 SE | 36 | 40 | 0.013347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
38 | LV_1104-19_0_4_line_38 | NAYY 4x150 SE | 37 | 45 | 0.11087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1104-19_0_4_line_39 | NAYY 4x150 SE | 38 | 39 | 0.018449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1104-19_0_4_line_40 | NAYY 4x150 SE | 39 | 40 | 0.010932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1104-19_0_4_line_41 | NAYY 4x150 SE | 40 | 41 | 0.030826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
42 | LV_1104-19_0_4_line_42 | NAYY 4x150 SE | 41 | 42 | 0.016901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
43 | LV_1104-19_0_4_line_43 | NAYY 4x150 SE | 42 | 43 | 0.010981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1104-19_0_4_line_44 | NAYY 4x150 SE | 42 | 44 | 0.0071909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
45 | LV_1104-19_0_4_line_45 | NAYY 4x150 SE | 43 | 51 | 0.018014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1104-19_0_4_line_46 | NAYY 4x150 SE | 44 | 49 | 0.039929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
47 | LV_1104-19_0_4_line_47 | NAYY 4x150 SE | 45 | 46 | 0.020336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1104-19_0_4_line_48 | NAYY 4x150 SE | 45 | 47 | 0.072338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1104-19_0_4_line_49 | NAYY 4x150 SE | 46 | 48 | 0.051376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1104-19_0_4_line_50 | NAYY 4x150 SE | 48 | 52 | 0.011815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1104-19_0_4_line_51 | NAYY 4x150 SE | 49 | 50 | 0.022071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
52 | LV_1104-19_0_4_line_52 | NAYY 4x150 SE | 52 | 53 | 0.033901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1104-19_0_4_line_53 | NAYY 4x150 SE | 53 | 54 | 0.0017059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1104-19_0_4_trafo_46 | 0.25 MVA 20/0.4 kV | 55 | 44 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2648304.0555 | 1231722.1788 | 2648317.177 | 1231729.8328
1 | 2648304.0555 | 1231722.1788 | 2648298.8954 | 1231737.6965
2 | 2648313.5332 | 1231693.6934 | 2648304.0555 | 1231722.1788
3 | 2648297.0177 | 1231743.3432 | 2648298.8954 | 1231737.6965
4 | 2648313.5332 | 1231693.6934 | 2648300.2563 | 1231687.7196
5 | 2648297.0177 | 1231743.3432 | 2648291.3918 | 1231760.2614
6 | 2648300.2563 | 1231687.7196 | 2648291.6146 | 1231683.8314 | 2648287.2022 | 1231683.5287 | 2648270.9967 | 1231692.8476 | 2648264.9737 | 1231695.9982
7 | 2648276.4872 | 1231802.8616 | 2648279.3397 | 1231804.0855 | 2648290.9382 | 1231809.0717 | 2648299.4327 | 1231813.5779
8 | 2648263.2756 | 1231800.6975 | 2648272.4186 | 1231802.1948 | 2648276.4872 | 1231802.8616
9 | 2648276.4872 | 1231802.8616 | 2648268.1433 | 1231823.2623 | 2648259.9872 | 1231842.466
10 | 2648276.4872 | 1231802.8616 | 2648282.6551 | 1231786.5347 | 2648282.7707 | 1231786.187
11 | 2648289.6589 | 1231765.4726 | 2648291.3918 | 1231760.2614
12 | 2648264.9737 | 1231695.9982 | 2648251.5737 | 1231703.0075
13 | 2648289.6589 | 1231765.4726 | 2648289.6541 | 1231765.4872
14 | 2648289.6541 | 1231765.4872 | 2648282.7707 | 1231786.187
15 | 2648263.2756 | 1231800.6975 | 2648247.5151 | 1231794.4212
16 | 2648263.2756 | 1231800.6975 | 2648256.7376 | 1231806.6482 | 2648249.8487 | 1231814.7863 | 2648242.7899 | 1231823.9671
17 | 2648251.2787 | 1231862.9701 | 2648259.9872 | 1231842.466
18 | 2648242.7899 | 1231823.9671 | 2648235.7468 | 1231833.1274
19 | 2648249.0517 | 1231868.2136 | 2648251.2787 | 1231862.9701
20 | 2648211.253 | 1231860.38 | 2648215.2382 | 1231857.3215 | 2648234.0218 | 1231835.371 | 2648235.7468 | 1231833.1274
21 | 2648249.0517 | 1231868.2136 | 2648262.7968 | 1231873.673
22 | 2648262.7968 | 1231873.673 | 2648277.1941 | 1231879.3972
23 | 2648179.6327 | 1231884.1287 | 2648176.7612 | 1231886.2024
24 | 2648169.2907 | 1231891.5975 | 2648176.7612 | 1231886.2024
25 | 2648211.253 | 1231860.38 | 2648190.2758 | 1231876.4424 | 2648179.6327 | 1231884.1287
26 | 2648169.2907 | 1231891.5975 | 2648154.0875 | 1231902.577 | 2648154.0875 | 1231902.577
27 | 2648211.253 | 1231860.38 | 2648198.4357 | 1231849.9973
28 | 2648143.7689 | 1231913.4782 | 2648154.0875 | 1231902.577
29 | 2648198.4357 | 1231849.9973 | 2648191.8412 | 1231844.6553
30 | 2648187.9631 | 1231841.5139 | 2648191.8412 | 1231844.6553
31 | 2648144.5072 | 1231842.8729 | 2648156.7384 | 1231830.2528
32 | 2648187.9631 | 1231841.5139 | 2648177.2035 | 1231832.7979 | 2648164.8961 | 1231821.8358 | 2648156.7384 | 1231830.2528
33 | 2648092.5055 | 1231738.1974 | 2648101.039 | 1231744.8594 | 2648145.5759 | 1231765.1384
34 | 2648092.5055 | 1231738.1974 | 2648151.3414 | 1231680.6369 | 2648170.3823 | 1231665.2799
35 | 2648154.1237 | 1231769.0304 | 2648145.5759 | 1231765.1384
36 | 2648214.0181 | 1231633.3035 | 2648191.43 | 1231649.0193 | 2648187.2358 | 1231651.687 | 2648170.3823 | 1231665.2799
37 | 2648166.2711 | 1231774.5615 | 2648154.1237 | 1231769.0304
38 | 2648194.096 | 1231543.3965 | 2648217.6444 | 1231560.5982 | 2648204.3476 | 1231579.1466 | 2648201.0232 | 1231587.5471 | 2648200.7787 | 1231593.4155 | 2648200.7497 | 1231612.872 | 2648203.2893 | 1231619.0743 | 2648206.663 | 1231623.282 | 2648214.0181 | 1231633.3035
39 | 2648193.5685 | 1231784.1752 | 2648186.7766 | 1231784.0335 | 2648176.1957 | 1231779.1459
40 | 2648166.2711 | 1231774.5615 | 2648176.1957 | 1231779.1459
41 | 2648166.2711 | 1231774.5615 | 2648168.554 | 1231766.6416 | 2648182.79 | 1231749.1103
42 | 2648193.4436 | 1231735.9905 | 2648182.79 | 1231749.1103
43 | 2648193.4436 | 1231735.9905 | 2648190.6095 | 1231731.5648 | 2648185.923 | 1231728.2754
44 | 2648193.4436 | 1231735.9905 | 2648198.3372 | 1231730.7215
45 | 2648185.923 | 1231728.2754 | 2648180.113 | 1231724.1973 | 2648177.7397 | 1231719.8976 | 2648179.259 | 1231716.5078 | 2648180.7685 | 1231714.7866
46 | 2648230.0863 | 1231707.3985 | 2648221.6526 | 1231710.6587 | 2648206.736 | 1231721.6781 | 2648198.3372 | 1231730.7215
47 | 2648194.096 | 1231543.3965 | 2648182.269 | 1231559.9401
48 | 2648194.096 | 1231543.3965 | 2648182.9993 | 1231535.2904 | 2648178.1668 | 1231532.6051 | 2648173.5307 | 1231532.7899 | 2648167.3195 | 1231536.7088 | 2648143.1376 | 1231569.9218
49 | 2648182.269 | 1231559.9401 | 2648152.3902 | 1231601.7342
50 | 2648145.5187 | 1231611.3461 | 2648152.3902 | 1231601.7342
51 | 2648230.0863 | 1231707.3985 | 2648236.5265 | 1231704.9089 | 2648251.5737 | 1231703.0075 | 2648251.5737 | 1231703.0075
52 | 2648145.5187 | 1231611.3461 | 2648112.4559 | 1231618.8389
53 | 2648112.4559 | 1231618.8389 | 2648111.4518 | 1231620.218

## bus_geodata
| x | y | coords
0 | 2648317.177 | 1231729.8328
1 | 2648304.0555 | 1231722.1788
2 | 2648298.8954 | 1231737.6965
3 | 2648313.5332 | 1231693.6934
4 | 2648297.0177 | 1231743.3432
5 | 2648300.2563 | 1231687.7196
6 | 2648299.4327 | 1231813.5779
7 | 2648276.4872 | 1231802.8616
8 | 2648291.3918 | 1231760.2614
9 | 2648264.9737 | 1231695.9982
10 | 2648289.6589 | 1231765.4726
11 | 2648289.6541 | 1231765.4872
12 | 2648282.7707 | 1231786.187
13 | 2648263.2756 | 1231800.6975
14 | 2648259.9872 | 1231842.466
15 | 2648247.5151 | 1231794.4212
16 | 2648242.7899 | 1231823.9671
17 | 2648251.2787 | 1231862.9701
18 | 2648235.7468 | 1231833.1274
19 | 2648249.0517 | 1231868.2136
20 | 2648277.1941 | 1231879.3972
21 | 2648262.7968 | 1231873.673
22 | 2648176.7613 | 1231886.2024
23 | 2648179.6327 | 1231884.1287
24 | 2648169.2907 | 1231891.5975
25 | 2648211.253 | 1231860.38
26 | 2648154.0875 | 1231902.577
27 | 2648198.4357 | 1231849.9973
28 | 2648143.7689 | 1231913.4782
29 | 2648191.8412 | 1231844.6553
30 | 2648144.5072 | 1231842.8729
31 | 2648156.7384 | 1231830.2528
32 | 2648187.9631 | 1231841.5139
33 | 2648092.5055 | 1231738.1974
34 | 2648145.5759 | 1231765.1384
35 | 2648170.3823 | 1231665.2799
36 | 2648154.1237 | 1231769.0304
37 | 2648214.0181 | 1231633.3035
38 | 2648193.5685 | 1231784.1752
39 | 2648176.1957 | 1231779.1459
40 | 2648166.2711 | 1231774.5615
41 | 2648182.79 | 1231749.1103
42 | 2648193.4436 | 1231735.9905
43 | 2648185.923 | 1231728.2754
44 | 2648198.3372 | 1231730.7215
45 | 2648194.096 | 1231543.3965
46 | 2648182.269 | 1231559.9401
47 | 2648143.1376 | 1231569.9218
48 | 2648152.3902 | 1231601.7342
49 | 2648230.0863 | 1231707.3985
50 | 2648251.5737 | 1231703.0075
51 | 2648180.7685 | 1231714.7866
52 | 2648145.5187 | 1231611.3461
53 | 2648112.4559 | 1231618.8389
54 | 2648111.4518 | 1231620.218
55 | 2648193.4436 | 1231735.9905

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98231 | -0.12302 | 0.0082393 | 0.002065
1 | 0.98249 | -0.12172 | 0.0022864 | 0.00057302
2 | 0.98101 | -0.13223 | 0.0077986 | 0.0019545
3 | 0.98545 | -0.10089 | 0 | 0
4 | 0.9805 | -0.13582 | 0.0066634 | 0.00167
5 | 0.98688 | -0.090827 | 0.016272 | 0.0040781
6 | 0.97541 | -0.1721 | 0.009262 | 0.0023213
7 | 0.97575 | -0.16964 | 0 | 0
8 | 0.97907 | -0.14599 | 0.0017466 | 0.00043773
9 | 0.99123 | -0.060497 | 0.0014646 | 0.00036706
10 | 0.97863 | -0.14907 | 0.0024549 | 0.00061525
11 | 0.97863 | -0.14908 | 0.0028586 | 0.00071644
12 | 0.97699 | -0.16076 | 0.007475 | 0.0018734
13 | 0.97531 | -0.17279 | 0 | 0
14 | 0.97318 | -0.18801 | 0.0042917 | 0.0010756
15 | 0.97526 | -0.17316 | 0.00204 | 0.00051127
16 | 0.97433 | -0.17982 | 0.0051332 | 0.0012865
17 | 0.97199 | -0.19658 | 0.0036214 | 0.00090761
18 | 0.97368 | -0.18443 | 0.0013967 | 0.00035004
19 | 0.97172 | -0.19856 | 0 | 0
20 | 0.97026 | -0.20907 | 0.032834 | 0.0082289
21 | 0.971 | -0.20368 | 0 | 0
22 | 0.97077 | -0.20541 | 0.0050434 | 0.001264
23 | 0.97083 | -0.20497 | 0.0035889 | 0.00089945
24 | 0.97068 | -0.20606 | 0.0012306 | 0.00030841
25 | 0.97171 | -0.19858 | 0 | 0
26 | 0.97053 | -0.20714 | 0.0015232 | 0.00038176
27 | 0.9712 | -0.20229 | 0.0029082 | 0.00072886
28 | 0.97044 | -0.20775 | 0.0038848 | 0.00097363
29 | 0.97097 | -0.20393 | 0.0070585 | 0.001769
30 | 0.97025 | -0.20912 | 0.002685 | 0.00067293
31 | 0.97032 | -0.20862 | 0.0064992 | 0.0016289
32 | 0.97089 | -0.20453 | 0.0020778 | 0.00052075
33 | 0.99161 | -0.057904 | 0 | 0
34 | 0.99598 | -0.027654 | 0.0069337 | 0.0017378
35 | 0.98378 | -0.11261 | 0.0099276 | 0.0024881
36 | 0.99676 | -0.02227 | 0.0027204 | 0.0006818
37 | 0.9806 | -0.1351 | 0 | 0
38 | 0.9972 | -0.019284 | 0.0025722 | 0.00064464
39 | 0.99727 | -0.018808 | 0.0023596 | 0.00059138
40 | 0.99735 | -0.018267 | 0 | 0
41 | 0.9988 | -0.0082778 | 0.0027255 | 0.00068307
42 | 0.99962 | -0.0025831 | 0 | 0
43 | 0.99955 | -0.0030807 | 0.0022621 | 0.00056694
44 | 1 | 0 | -0.23573 | -0.059539
45 | 0.97407 | -0.1816 | 0 | 0
46 | 0.97309 | -0.18861 | 0.0068412 | 0.0017146
47 | 0.97329 | -0.1872 | 0.0073618 | 0.001845
48 | 0.97114 | -0.20267 | 0.0072095 | 0.0018069
49 | 0.99539 | -0.031636 | 0.0039246 | 0.0009836
50 | 0.99291 | -0.04881 | 0.0016936 | 0.00042446
51 | 0.99949 | -0.0034898 | 0.0022725 | 0.00056955
52 | 0.97081 | -0.20501 | 0.0059884 | 0.0015008
53 | 0.97018 | -0.20958 | 0.0096404 | 0.0024161
54 | 0.97017 | -0.20964 | 0.0030739 | 0.0007704
55 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0082393 | -0.002065 | 0.0082408 | 0.0020653 | 1.4766e-06 | 3.7558e-07 | 0.012481 | 0.012481 | 0.012481 | 0.98231 | -0.12302 | 0.98249 | -0.12172 | 4.6226
1 | 0.12521 | 0.031525 | -0.12503 | -0.031455 | 0.00018358 | 7.0194e-05 | 0.18969 | 0.18969 | 0.18969 | 0.98249 | -0.12172 | 0.98101 | -0.13223 | 35.1271
2 | -0.13574 | -0.034163 | 0.13613 | 0.034315 | 0.000396 | 0.00015154 | 0.20563 | 0.20563 | 0.20563 | 0.98249 | -0.12172 | 0.98545 | -0.10089 | 38.0796
3 | 0.11723 | 0.0295 | -0.11717 | -0.029478 | 5.8731e-05 | 2.2439e-05 | 0.17786 | 0.17786 | 0.17786 | 0.98101 | -0.13223 | 0.9805 | -0.13582 | 32.9365
4 | -0.13613 | -0.034315 | 0.13633 | 0.034388 | 0.00019207 | 7.35e-05 | 0.20563 | 0.20563 | 0.20563 | 0.98545 | -0.10089 | 0.98688 | -0.090827 | 38.0795
5 | 0.11051 | 0.027808 | -0.11035 | -0.027748 | 0.00015652 | 5.9752e-05 | 0.16774 | 0.16774 | 0.16774 | 0.9805 | -0.13582 | 0.97907 | -0.14599 | 31.0639
6 | -0.1526 | -0.038466 | 0.15325 | 0.038716 | 0.00065105 | 0.00024939 | 0.23016 | 0.23016 | 0.23016 | 0.98688 | -0.090827 | 0.99123 | -0.060497 | 42.6229
7 | -0.009262 | -0.0023213 | 0.0092652 | 0.0023222 | 3.1573e-06 | 8.979e-07 | 0.01413 | 0.014129 | 0.01413 | 0.97541 | -0.1721 | 0.97575 | -0.16964 | 5.2332
8 | 0.045265 | 0.011367 | -0.045245 | -0.011359 | 1.985e-05 | 7.3015e-06 | 0.069037 | 0.069037 | 0.069037 | 0.97575 | -0.16964 | 0.97531 | -0.17279 | 12.7847
9 | 0.040951 | 0.01029 | -0.040847 | -0.01025 | 0.00010445 | 3.9638e-05 | 0.06246 | 0.06246 | 0.06246 | 0.97575 | -0.16964 | 0.97318 | -0.18801 | 23.1335
10 | -0.095482 | -0.023978 | 0.0956 | 0.024023 | 0.0001179 | 4.4902e-05 | 0.14563 | 0.14563 | 0.14563 | 0.97575 | -0.16964 | 0.97699 | -0.16076 | 26.9679
11 | 0.1086 | 0.02731 | -0.10856 | -0.027292 | 4.67e-05 | 1.7823e-05 | 0.16509 | 0.16509 | 0.16509 | 0.97907 | -0.14599 | 0.97863 | -0.14907 | 30.5723
12 | -0.15471 | -0.039083 | 0.15497 | 0.03918 | 0.00025475 | 9.7589e-05 | 0.23236 | 0.23236 | 0.23236 | 0.99123 | -0.060497 | 0.99291 | -0.04881 | 43.03
13 | 0.1061 | 0.026677 | -0.1061 | -0.026677 | 1.2441e-07 | 4.7466e-08 | 0.16136 | 0.16136 | 0.16136 | 0.97863 | -0.14907 | 0.97863 | -0.14908 | 29.8811
14 | 0.10324 | 0.025961 | -0.10307 | -0.025897 | 0.00016779 | 6.3986e-05 | 0.15701 | 0.15701 | 0.15701 | 0.97863 | -0.14908 | 0.97699 | -0.16076 | 29.0762
15 | 0.0020401 | 0.0005111 | -0.00204 | -0.00051127 | 1.0255e-07 | -1.7225e-07 | 0.0031125 | 0.0031126 | 0.0031126 | 0.97531 | -0.17279 | 0.97526 | -0.17316 | 1.1528
16 | 0.043205 | 0.010848 | -0.043163 | -0.010833 | 4.2149e-05 | 1.5436e-05 | 0.065925 | 0.065925 | 0.065925 | 0.97531 | -0.17279 | 0.97433 | -0.17982 | 12.2083
17 | 0.036555 | 0.0091743 | -0.036512 | -0.0091579 | 4.3435e-05 | 1.6429e-05 | 0.055898 | 0.055899 | 0.055899 | 0.97318 | -0.18801 | 0.97199 | -0.19658 | 20.7031
18 | 0.03803 | 0.0095463 | -0.038005 | -0.0095371 | 2.4327e-05 | 9.2127e-06 | 0.058086 | 0.058086 | 0.058086 | 0.97433 | -0.17982 | 0.97368 | -0.18443 | 21.5132
19 | 0.03289 | 0.0082503 | -0.032881 | -0.0082469 | 9.0136e-06 | 3.3962e-06 | 0.050355 | 0.050355 | 0.050355 | 0.97199 | -0.19658 | 0.97172 | -0.19856 | 18.6498
20 | 0.036609 | 0.009187 | -0.036537 | -0.0091599 | 7.1778e-05 | 2.7151e-05 | 0.055951 | 0.055951 | 0.055951 | 0.97368 | -0.18443 | 0.97171 | -0.19858 | 20.7227
21 | 0.032881 | 0.0082469 | -0.032858 | -0.0082381 | 2.3341e-05 | 8.7946e-06 | 0.050355 | 0.050355 | 0.050355 | 0.97172 | -0.19856 | 0.971 | -0.20368 | 18.6499
22 | -0.032834 | -0.0082289 | 0.032858 | 0.0082381 | 2.4514e-05 | 9.237e-06 | 0.050355 | 0.050355 | 0.050355 | 0.97026 | -0.20907 | 0.971 | -0.20368 | 18.6499
23 | -0.011684 | -0.0029279 | 0.011684 | 0.0029282 | 7.0889e-07 | 2.2885e-07 | 0.017909 | 0.017909 | 0.017909 | 0.97077 | -0.20541 | 0.97083 | -0.20497 | 6.633
24 | 0.0066404 | 0.0016639 | -0.0066398 | -0.0016638 | 5.9572e-07 | 1.1521e-07 | 0.010178 | 0.010178 | 0.010178 | 0.97077 | -0.20541 | 0.97068 | -0.20606 | 3.7698
25 | -0.015273 | -0.0038276 | 0.015287 | 0.0038323 | 1.3524e-05 | 4.7122e-06 | 0.02341 | 0.02341 | 0.02341 | 0.97083 | -0.20497 | 0.97171 | -0.19858 | 8.6703
26 | 0.0054092 | 0.0013554 | -0.0054084 | -0.0013553 | 8.0462e-07 | 7.7692e-08 | 0.0082921 | 0.0082921 | 0.0082921 | 0.97068 | -0.20606 | 0.97053 | -0.20714 | 3.0712
27 | 0.02125 | 0.0053275 | -0.021239 | -0.0053236 | 1.09e-05 | 3.988e-06 | 0.032542 | 0.032542 | 0.032542 | 0.97171 | -0.19858 | 0.9712 | -0.20229 | 12.0525
28 | 0.0038852 | 0.00097358 | -0.0038848 | -0.00097363 | 3.3235e-07 | -5.7646e-08 | 0.0059567 | 0.0059568 | 0.0059568 | 0.97053 | -0.20714 | 0.97044 | -0.20775 | 2.2062
29 | 0.018331 | 0.0045947 | -0.018327 | -0.0045932 | 4.1773e-06 | 1.5017e-06 | 0.028086 | 0.028086 | 0.028086 | 0.9712 | -0.20229 | 0.97097 | -0.20393 | 10.4022
30 | 0.011268 | 0.0028242 | -0.011267 | -0.0028239 | 9.2872e-07 | 2.9547e-07 | 0.017269 | 0.017269 | 0.017269 | 0.97097 | -0.20393 | 0.97089 | -0.20453 | 6.3959
31 | -0.002685 | -0.00067293 | 0.0026852 | 0.00067278 | 1.8595e-07 | -1.4555e-07 | 0.0041179 | 0.0041178 | 0.0041179 | 0.97025 | -0.20912 | 0.97032 | -0.20862 | 1.5251
32 | -0.0091844 | -0.0023016 | 0.0091896 | 0.0023031 | 5.2051e-06 | 1.4822e-06 | 0.014085 | 0.014084 | 0.014085 | 0.97032 | -0.20862 | 0.97089 | -0.20453 | 5.2165
33 | -0.050923 | -0.012875 | 0.051141 | 0.012958 | 0.00021799 | 8.3067e-05 | 0.076456 | 0.076456 | 0.076456 | 0.99161 | -0.057904 | 0.99598 | -0.027654 | 28.317
34 | 0.050923 | 0.012875 | -0.050534 | -0.012726 | 0.00038946 | 0.00014843 | 0.076456 | 0.076456 | 0.076456 | 0.99161 | -0.057904 | 0.98378 | -0.11261 | 28.3172
35 | -0.058075 | -0.014696 | 0.058119 | 0.014712 | 4.4171e-05 | 1.6867e-05 | 0.086815 | 0.086815 | 0.086815 | 0.99598 | -0.027654 | 0.99676 | -0.02227 | 32.1536
36 | 0.040606 | 0.010238 | -0.040479 | -0.01019 | 0.00012753 | 4.8365e-05 | 0.061441 | 0.061441 | 0.061441 | 0.98378 | -0.11261 | 0.9806 | -0.1351 | 22.7558
37 | -0.06084 | -0.015394 | 0.060874 | 0.015407 | 3.4391e-05 | 1.2879e-05 | 0.090876 | 0.090876 | 0.090876 | 0.99676 | -0.02227 | 0.99735 | -0.018267 | 16.8289
38 | 0.040479 | 0.01019 | -0.040217 | -0.010091 | 0.00026118 | 9.9063e-05 | 0.061441 | 0.061441 | 0.061441 | 0.9806 | -0.1351 | 0.97407 | -0.1816 | 22.756
39 | -0.0025722 | -0.00064464 | 0.0025723 | 0.00064447 | 1.6958e-07 | -1.7547e-07 | 0.0038382 | 0.0038381 | 0.0038382 | 0.9972 | -0.019284 | 0.99727 | -0.018808 | 1.4215
40 | -0.004932 | -0.0012359 | 0.0049323 | 0.0012358 | 3.6942e-07 | -5.693e-10 | 0.0073589 | 0.0073588 | 0.0073589 | 0.99727 | -0.018808 | 0.99735 | -0.018267 | 2.7255
41 | -0.065806 | -0.016643 | 0.065899 | 0.016678 | 9.281e-05 | 3.489e-05 | 0.098234 | 0.098234 | 0.098234 | 0.99735 | -0.018267 | 0.9988 | -0.0082778 | 18.1916
42 | -0.068625 | -0.017361 | 0.06868 | 0.017382 | 5.5177e-05 | 2.0779e-05 | 0.10229 | 0.10229 | 0.10229 | 0.9988 | -0.0082778 | 0.99962 | -0.0025831 | 18.9434
43 | 0.0045351 | 0.0011363 | -0.0045348 | -0.0011363 | 3.1227e-07 | -2.3841e-08 | 0.0067507 | 0.0067508 | 0.0067508 | 0.99962 | -0.0025831 | 0.99955 | -0.0030807 | 2.5003
44 | -0.073215 | -0.018518 | 0.073241 | 0.018528 | 2.6678e-05 | 1.0072e-05 | 0.10905 | 0.10905 | 0.10905 | 0.99962 | -0.0025831 | 1 | 0 | 20.1935
45 | 0.0022727 | 0.00056937 | -0.0022725 | -0.00056955 | 1.2866e-07 | -1.8662e-07 | 0.0033832 | 0.0033833 | 0.0033833 | 0.99955 | -0.0030807 | 0.99949 | -0.0034898 | 1.2531
46 | 0.16169 | 0.041011 | -0.16097 | -0.040734 | 0.00072217 | 0.00027671 | 0.24077 | 0.24077 | 0.24077 | 1 | 0 | 0.99539 | -0.031636 | 44.5864
47 | 0.03285 | 0.0082445 | -0.032818 | -0.0082324 | 3.1962e-05 | 1.204e-05 | 0.050187 | 0.050187 | 0.050187 | 0.97407 | -0.1816 | 0.97309 | -0.18861 | 18.5877
48 | 0.0073675 | 0.0018463 | -0.0073618 | -0.001845 | 5.7178e-06 | 1.2994e-06 | 0.011255 | 0.011255 | 0.011255 | 0.97407 | -0.1816 | 0.97329 | -0.1872 | 4.1685
49 | 0.025977 | 0.0065179 | -0.025926 | -0.006499 | 5.0592e-05 | 1.8822e-05 | 0.039725 | 0.039726 | 0.039726 | 0.97309 | -0.18861 | 0.97114 | -0.20267 | 14.7132
50 | 0.018717 | 0.0046922 | -0.018711 | -0.00469 | 6.0641e-06 | 2.1862e-06 | 0.028679 | 0.028679 | 0.028679 | 0.97114 | -0.20267 | 0.97081 | -0.20501 | 10.6219
51 | 0.15704 | 0.03975 | -0.15666 | -0.039605 | 0.00037997 | 0.00014557 | 0.2349 | 0.2349 | 0.2349 | 0.99539 | -0.031636 | 0.99291 | -0.04881 | 43.5
52 | 0.012722 | 0.0031892 | -0.012714 | -0.0031865 | 8.0443e-06 | 2.6751e-06 | 0.0195 | 0.019501 | 0.019501 | 0.97081 | -0.20501 | 0.97018 | -0.20958 | 7.2224
53 | 0.0030739 | 0.00077038 | -0.0030739 | -0.0007704 | 2.3661e-08 | -1.1965e-08 | 0.0047146 | 0.0047147 | 0.0047147 | 0.97018 | -0.20958 | 0.97017 | -0.20964 | 1.7462

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24007 | 0.060626

## res_load
| p_mw | q_mvar
0 | 0.0082393 | 0.002065
1 | 0.0022864 | 0.00057302
2 | 0.0077986 | 0.0019545
3 | 0.0066634 | 0.00167
4 | 0.016272 | 0.0040781
5 | 0.009262 | 0.0023213
6 | 0.0017466 | 0.00043773
7 | 0.0014646 | 0.00036706
8 | 0.0024549 | 0.00061525
9 | 0.0028586 | 0.00071644
10 | 0.007475 | 0.0018734
11 | 0.0042917 | 0.0010756
12 | 0.00204 | 0.00051127
13 | 0.0051332 | 0.0012865
14 | 0.0036214 | 0.00090761
15 | 0.0013967 | 0.00035004
16 | 0.032834 | 0.0082289
17 | 0.0050434 | 0.001264
18 | 0.0035889 | 0.00089945
19 | 0.0012306 | 0.00030841
20 | 0.0015232 | 0.00038176
21 | 0.0029082 | 0.00072886
22 | 0.0038848 | 0.00097363
23 | 0.0070585 | 0.001769
24 | 0.002685 | 0.00067293
25 | 0.0064992 | 0.0016289
26 | 0.0020778 | 0.00052075
27 | 0.0069337 | 0.0017378
28 | 0.0099276 | 0.0024881
29 | 0.0027204 | 0.0006818
30 | 0.0025722 | 0.00064464
31 | 0.0023596 | 0.00059138
32 | 0.0027255 | 0.00068307
33 | 0.0022621 | 0.00056694
34 | 0.0043366 | 0.0010869
35 | 0.0068412 | 0.0017146
36 | 0.0073618 | 0.001845
37 | 0.0072095 | 0.0018069
38 | 0.0039246 | 0.0009836
39 | 0.0016936 | 0.00042446
40 | 0.0022725 | 0.00056955
41 | 0.0059884 | 0.0015008
42 | 0.0096404 | 0.0024161
43 | 0.0030739 | 0.0007704

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1