## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1125-19_1_3_node_13 | 0.4 | n |  | TRUE
1 | bus_LV_1125-19_1_3_node_14 | 0.4 | n |  | TRUE
2 | bus_LV_1125-19_1_3_node_21 | 0.4 | n |  | TRUE
3 | bus_LV_1125-19_1_3_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_1125-19_1_3_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1125-19_1_3_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_1125-19_1_3_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_1125-19_1_3_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_1125-19_1_3_node_23 | 0.4 | n |  | TRUE
9 | bus_LV_1125-19_1_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_1125-19_1_3_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1125-19_1_3_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_1125-19_1_3_node_44 | 0.4 | n |  | TRUE
13 | bus_LV_1125-19_1_3_node_41 | 0.4 | n |  | TRUE
14 | bus_LV_1125-19_1_3_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_1125-19_1_3_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_1125-19_1_3_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_1125-19_1_3_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_1125-19_1_3_node_71 | 0.4 | n |  | TRUE
19 | bus_LV_1125-19_1_3_node_42 | 0.4 | n |  | TRUE
20 | bus_LV_1125-19_1_3_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1125-19_1_3_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_1125-19_1_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_1125-19_1_3_node_53 | 0.4 | n |  | TRUE
24 | bus_LV_1125-19_1_3_node_28 | 0.4 | n |  | TRUE
25 | bus_LV_1125-19_1_3_node_43 | 0.4 | n |  | TRUE
26 | bus_LV_1125-19_1_3_node_66 | 0.4 | n |  | TRUE
27 | bus_LV_1125-19_1_3_node_73 | 0.4 | n |  | TRUE
28 | bus_LV_1125-19_1_3_node_56 | 0.4 | n |  | TRUE
29 | bus_LV_1125-19_1_3_node_67 | 0.4 | n |  | TRUE
30 | bus_LV_1125-19_1_3_node_55 | 0.4 | n |  | TRUE
31 | bus_LV_1125-19_1_3_node_54 | 0.4 | n |  | TRUE
32 | bus_LV_1125-19_1_3_node_57 | 0.4 | n |  | TRUE
33 | bus_MV_130_0_node_161 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1125-19_1_3_load_13 | 0 | 0.0082961 | 0.0020792 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1125-19_1_3_load_14 | 1 | 0.0024937 | 0.00062499 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1125-19_1_3_load_21 | 2 | 0.001619 | 0.00040576 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1125-19_1_3_load_5 | 3 | 0.00036014 | 9.026e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1125-19_1_3_load_23 | 8 | 7.5955e-05 | 1.9036e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1125-19_1_3_load_17 | 11 | 0.0014668 | 0.00036761 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1125-19_1_3_load_41 | 13 | 0.0041576 | 0.001042 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1125-19_1_3_load_18 | 14 | 0.0016225 | 0.00040664 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1125-19_1_3_load_25 | 17 | 0.0054174 | 0.0013577 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1125-19_1_3_load_71 | 18 | 0.012847 | 0.0032196 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1125-19_1_3_load_15 | 20 | 0.0013683 | 0.00034293 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1125-19_1_3_load_22 | 21 | 0.0065327 | 0.0016372 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1125-19_1_3_load_19 | 22 | 0.001693 | 0.00042431 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1125-19_1_3_load_53 | 23 | 0.0042034 | 0.0010535 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1125-19_1_3_load_66 | 26 | 0.015514 | 0.0038883 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1125-19_1_3_load_73 | 27 | 0.016059 | 0.0040248 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1125-19_1_3_load_67 | 29 | 0.018938 | 0.0047463 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1125-19_1_3_load_54 | 31 | 0.016166 | 0.0040515 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1125-19_1_3_load_57 | 32 | 0.018436 | 0.0046204 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1125-19_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.010302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1125-19_1_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.054416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1125-19_1_3_line_2 | NAYY 4x150 SE | 1 | 20 | 0.01583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1125-19_1_3_line_3 | NAYY 4x150 SE | 2 | 7 | 0.023885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1125-19_1_3_line_4 | NAYY 4x150 SE | 3 | 4 | 0.013516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1125-19_1_3_line_5 | NAYY 4x150 SE | 3 | 5 | 0.086437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1125-19_1_3_line_6 | NAYY 4x150 SE | 4 | 6 | 0.005078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1125-19_1_3_line_7 | NAYY 4x150 SE | 5 | 7 | 0.03301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1125-19_1_3_line_8 | NAYY 4x150 SE | 6 | 8 | 0.10295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1125-19_1_3_line_9 | NAYY 4x150 SE | 7 | 9 | 0.039622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1125-19_1_3_line_10 | NAYY 4x150 SE | 7 | 10 | 0.033896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1125-19_1_3_line_11 | NAYY 4x150 SE | 9 | 12 | 0.019069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1125-19_1_3_line_12 | NAYY 4x150 SE | 9 | 13 | 0.023311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1125-19_1_3_line_13 | NAYY 4x150 SE | 10 | 11 | 0.0025607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1125-19_1_3_line_14 | NAYY 4x150 SE | 11 | 14 | 0.028039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1125-19_1_3_line_15 | NAYY 4x150 SE | 12 | 18 | 0.03664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1125-19_1_3_line_16 | NAYY 4x150 SE | 13 | 19 | 0.013403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_1125-19_1_3_line_17 | NAYY 4x150 SE | 14 | 22 | 0.020357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1125-19_1_3_line_18 | NAYY 4x150 SE | 15 | 16 | 0.036312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1125-19_1_3_line_19 | NAYY 4x150 SE | 15 | 17 | 0.016765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1125-19_1_3_line_20 | NAYY 4x150 SE | 16 | 19 | 0.025544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1125-19_1_3_line_21 | NAYY 4x150 SE | 16 | 23 | 0.0069997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1125-19_1_3_line_22 | NAYY 4x150 SE | 18 | 28 | 0.012158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1125-19_1_3_line_23 | NAYY 4x150 SE | 20 | 21 | 0.040502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1125-19_1_3_line_24 | NAYY 4x150 SE | 24 | 25 | 0.031801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1125-19_1_3_line_25 | NAYY 4x150 SE | 24 | 26 | 0.01851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1125-19_1_3_line_26 | NAYY 4x150 SE | 25 | 27 | 0.01859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1125-19_1_3_line_27 | NAYY 4x150 SE | 25 | 28 | 0.018947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1125-19_1_3_line_28 | NAYY 4x150 SE | 26 | 29 | 0.011796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1125-19_1_3_line_29 | NAYY 4x150 SE | 28 | 30 | 0.027083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1125-19_1_3_line_30 | NAYY 4x150 SE | 30 | 32 | 0.025199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1125-19_1_3_line_31 | NAYY 4x150 SE | 30 | 31 | 0.022921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1125-19_1_3_trafo_42 | 0.25 MVA 20/0.4 kV | 33 | 19 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2642186.3509 | 1228968.0724 | 2642186.3509 | 1228968.0724 | 2642193.0135 | 1228960.2146
1 | 2642206.1638 | 1229018.7536 | 2642186.3509 | 1228968.0724
2 | 2642203.2511 | 1228948.1405 | 2642193.0135 | 1228960.2146
3 | 2642208.8087 | 1229042.4886 | 2642206.9948 | 1229027.989 | 2642206.1638 | 1229018.7536
4 | 2642334.5501 | 1229026.0157 | 2642321.4389 | 1229029.2977
5 | 2642237.2793 | 1229048.85 | 2642248.0187 | 1229047.1807 | 2642267.8654 | 1229042.163 | 2642304.8373 | 1229033.4535 | 2642321.4389 | 1229029.2977
6 | 2642332.1044 | 1229021.5622 | 2642334.5501 | 1229026.0157
7 | 2642208.8087 | 1229042.4886 | 2642214.6262 | 1229042.6077 | 2642227.6039 | 1229042.5886 | 2642235.5116 | 1229042.8004 | 2642237.2793 | 1229048.85
8 | 2642332.1044 | 1229021.5622 | 2642353.0515 | 1229016.308 | 2642431.9511 | 1228996.4884
9 | 2642208.8087 | 1229042.4886 | 2642204.2937 | 1229042.4566 | 2642204.8796 | 1229047.4305 | 2642218.2035 | 1229074.4194
10 | 2642174.9182 | 1229041.8925 | 2642204.2937 | 1229042.4566 | 2642208.8087 | 1229042.4886
11 | 2642218.2035 | 1229074.4194 | 2642220.6224 | 1229078.3834 | 2642230.7083 | 1229088.728
12 | 2642218.2035 | 1229074.4194 | 2642198.6931 | 1229087.1769
13 | 2642174.9182 | 1229041.8925 | 2642172.3577 | 1229041.8584
14 | 2642144.3255 | 1229042.0426 | 2642144.3255 | 1229042.0426 | 2642157.0785 | 1229041.6549 | 2642172.3577 | 1229041.8584
15 | 2642230.7083 | 1229088.728 | 2642225.4227 | 1229093.7269 | 2642209.2031 | 1229118.2059
16 | 2642188.4549 | 1229095.5215 | 2642190.5673 | 1229092.4902 | 2642198.6931 | 1229087.1769
17 | 2642124.0533 | 1229043.7858 | 2642131.8956 | 1229042.7995 | 2642144.3255 | 1229042.0426
18 | 2642139.8629 | 1229076.3211 | 2642151.9551 | 1229080.4425 | 2642153.1418 | 1229085.1094 | 2642170.2639 | 1229077.5371
19 | 2642139.8629 | 1229076.3211 | 2642124.9075 | 1229083.8977
20 | 2642188.4549 | 1229095.5215 | 2642170.2639 | 1229077.5371
21 | 2642170.2639 | 1229077.5371 | 2642173.1869 | 1229071.1769
22 | 2642202.4874 | 1229128.3412 | 2642209.2031 | 1229118.2059
23 | 2642242.9763 | 1228956.0331 | 2642203.2511 | 1228948.1405
24 | 2642161.8821 | 1229107.8742 | 2642174.2561 | 1229116.0558 | 2642183.5799 | 1229130.2306
25 | 2642161.8821 | 1229107.8742 | 2642144.6493 | 1229114.6309
26 | 2642167.7901 | 1229140.1138 | 2642183.5799 | 1229130.2306
27 | 2642202.4874 | 1229128.3412 | 2642183.5799 | 1229130.2306
28 | 2642133.6671 | 1229118.9369 | 2642144.6493 | 1229114.6309
29 | 2642216.87 | 1229151.313 | 2642202.4874 | 1229128.3412
30 | 2642216.87 | 1229151.313 | 2642238.1204 | 1229137.7694
31 | 2642216.87 | 1229151.313 | 2642197.5392 | 1229163.6297

## bus_geodata
| x | y | coords
0 | 2642186.3509 | 1228968.0724
1 | 2642193.0135 | 1228960.2146
2 | 2642206.1638 | 1229018.7535
3 | 2642321.4389 | 1229029.2977
4 | 2642334.5501 | 1229026.0157
5 | 2642237.2793 | 1229048.85
6 | 2642332.1044 | 1229021.5622
7 | 2642208.8087 | 1229042.4886
8 | 2642431.9511 | 1228996.4884
9 | 2642218.2035 | 1229074.4194
10 | 2642174.9182 | 1229041.8925
11 | 2642172.3577 | 1229041.8584
12 | 2642230.7083 | 1229088.728
13 | 2642198.6931 | 1229087.1769
14 | 2642144.3255 | 1229042.0426
15 | 2642139.8629 | 1229076.3211
16 | 2642170.2639 | 1229077.5371
17 | 2642124.9075 | 1229083.8977
18 | 2642209.2031 | 1229118.2059
19 | 2642188.4549 | 1229095.5215
20 | 2642203.2511 | 1228948.1405
21 | 2642242.9763 | 1228956.0331
22 | 2642124.0533 | 1229043.7858
23 | 2642173.1869 | 1229071.1769
24 | 2642161.8821 | 1229107.8742
25 | 2642183.5799 | 1229130.2306
26 | 2642144.6493 | 1229114.6309
27 | 2642167.7901 | 1229140.1138
28 | 2642202.4874 | 1229128.3412
29 | 2642133.6671 | 1229118.9369
30 | 2642216.87 | 1229151.313
31 | 2642197.5392 | 1229163.6297
32 | 2642238.1204 | 1229137.7694
33 | 2642174.2561 | 1229116.0558

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99308 | -0.048366 | 0.0082961 | 0.0020792
1 | 0.99292 | -0.04945 | 0.0024937 | 0.00062499
2 | 0.99454 | -0.038083 | 0.001619 | 0.00040576
3 | 0.99516 | -0.033735 | 0.00036014 | 9.026e-05
4 | 0.99516 | -0.033747 | 0 | 0
5 | 0.99521 | -0.033341 | 0 | 0
6 | 0.99516 | -0.033751 | 0 | 0
7 | 0.99523 | -0.033189 | 0 | 0
8 | 0.99515 | -0.033835 | 7.5955e-05 | 1.9036e-05
9 | 0.99669 | -0.022993 | 0 | 0
10 | 0.995 | -0.034825 | 0 | 0
11 | 0.99498 | -0.034948 | 0.0014668 | 0.00036761
12 | 0.99398 | -0.041815 | 0 | 0
13 | 0.99876 | -0.0085534 | 0.0041576 | 0.001042
14 | 0.99485 | -0.035886 | 0.0016225 | 0.00040664
15 | 0.99937 | -0.0044219 | 0 | 0
16 | 0.99965 | -0.0024554 | 0 | 0
17 | 0.99924 | -0.0053297 | 0.0054174 | 0.0013577
18 | 0.98879 | -0.07827 | 0.012847 | 0.0032196
19 | 1 | 0 | -0.13968 | -0.035012
20 | 0.99274 | -0.050718 | 0.0013683 | 0.00034293
21 | 0.99236 | -0.053399 | 0.0065327 | 0.0016372
22 | 0.9948 | -0.036234 | 0.001693 | 0.00042431
23 | 0.99961 | -0.0027493 | 0.0042034 | 0.0010535
24 | 0.98432 | -0.10993 | 0 | 0
25 | 0.9859 | -0.098666 | 0 | 0
26 | 0.98339 | -0.11651 | 0.015514 | 0.0038883
27 | 0.98547 | -0.10173 | 0.016059 | 0.0040248
28 | 0.98729 | -0.088851 | 0 | 0
29 | 0.98307 | -0.11882 | 0.018938 | 0.0047463
30 | 0.98593 | -0.098461 | 0 | 0
31 | 0.9854 | -0.10227 | 0.016166 | 0.0040515
32 | 0.98526 | -0.10323 | 0.018436 | 0.0046204
33 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0104 | 0.0026064 | -0.010399 | -0.0026059 | 1.5611e-06 | 4.6716e-07 | 0.015583 | 0.015583 | 0.015583 | 0.99308 | -0.048366 | 0.99292 | -0.04945 | 5.7716
1 | -0.018696 | -0.0046856 | 0.018723 | 0.0046951 | 2.6648e-05 | 9.5442e-06 | 0.028014 | 0.028014 | 0.028014 | 0.99308 | -0.048366 | 0.99454 | -0.038083 | 10.3756
2 | 0.0079048 | 0.0019809 | -0.0079034 | -0.0019806 | 1.3862e-06 | 3.2845e-07 | 0.011846 | 0.011846 | 0.011846 | 0.99292 | -0.04945 | 0.99274 | -0.050718 | 4.3875
3 | -0.020342 | -0.0051009 | 0.020356 | 0.0051059 | 1.3807e-05 | 5.0002e-06 | 0.030436 | 0.030436 | 0.030436 | 0.99454 | -0.038083 | 0.99523 | -0.033189 | 11.2727
4 | 7.5956e-05 | 1.7457e-05 | -7.5956e-05 | -1.7633e-05 | 1.0782e-10 | -1.7556e-07 | 0.00011304 | 0.0001131 | 0.0001131 | 0.99516 | -0.033735 | 0.99516 | -0.033747 | 0.041887
5 | -0.0004361 | -0.00010772 | 0.00043612 | 0.0001066 | 2.2881e-08 | -1.1143e-06 | 0.00065152 | 0.00065113 | 0.00065152 | 0.99516 | -0.033735 | 0.99521 | -0.033341 | 0.2413
6 | 7.5956e-05 | 1.7633e-05 | -7.5956e-05 | -1.7699e-05 | 4.051e-11 | -6.5961e-08 | 0.0001131 | 0.00011312 | 0.00011312 | 0.99516 | -0.033747 | 0.99516 | -0.033751 | 0.041895
7 | -0.00043612 | -0.0001066 | 0.00043613 | 0.00010618 | 8.731e-09 | -4.2558e-07 | 0.00065113 | 0.00065099 | 0.00065113 | 0.99521 | -0.033341 | 0.99523 | -0.033189 | 0.24116
8 | 7.5956e-05 | 1.7699e-05 | -7.5955e-05 | -1.9036e-05 | 8.2523e-10 | -1.3372e-06 | 0.00011312 | 0.00011357 | 0.00011357 | 0.99516 | -0.033751 | 0.99515 | -0.033835 | 0.042064
9 | -0.025576 | -0.0064102 | 0.025612 | 0.0064235 | 3.6153e-05 | 1.3389e-05 | 0.03824 | 0.038239 | 0.03824 | 0.99523 | -0.033189 | 0.99669 | -0.022993 | 14.1628
10 | 0.0047839 | 0.0011981 | -0.0047829 | -0.0011981 | 1.082e-06 | -2.4192e-08 | 0.0071524 | 0.0071525 | 0.0071525 | 0.99523 | -0.033189 | 0.995 | -0.034825 | 2.6491
11 | 0.09908 | 0.024979 | -0.09882 | -0.024879 | 0.00026055 | 9.9964e-05 | 0.14798 | 0.14798 | 0.14798 | 0.99669 | -0.022993 | 0.99398 | -0.041815 | 54.8058
12 | -0.12469 | -0.031403 | 0.12494 | 0.031499 | 0.0002522 | 9.6392e-05 | 0.18621 | 0.18621 | 0.18621 | 0.99669 | -0.022993 | 0.99876 | -0.0085534 | 34.4842
13 | 0.0047829 | 0.0011981 | -0.0047828 | -0.0011981 | 8.1746e-08 | -1.8185e-09 | 0.0071525 | 0.0071525 | 0.0071525 | 0.995 | -0.034825 | 0.99498 | -0.034948 | 2.6491
14 | 0.003316 | 0.00083051 | -0.0033156 | -0.00083071 | 4.3027e-07 | -1.9864e-07 | 0.004959 | 0.0049591 | 0.0049591 | 0.99498 | -0.034948 | 0.99485 | -0.035886 | 1.8367
15 | 0.09882 | 0.024879 | -0.098319 | -0.024687 | 0.00050063 | 0.00019208 | 0.14798 | 0.14798 | 0.14798 | 0.99398 | -0.041815 | 0.98879 | -0.07827 | 54.8058
16 | -0.1291 | -0.032541 | 0.12926 | 0.0326 | 0.00015482 | 5.9194e-05 | 0.19241 | 0.19241 | 0.19241 | 0.99876 | -0.0085534 | 1 | 0 | 35.6312
17 | 0.0016931 | 0.00042407 | -0.001693 | -0.00042431 | 8.1459e-08 | -2.3298e-07 | 0.0025323 | 0.0025324 | 0.0025324 | 0.99485 | -0.035886 | 0.9948 | -0.036234 | 0.93792
18 | -0.0054181 | -0.0013578 | 0.0054195 | 0.0013579 | 1.4746e-06 | 9.1234e-08 | 0.0080672 | 0.008067 | 0.0080672 | 0.99937 | -0.0044219 | 0.99965 | -0.0024554 | 2.9879
19 | 0.0054181 | 0.0013578 | -0.0054174 | -0.0013577 | 6.8084e-07 | 4.222e-08 | 0.0080672 | 0.0080673 | 0.0080673 | 0.99937 | -0.0044219 | 0.99924 | -0.0053297 | 2.9879
20 | -0.0096231 | -0.0024113 | 0.0096264 | 0.0024122 | 3.2705e-06 | 9.2288e-07 | 0.014324 | 0.014324 | 0.014324 | 0.99965 | -0.0024554 | 1 | 0 | 5.3053
21 | 0.0042036 | 0.0010534 | -0.0042034 | -0.0010535 | 1.7101e-07 | -2.599e-08 | 0.0062572 | 0.0062572 | 0.0062572 | 0.99965 | -0.0024554 | 0.99961 | -0.0027493 | 2.3175
22 | 0.085473 | 0.021467 | -0.085347 | -0.021419 | 0.00012555 | 4.8135e-05 | 0.12864 | 0.12864 | 0.12864 | 0.98879 | -0.07827 | 0.98729 | -0.088851 | 47.6456
23 | 0.0065351 | 0.0016377 | -0.0065327 | -0.0016372 | 2.425e-06 | 4.0922e-07 | 0.0097954 | 0.0097956 | 0.0097956 | 0.99274 | -0.050718 | 0.99236 | -0.053399 | 3.628
24 | -0.03449 | -0.0086486 | 0.034544 | 0.0086689 | 5.3948e-05 | 2.0344e-05 | 0.052141 | 0.052141 | 0.052141 | 0.98432 | -0.10993 | 0.9859 | -0.098666 | 19.3114
25 | 0.03449 | 0.0086486 | -0.034458 | -0.0086367 | 3.1401e-05 | 1.1842e-05 | 0.052141 | 0.052141 | 0.052141 | 0.98432 | -0.10993 | 0.98339 | -0.11651 | 19.3114
26 | 0.016066 | 0.0040272 | -0.016059 | -0.0040248 | 6.8209e-06 | 2.3865e-06 | 0.024249 | 0.024249 | 0.024249 | 0.9859 | -0.098666 | 0.98547 | -0.10173 | 8.981
27 | -0.05061 | -0.012696 | 0.050679 | 0.012722 | 6.899e-05 | 2.6293e-05 | 0.076389 | 0.076389 | 0.076389 | 0.9859 | -0.098666 | 0.98729 | -0.088851 | 28.2923
28 | 0.018944 | 0.0047485 | -0.018938 | -0.0047463 | 6.0484e-06 | 2.1767e-06 | 0.028665 | 0.028665 | 0.028665 | 0.98339 | -0.11651 | 0.98307 | -0.11882 | 10.6168
29 | 0.034668 | 0.0086967 | -0.034622 | -0.0086793 | 4.6145e-05 | 1.7402e-05 | 0.052254 | 0.052254 | 0.052254 | 0.98729 | -0.088851 | 0.98593 | -0.098461 | 19.3534
30 | 0.018448 | 0.0046248 | -0.018436 | -0.0046204 | 1.219e-05 | 4.3673e-06 | 0.027843 | 0.027843 | 0.027843 | 0.98593 | -0.098461 | 0.98526 | -0.10323 | 10.3122
31 | 0.016174 | 0.0040545 | -0.016166 | -0.0040515 | 8.5234e-06 | 2.9861e-06 | 0.024411 | 0.024412 | 0.024412 | 0.98593 | -0.098461 | 0.9854 | -0.10227 | 9.0413

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.13968 | 0.035012

## res_load
| p_mw | q_mvar
0 | 0.0082961 | 0.0020792
1 | 0.0024937 | 0.00062499
2 | 0.001619 | 0.00040576
3 | 0.00036014 | 9.026e-05
4 | 7.5955e-05 | 1.9036e-05
5 | 0.0014668 | 0.00036761
6 | 0.0041576 | 0.001042
7 | 0.0016225 | 0.00040664
8 | 0.0054174 | 0.0013577
9 | 0.012847 | 0.0032196
10 | 0.0013683 | 0.00034293
11 | 0.0065327 | 0.0016372
12 | 0.001693 | 0.00042431
13 | 0.0042034 | 0.0010535
14 | 0.015514 | 0.0038883
15 | 0.016059 | 0.0040248
16 | 0.018938 | 0.0047463
17 | 0.016166 | 0.0040515
18 | 0.018436 | 0.0046204

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1