## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1125-24_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1125-24_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1125-24_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1125-24_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1125-24_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1125-24_0_4_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_1125-24_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1125-24_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1125-24_0_4_node_26 | 0.4 | n |  | TRUE
9 | bus_LV_1125-24_0_4_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_1125-24_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1125-24_0_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_1125-24_0_4_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_1125-24_0_4_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_1125-24_0_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1125-24_0_4_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_1125-24_0_4_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_1125-24_0_4_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_1125-24_0_4_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_1125-24_0_4_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_1125-24_0_4_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_1125-24_0_4_node_28 | 0.4 | n |  | TRUE
22 | bus_LV_1125-24_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1125-24_0_4_node_29 | 0.4 | n |  | TRUE
24 | bus_LV_1125-24_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_1125-24_0_4_node_16 | 0.4 | n |  | TRUE
26 | bus_MV_130_0_node_150 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1125-24_0_4_load_0 | 0 | 0.068834 | 0.017252 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1125-24_0_4_load_1 | 1 | 0.0094938 | 0.0023794 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1125-24_0_4_load_3 | 3 | 0.0094646 | 0.0023721 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1125-24_0_4_load_4 | 4 | 0.019159 | 0.0048017 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1125-24_0_4_load_13 | 5 | 0.0077496 | 0.0019422 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1125-24_0_4_load_17 | 9 | 0.012788 | 0.003205 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1125-24_0_4_load_15 | 12 | 0.0058303 | 0.0014612 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1125-24_0_4_load_24 | 15 | 0.014663 | 0.003675 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1125-24_0_4_load_21 | 17 | 0.0059922 | 0.0015018 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1125-24_0_4_load_27 | 18 | 0.025042 | 0.0062762 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1125-24_0_4_load_19 | 19 | 0.0034581 | 0.00086668 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1125-24_0_4_load_25 | 20 | 0.0097528 | 0.0024443 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1125-24_0_4_load_28 | 21 | 0.0029335 | 0.00073519 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1125-24_0_4_load_18 | 22 | 0.0067292 | 0.0016865 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1125-24_0_4_load_29 | 23 | 0.0094398 | 0.0023658 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1125-24_0_4_load_14 | 24 | 0.0036552 | 0.00091609 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1125-24_0_4_load_16 | 25 | 0.0015632 | 0.00039178 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1125-24_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.030097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1125-24_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1125-24_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0099795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1125-24_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0080017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1125-24_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.002379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1125-24_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.021608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1125-24_0_4_line_6 | NAYY 4x150 SE | 5 | 19 | 0.0038272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1125-24_0_4_line_7 | NAYY 4x150 SE | 6 | 9 | 0.020007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1125-24_0_4_line_8 | NAYY 4x150 SE | 6 | 7 | 0.030101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1125-24_0_4_line_9 | NAYY 4x150 SE | 7 | 8 | 0.007507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1125-24_0_4_line_10 | NAYY 4x150 SE | 8 | 18 | 0.034627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1125-24_0_4_line_11 | NAYY 4x150 SE | 8 | 20 | 0.012697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1125-24_0_4_line_12 | NAYY 4x150 SE | 9 | 22 | 0.0019697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1125-24_0_4_line_13 | NAYY 4x150 SE | 10 | 11 | 0.008794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1125-24_0_4_line_14 | NAYY 4x150 SE | 10 | 12 | 0.012418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1125-24_0_4_line_15 | NAYY 4x150 SE | 11 | 13 | 0.0085019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1125-24_0_4_line_16 | NAYY 4x150 SE | 12 | 24 | 0.016944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1125-24_0_4_line_17 | NAYY 4x150 SE | 13 | 18 | 0.038852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1125-24_0_4_line_18 | NAYY 4x150 SE | 14 | 15 | 0.023929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1125-24_0_4_line_19 | NAYY 4x150 SE | 14 | 16 | 0.004344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1125-24_0_4_line_20 | NAYY 4x150 SE | 14 | 17 | 0.028258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1125-24_0_4_line_21 | NAYY 4x150 SE | 15 | 20 | 0.02316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1125-24_0_4_line_22 | NAYY 4x150 SE | 16 | 23 | 0.033031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1125-24_0_4_line_23 | NAYY 4x150 SE | 16 | 21 | 0.016767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1125-24_0_4_line_24 | NAYY 4x150 SE | 24 | 25 | 0.0074618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1125-24_0_4_trafo_6 | 0.25 MVA 20/0.4 kV | 26 | 6 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2641703.7089 | 1229227.999 | 2641698.4384 | 1229222.2807 | 2641681.5867 | 1229207.6446
1 | 2641710.2723 | 1229238.3958 | 2641707.712 | 1229234.0307 | 2641703.7089 | 1229227.999
2 | 2641681.5867 | 1229207.6446 | 2641681.5715 | 1229207.6314 | 2641673.755 | 1229201.4596
3 | 2641710.2723 | 1229238.3958 | 2641703.2904 | 1229242.3049
4 | 2641671.8879 | 1229199.9854 | 2641673.755 | 1229201.4596
5 | 2641697.7291 | 1229262.9564 | 2641699.2613 | 1229259.4428 | 2641701.6265 | 1229253.8003 | 2641703.0666 | 1229247.2174 | 2641703.2904 | 1229242.3049
6 | 2641668.8842 | 1229197.6137 | 2641671.8879 | 1229199.9854
7 | 2641697.7291 | 1229262.9564 | 2641690.0864 | 1229270.363 | 2641682.3285 | 1229275.6073
8 | 2641689.0543 | 1229282.5077 | 2641686.2684 | 1229278.9972 | 2641701.8756 | 1229267.9886 | 2641697.7291 | 1229262.9564
9 | 2641689.0543 | 1229282.5077 | 2641682.6855 | 1229286.5101
10 | 2641682.6855 | 1229286.5101 | 2641677.6711 | 1229289.6547 | 2641667.9057 | 1229296.2126 | 2641658.4415 | 1229305.1963 | 2641655.2693 | 1229307.4581
11 | 2641682.6855 | 1229286.5101 | 2641686.5009 | 1229287.971 | 2641689.3541 | 1229290.537 | 2641692.448 | 1229294.1729
12 | 2641682.3285 | 1229275.6073 | 2641680.6967 | 1229276.7104
13 | 2641609.5263 | 1229324.6329 | 2641616.4956 | 1229319.245
14 | 2641609.5263 | 1229324.6329 | 2641600.4104 | 1229316.2003
15 | 2641616.4956 | 1229319.245 | 2641619.0088 | 1229322.7647 | 2641621.4396 | 1229326.1616
16 | 2641587.9722 | 1229304.6944 | 2641600.4104 | 1229316.2003
17 | 2641621.4396 | 1229326.1616 | 2641627.1476 | 1229322.3992 | 2641636.7869 | 1229318.6976 | 2641646.3815 | 1229313.7951 | 2641655.2693 | 1229307.4581
18 | 2641724.8692 | 1229328.2536 | 2641723.1453 | 1229326.7072 | 2641717.9884 | 1229322.0904 | 2641717.0172 | 1229321.2275 | 2641707.8974 | 1229311.4194
19 | 2641727.9287 | 1229325.162 | 2641724.8692 | 1229328.2536
20 | 2641724.8692 | 1229328.2536 | 2641747.9073 | 1229344.6163
21 | 2641692.448 | 1229294.1729 | 2641698.7763 | 1229301.6099 | 2641707.8974 | 1229311.4194
22 | 2641727.9287 | 1229325.162 | 2641732.014 | 1229320.5545 | 2641742.5344 | 1229312.2008 | 2641752.3148 | 1229302.9831
23 | 2641727.9287 | 1229325.162 | 2641726.7231 | 1229324.2307 | 2641719.7416 | 1229318.3782 | 2641715.3365 | 1229314.11
24 | 2641582.4946 | 1229299.6274 | 2641587.9722 | 1229304.6944

## bus_geodata
| x | y | coords
0 | 2641703.7089 | 1229227.999
1 | 2641681.5867 | 1229207.6446
2 | 2641710.2723 | 1229238.3958
3 | 2641673.755 | 1229201.4596
4 | 2641703.2904 | 1229242.3049
5 | 2641671.8879 | 1229199.9854
6 | 2641697.7291 | 1229262.9564
7 | 2641689.0543 | 1229282.5077
8 | 2641682.6855 | 1229286.5101
9 | 2641682.3285 | 1229275.6073
10 | 2641609.5263 | 1229324.6329
11 | 2641616.4956 | 1229319.245
12 | 2641600.4104 | 1229316.2003
13 | 2641621.4396 | 1229326.1616
14 | 2641724.8692 | 1229328.2536
15 | 2641707.8974 | 1229311.4194
16 | 2641727.9287 | 1229325.162
17 | 2641747.9073 | 1229344.6163
18 | 2641655.2693 | 1229307.4581
19 | 2641668.8842 | 1229197.6137
20 | 2641692.448 | 1229294.1729
21 | 2641715.3365 | 1229314.11
22 | 2641680.6967 | 1229276.7104
23 | 2641752.3148 | 1229302.9831
24 | 2641587.9722 | 1229304.6944
25 | 2641582.4946 | 1229299.6274
26 | 2641701.8756 | 1229267.9886

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99529 | -0.032957 | 0.068834 | 0.017252
1 | 0.99399 | -0.042117 | 0.0094938 | 0.0023794
2 | 0.99704 | -0.020709 | 0 | 0
3 | 0.99369 | -0.044201 | 0.0094646 | 0.0023721
4 | 0.99817 | -0.012765 | 0.019159 | 0.0048017
5 | 0.99366 | -0.044471 | 0.0077496 | 0.0019422
6 | 1 | 0 | -0.21838 | -0.054664
7 | 0.99659 | -0.023784 | 0 | 0
8 | 0.99574 | -0.029741 | 0 | 0
9 | 0.99944 | -0.0038995 | 0.012788 | 0.003205
10 | 0.99306 | -0.048623 | 0 | 0
11 | 0.9932 | -0.04764 | 0 | 0
12 | 0.99286 | -0.050012 | 0.0058303 | 0.0014612
13 | 0.99334 | -0.046689 | 0 | 0
14 | 0.99324 | -0.047383 | 0 | 0
15 | 0.99387 | -0.042938 | 0.014663 | 0.003675
16 | 0.99316 | -0.047927 | 0 | 0
17 | 0.99299 | -0.049097 | 0.0059922 | 0.0015018
18 | 0.99395 | -0.042347 | 0.025042 | 0.0062762
19 | 0.99364 | -0.044605 | 0.0034581 | 0.00086668
20 | 0.99497 | -0.035215 | 0.0097528 | 0.0024443
21 | 0.99309 | -0.048425 | 0.0029335 | 0.00073519
22 | 0.99942 | -0.0040319 | 0.0067292 | 0.0016865
23 | 0.99271 | -0.051084 | 0.0094398 | 0.0023658
24 | 0.99274 | -0.050908 | 0.0036552 | 0.00091609
25 | 0.99272 | -0.051026 | 0.0015632 | 0.00039178
26 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.030211 | 0.007577 | -0.030173 | -0.0075626 | 3.8317e-05 | 1.4346e-05 | 0.045169 | 0.045169 | 0.045169 | 0.99529 | -0.032957 | 0.99399 | -0.042117 | 16.7292
1 | -0.099045 | -0.024828 | 0.099214 | 0.024893 | 0.0001683 | 6.4569e-05 | 0.14808 | 0.14808 | 0.14808 | 0.99529 | -0.032957 | 0.99704 | -0.020709 | 54.8444
2 | 0.020679 | 0.0051832 | -0.020673 | -0.0051811 | 5.9676e-06 | 2.1659e-06 | 0.030957 | 0.030957 | 0.030957 | 0.99399 | -0.042117 | 0.99369 | -0.044201 | 11.4654
3 | -0.099214 | -0.024893 | 0.099323 | 0.024935 | 0.00010949 | 4.2006e-05 | 0.14808 | 0.14808 | 0.14808 | 0.99704 | -0.020709 | 0.99817 | -0.012765 | 54.8444
4 | 0.011208 | 0.002809 | -0.011208 | -0.0028089 | 4.1817e-07 | 1.3002e-07 | 0.016784 | 0.016784 | 0.016784 | 0.99369 | -0.044201 | 0.99366 | -0.044471 | 6.2162
5 | -0.11848 | -0.029737 | 0.11869 | 0.029817 | 0.00021035 | 8.0338e-05 | 0.17664 | 0.17664 | 0.17664 | 0.99817 | -0.012765 | 1 | 0 | 32.7113
6 | 0.0034582 | 0.00086665 | -0.0034581 | -0.00086668 | 6.4046e-08 | -2.4941e-08 | 0.0051786 | 0.0051787 | 0.0051787 | 0.99366 | -0.044471 | 0.99364 | -0.044605 | 1.918
7 | 0.019528 | 0.0048953 | -0.019517 | -0.0048915 | 1.0542e-05 | 3.7921e-06 | 0.029058 | 0.029058 | 0.029058 | 1 | 0 | 0.99944 | -0.0038995 | 10.7623
8 | 0.079361 | 0.019951 | -0.079099 | -0.019851 | 0.00026204 | 0.00010039 | 0.11811 | 0.11811 | 0.11811 | 1 | 0 | 0.99659 | -0.023784 | 43.7455
9 | 0.079099 | 0.019851 | -0.079034 | -0.019826 | 6.535e-05 | 2.5037e-05 | 0.11811 | 0.11811 | 0.11811 | 0.99659 | -0.023784 | 0.99574 | -0.029741 | 43.7455
10 | 0.036166 | 0.0090726 | -0.036103 | -0.0090488 | 6.3122e-05 | 2.3828e-05 | 0.054049 | 0.054049 | 0.054049 | 0.99574 | -0.029741 | 0.99395 | -0.042347 | 20.0183
11 | 0.042868 | 0.010753 | -0.042835 | -0.010741 | 3.2517e-05 | 1.2341e-05 | 0.064064 | 0.064064 | 0.064064 | 0.99574 | -0.029741 | 0.99497 | -0.035215 | 23.7273
12 | 0.0067293 | 0.0016865 | -0.0067292 | -0.0016865 | 1.2337e-07 | 2.164e-08 | 0.010019 | 0.010019 | 0.010019 | 0.99944 | -0.0038995 | 0.99942 | -0.0040319 | 3.7107
13 | -0.011052 | -0.0027697 | 0.011053 | 0.0027701 | 1.5048e-06 | 4.6498e-07 | 0.01656 | 0.01656 | 0.01656 | 0.99306 | -0.048623 | 0.9932 | -0.04764 | 6.1332
14 | 0.011052 | 0.0027697 | -0.011049 | -0.002769 | 2.125e-06 | 6.5666e-07 | 0.01656 | 0.01656 | 0.01656 | 0.99306 | -0.048623 | 0.99286 | -0.050012 | 6.1333
15 | -0.011053 | -0.0027701 | 0.011055 | 0.0027706 | 1.4548e-06 | 4.495e-07 | 0.01656 | 0.01656 | 0.01656 | 0.9932 | -0.04764 | 0.99334 | -0.046689 | 6.1332
16 | 0.0052191 | 0.0013078 | -0.0052185 | -0.0013078 | 6.4688e-07 | 2.9697e-08 | 0.0078219 | 0.0078219 | 0.0078219 | 0.99286 | -0.050012 | 0.99274 | -0.050908 | 2.897
17 | -0.011055 | -0.0027706 | 0.011061 | 0.0027726 | 6.6481e-06 | 2.0537e-06 | 0.01656 | 0.01656 | 0.01656 | 0.99334 | -0.046689 | 0.99395 | -0.042347 | 6.1332
18 | -0.018372 | -0.0046043 | 0.018383 | 0.0046084 | 1.1312e-05 | 4.0409e-06 | 0.027524 | 0.027524 | 0.027524 | 0.99324 | -0.047383 | 0.99387 | -0.042938 | 10.1941
19 | 0.012379 | 0.0031024 | -0.012378 | -0.003102 | 9.3223e-07 | 3.0233e-07 | 0.018545 | 0.018545 | 0.018545 | 0.99324 | -0.047383 | 0.99316 | -0.047927 | 6.8685
20 | 0.0059936 | 0.001502 | -0.0059922 | -0.0015018 | 1.4217e-06 | 1.8117e-07 | 0.0089792 | 0.0089794 | 0.0089794 | 0.99324 | -0.047383 | 0.99299 | -0.049097 | 3.3257
21 | -0.033047 | -0.0082834 | 0.033082 | 0.0082967 | 3.5379e-05 | 1.3307e-05 | 0.049478 | 0.049478 | 0.049478 | 0.99387 | -0.042938 | 0.99497 | -0.035215 | 18.3252
22 | 0.0094439 | 0.002367 | -0.0094398 | -0.0023658 | 4.1266e-06 | 1.1599e-06 | 0.01415 | 0.01415 | 0.01415 | 0.99316 | -0.047927 | 0.99271 | -0.051084 | 5.2406
23 | 0.0029337 | 0.00073505 | -0.0029335 | -0.00073519 | 2.0213e-07 | -1.3922e-07 | 0.0043953 | 0.0043954 | 0.0043954 | 0.99316 | -0.047927 | 0.99309 | -0.048425 | 1.6279
24 | 0.0015632 | 0.00039169 | -0.0015632 | -0.00039178 | 2.5564e-08 | -8.6643e-08 | 0.0023431 | 0.0023432 | 0.0023432 | 0.99274 | -0.050908 | 0.99272 | -0.051026 | 0.86784

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21838 | 0.054664

## res_load
| p_mw | q_mvar
0 | 0.068834 | 0.017252
1 | 0.0094938 | 0.0023794
2 | 0.0094646 | 0.0023721
3 | 0.019159 | 0.0048017
4 | 0.0077496 | 0.0019422
5 | 0.012788 | 0.003205
6 | 0.0058303 | 0.0014612
7 | 0.014663 | 0.003675
8 | 0.0059922 | 0.0015018
9 | 0.025042 | 0.0062762
10 | 0.0034581 | 0.00086668
11 | 0.0097528 | 0.0024443
12 | 0.0029335 | 0.00073519
13 | 0.0067292 | 0.0016865
14 | 0.0094398 | 0.0023658
15 | 0.0036552 | 0.00091609
16 | 0.0015632 | 0.00039178

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1