## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1125-7_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1125-7_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1125-7_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1125-7_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1125-7_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1125-7_0_6_node_106 | 0.4 | n |  | TRUE
6 | bus_LV_1125-7_0_6_node_130 | 0.4 | n |  | TRUE
7 | bus_LV_1125-7_0_6_node_51 | 0.4 | n |  | TRUE
8 | bus_LV_1125-7_0_6_node_129 | 0.4 | n |  | TRUE
9 | bus_LV_1125-7_0_6_node_111 | 0.4 | n |  | TRUE
10 | bus_LV_1125-7_0_6_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1125-7_0_6_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1125-7_0_6_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1125-7_0_6_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1125-7_0_6_node_109 | 0.4 | n |  | TRUE
15 | bus_LV_1125-7_0_6_node_47 | 0.4 | n |  | TRUE
16 | bus_LV_1125-7_0_6_node_103 | 0.4 | n |  | TRUE
17 | bus_LV_1125-7_0_6_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_1125-7_0_6_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1125-7_0_6_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1125-7_0_6_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1125-7_0_6_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_1125-7_0_6_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1125-7_0_6_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1125-7_0_6_node_10 | 0.4 | n |  | TRUE
25 | bus_LV_1125-7_0_6_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_1125-7_0_6_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_1125-7_0_6_node_33 | 0.4 | n |  | TRUE
28 | bus_LV_1125-7_0_6_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_1125-7_0_6_node_34 | 0.4 | n |  | TRUE
30 | bus_LV_1125-7_0_6_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_1125-7_0_6_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_1125-7_0_6_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_1125-7_0_6_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_1125-7_0_6_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_1125-7_0_6_node_37 | 0.4 | n |  | TRUE
36 | bus_LV_1125-7_0_6_node_38 | 0.4 | n |  | TRUE
37 | bus_LV_1125-7_0_6_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_1125-7_0_6_node_35 | 0.4 | n |  | TRUE
39 | bus_LV_1125-7_0_6_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_1125-7_0_6_node_41 | 0.4 | n |  | TRUE
41 | bus_LV_1125-7_0_6_node_39 | 0.4 | n |  | TRUE
42 | bus_LV_1125-7_0_6_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_1125-7_0_6_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_1125-7_0_6_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_1125-7_0_6_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_1125-7_0_6_node_70 | 0.4 | n |  | TRUE
47 | bus_LV_1125-7_0_6_node_69 | 0.4 | n |  | TRUE
48 | bus_LV_1125-7_0_6_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_1125-7_0_6_node_80 | 0.4 | n |  | TRUE
50 | bus_LV_1125-7_0_6_node_77 | 0.4 | n |  | TRUE
51 | bus_LV_1125-7_0_6_node_76 | 0.4 | n |  | TRUE
52 | bus_LV_1125-7_0_6_node_42 | 0.4 | n |  | TRUE
53 | bus_LV_1125-7_0_6_node_44 | 0.4 | n |  | TRUE
54 | bus_LV_1125-7_0_6_node_43 | 0.4 | n |  | TRUE
55 | bus_LV_1125-7_0_6_node_45 | 0.4 | n |  | TRUE
56 | bus_LV_1125-7_0_6_node_46 | 0.4 | n |  | TRUE
57 | bus_LV_1125-7_0_6_node_91 | 0.4 | n |  | TRUE
58 | bus_LV_1125-7_0_6_node_88 | 0.4 | n |  | TRUE
59 | bus_LV_1125-7_0_6_node_54 | 0.4 | n |  | TRUE
60 | bus_LV_1125-7_0_6_node_102 | 0.4 | n |  | TRUE
61 | bus_LV_1125-7_0_6_node_89 | 0.4 | n |  | TRUE
62 | bus_LV_1125-7_0_6_node_55 | 0.4 | n |  | TRUE
63 | bus_LV_1125-7_0_6_node_48 | 0.4 | n |  | TRUE
64 | bus_LV_1125-7_0_6_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_1125-7_0_6_node_50 | 0.4 | n |  | TRUE
66 | bus_LV_1125-7_0_6_node_52 | 0.4 | n |  | TRUE
67 | bus_LV_1125-7_0_6_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_1125-7_0_6_node_87 | 0.4 | n |  | TRUE
69 | bus_LV_1125-7_0_6_node_65 | 0.4 | n |  | TRUE
70 | bus_LV_1125-7_0_6_node_82 | 0.4 | n |  | TRUE
71 | bus_LV_1125-7_0_6_node_63 | 0.4 | n |  | TRUE
72 | bus_LV_1125-7_0_6_node_83 | 0.4 | n |  | TRUE
73 | bus_LV_1125-7_0_6_node_56 | 0.4 | n |  | TRUE
74 | bus_LV_1125-7_0_6_node_79 | 0.4 | n |  | TRUE
75 | bus_LV_1125-7_0_6_node_68 | 0.4 | n |  | TRUE
76 | bus_LV_1125-7_0_6_node_78 | 0.4 | n |  | TRUE
77 | bus_LV_1125-7_0_6_node_67 | 0.4 | n |  | TRUE
78 | bus_LV_1125-7_0_6_node_64 | 0.4 | n |  | TRUE
79 | bus_LV_1125-7_0_6_node_66 | 0.4 | n |  | TRUE
80 | bus_LV_1125-7_0_6_node_58 | 0.4 | n |  | TRUE
81 | bus_LV_1125-7_0_6_node_59 | 0.4 | n |  | TRUE
82 | bus_LV_1125-7_0_6_node_60 | 0.4 | n |  | TRUE
83 | bus_LV_1125-7_0_6_node_61 | 0.4 | n |  | TRUE
84 | bus_LV_1125-7_0_6_node_62 | 0.4 | n |  | TRUE
85 | bus_LV_1125-7_0_6_node_71 | 0.4 | n |  | TRUE
86 | bus_LV_1125-7_0_6_node_72 | 0.4 | n |  | TRUE
87 | bus_LV_1125-7_0_6_node_73 | 0.4 | n |  | TRUE
88 | bus_LV_1125-7_0_6_node_74 | 0.4 | n |  | TRUE
89 | bus_LV_1125-7_0_6_node_75 | 0.4 | n |  | TRUE
90 | bus_LV_1125-7_0_6_node_93 | 0.4 | n |  | TRUE
91 | bus_LV_1125-7_0_6_node_107 | 0.4 | n |  | TRUE
92 | bus_LV_1125-7_0_6_node_108 | 0.4 | n |  | TRUE
93 | bus_LV_1125-7_0_6_node_92 | 0.4 | n |  | TRUE
94 | bus_LV_1125-7_0_6_node_81 | 0.4 | n |  | TRUE
95 | bus_LV_1125-7_0_6_node_98 | 0.4 | n |  | TRUE
96 | bus_LV_1125-7_0_6_node_100 | 0.4 | n |  | TRUE
97 | bus_LV_1125-7_0_6_node_86 | 0.4 | n |  | TRUE
98 | bus_LV_1125-7_0_6_node_96 | 0.4 | n |  | TRUE
99 | bus_LV_1125-7_0_6_node_84 | 0.4 | n |  | TRUE
100 | bus_LV_1125-7_0_6_node_85 | 0.4 | n |  | TRUE
101 | bus_LV_1125-7_0_6_node_90 | 0.4 | n |  | TRUE
102 | bus_LV_1125-7_0_6_node_95 | 0.4 | n |  | TRUE
103 | bus_LV_1125-7_0_6_node_94 | 0.4 | n |  | TRUE
104 | bus_LV_1125-7_0_6_node_97 | 0.4 | n |  | TRUE
105 | bus_LV_1125-7_0_6_node_99 | 0.4 | n |  | TRUE
106 | bus_LV_1125-7_0_6_node_105 | 0.4 | n |  | TRUE
107 | bus_LV_1125-7_0_6_node_104 | 0.4 | n |  | TRUE
108 | bus_LV_1125-7_0_6_node_110 | 0.4 | n |  | TRUE
109 | bus_LV_1125-7_0_6_node_112 | 0.4 | n |  | TRUE
110 | bus_LV_1125-7_0_6_node_113 | 0.4 | n |  | TRUE
111 | bus_LV_1125-7_0_6_node_120 | 0.4 | n |  | TRUE
112 | bus_LV_1125-7_0_6_node_121 | 0.4 | n |  | TRUE
113 | bus_LV_1125-7_0_6_node_114 | 0.4 | n |  | TRUE
114 | bus_LV_1125-7_0_6_node_115 | 0.4 | n |  | TRUE
115 | bus_LV_1125-7_0_6_node_116 | 0.4 | n |  | TRUE
116 | bus_LV_1125-7_0_6_node_117 | 0.4 | n |  | TRUE
117 | bus_LV_1125-7_0_6_node_118 | 0.4 | n |  | TRUE
118 | bus_LV_1125-7_0_6_node_119 | 0.4 | n |  | TRUE
119 | bus_LV_1125-7_0_6_node_128 | 0.4 | n |  | TRUE
120 | bus_LV_1125-7_0_6_node_126 | 0.4 | n |  | TRUE
121 | bus_LV_1125-7_0_6_node_122 | 0.4 | n |  | TRUE
122 | bus_MV_131_0_node_208 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1125-7_0_6_load_0 | 0 | 0.0022308 | 0.00055908 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1125-7_0_6_load_1 | 1 | 0.0047149 | 0.0011817 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1125-7_0_6_load_3 | 3 | 0.0023013 | 0.00057677 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1125-7_0_6_load_51 | 7 | 0.0013632 | 0.00034166 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1125-7_0_6_load_129 | 8 | 0.0042374 | 0.001062 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1125-7_0_6_load_111 | 9 | 0.00046643 | 0.0001169 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1125-7_0_6_load_5 | 10 | 0.0080685 | 0.0020222 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1125-7_0_6_load_8 | 13 | 0.0011864 | 0.00029733 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1125-7_0_6_load_47 | 15 | 0.00072 | 0.00018045 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1125-7_0_6_load_103 | 16 | 0.0019263 | 0.00048277 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1125-7_0_6_load_19 | 17 | 0.00066674 | 0.0001671 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1125-7_0_6_load_16 | 18 | 0.0014818 | 0.00037138 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1125-7_0_6_load_17 | 20 | 0.0008728 | 0.00021875 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1125-7_0_6_load_9 | 21 | 0.0029692 | 0.00074416 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1125-7_0_6_load_15 | 23 | 0.0019649 | 0.00049246 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1125-7_0_6_load_12 | 25 | 0.00067043 | 0.00016803 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1125-7_0_6_load_25 | 26 | 0.0025688 | 0.00064379 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1125-7_0_6_load_33 | 27 | 0.0014761 | 0.00036994 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1125-7_0_6_load_26 | 28 | 0.0044313 | 0.0011106 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1125-7_0_6_load_21 | 30 | 0.0010917 | 0.0002736 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1125-7_0_6_load_20 | 31 | 0.0028955 | 0.00072568 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1125-7_0_6_load_23 | 33 | 0.0058567 | 0.0014678 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1125-7_0_6_load_24 | 34 | 0.0082554 | 0.002069 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1125-7_0_6_load_38 | 36 | 0.0011769 | 0.00029495 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1125-7_0_6_load_32 | 37 | 0.0012657 | 0.00031721 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1125-7_0_6_load_35 | 38 | 0.0011794 | 0.00029557 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1125-7_0_6_load_36 | 39 | 0.0028509 | 0.0007145 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1125-7_0_6_load_41 | 40 | 0.0017306 | 0.00043374 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1125-7_0_6_load_39 | 41 | 0.0008576 | 0.00021494 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1125-7_0_6_load_28 | 42 | 0.00027029 | 6.774e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1125-7_0_6_load_29 | 43 | 0.00092439 | 0.00023168 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1125-7_0_6_load_31 | 45 | 0.00079406 | 0.00019901 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1125-7_0_6_load_70 | 46 | 0.0022845 | 0.00057255 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1125-7_0_6_load_69 | 47 | 0.0023522 | 0.00058952 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1125-7_0_6_load_40 | 48 | 0.0014298 | 0.00035835 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1125-7_0_6_load_80 | 49 | 0.0036537 | 0.00091569 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1125-7_0_6_load_76 | 51 | 0.0027818 | 0.00069719 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1125-7_0_6_load_42 | 52 | 0.00014934 | 3.7428e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1125-7_0_6_load_43 | 54 | 0.010722 | 0.0026871 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1125-7_0_6_load_91 | 57 | 0.0018858 | 0.00047264 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1125-7_0_6_load_88 | 58 | 0.0062249 | 0.0015601 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1125-7_0_6_load_54 | 59 | 0.00035784 | 8.9683e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1125-7_0_6_load_102 | 60 | 0.0035544 | 0.00089082 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1125-7_0_6_load_89 | 61 | 0.0069664 | 0.001746 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1125-7_0_6_load_55 | 62 | 0.00026952 | 6.7548e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1125-7_0_6_load_48 | 63 | 0.0011997 | 0.00030068 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1125-7_0_6_load_49 | 64 | 0.0011223 | 0.00028127 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1125-7_0_6_load_53 | 67 | 0.0037538 | 0.00094079 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1125-7_0_6_load_87 | 68 | 0.0047222 | 0.0011835 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1125-7_0_6_load_65 | 69 | 0.0035593 | 0.00089205 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1125-7_0_6_load_82 | 70 | 0.0044896 | 0.0011252 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1125-7_0_6_load_63 | 71 | 0.0026244 | 0.00065773 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1125-7_0_6_load_79 | 74 | 0.0017773 | 0.00044544 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1125-7_0_6_load_68 | 75 | 0.0015752 | 0.00039478 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1125-7_0_6_load_78 | 76 | 0.0019638 | 0.00049216 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1125-7_0_6_load_67 | 77 | 0.00094147 | 0.00023595 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1125-7_0_6_load_64 | 78 | 0.00092681 | 0.00023228 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1125-7_0_6_load_66 | 79 | 0.0014419 | 0.00036137 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1125-7_0_6_load_58 | 80 | 0.00075857 | 0.00019012 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1125-7_0_6_load_59 | 81 | 0.0013144 | 0.00032943 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1125-7_0_6_load_60 | 82 | 0.0017354 | 0.00043493 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1125-7_0_6_load_61 | 83 | 0.0042026 | 0.0010533 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1125-7_0_6_load_62 | 84 | 0.0017437 | 0.00043702 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1125-7_0_6_load_71 | 85 | 0.00092194 | 0.00023106 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1125-7_0_6_load_72 | 86 | 0.0011818 | 0.0002962 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1125-7_0_6_load_73 | 87 | 0.0010551 | 0.00026443 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1125-7_0_6_load_74 | 88 | 0.0013877 | 0.00034779 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1125-7_0_6_load_93 | 90 | 0.0013169 | 0.00033006 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1125-7_0_6_load_107 | 91 | 0.00057115 | 0.00014314 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1125-7_0_6_load_108 | 92 | 0.00079051 | 0.00019812 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1125-7_0_6_load_92 | 93 | 0.00093526 | 0.0002344 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1125-7_0_6_load_98 | 95 | 0.0014632 | 0.0003667 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1125-7_0_6_load_100 | 96 | 0.0023303 | 0.00058403 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1125-7_0_6_load_86 | 97 | 0.0051462 | 0.0012897 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1125-7_0_6_load_96 | 98 | 0.0018388 | 0.00046084 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1125-7_0_6_load_84 | 99 | 0.0024989 | 0.00062628 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1125-7_0_6_load_85 | 100 | 0.0069903 | 0.0017519 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1125-7_0_6_load_90 | 101 | 0.0015629 | 0.00039169 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1125-7_0_6_load_95 | 102 | 0.0021495 | 0.00053871 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1125-7_0_6_load_94 | 103 | 0.00086173 | 0.00021597 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1125-7_0_6_load_97 | 104 | 0.0015871 | 0.00039777 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1125-7_0_6_load_99 | 105 | 0.0018969 | 0.00047542 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1125-7_0_6_load_105 | 106 | 0.0018247 | 0.00045732 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1125-7_0_6_load_104 | 107 | 0.0021996 | 0.00055127 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1125-7_0_6_load_110 | 108 | 0.00014911 | 3.7371e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1125-7_0_6_load_112 | 109 | 5.1067e-05 | 1.2799e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1125-7_0_6_load_113 | 110 | 0.00012071 | 3.0253e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1125-7_0_6_load_120 | 111 | 0.00040866 | 0.00010242 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1125-7_0_6_load_114 | 113 | 0.00036462 | 9.1382e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1125-7_0_6_load_115 | 114 | 8.8509e-05 | 2.2183e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1125-7_0_6_load_117 | 116 | 0.00027117 | 6.7963e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1125-7_0_6_load_119 | 118 | 0.00072449 | 0.00018158 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1125-7_0_6_load_128 | 119 | 0.00045102 | 0.00011304 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1125-7_0_6_load_126 | 120 | 0.00023477 | 5.8838e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1125-7_0_6_load_122 | 121 | 0.00064791 | 0.00016238 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1125-7_0_6_line_0 | NAYY 4x150 SE | 0 | 1 | 0.023861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1125-7_0_6_line_1 | NAYY 4x150 SE | 0 | 2 | 0.025867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1125-7_0_6_line_2 | NAYY 4x150 SE | 1 | 3 | 0.018524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1125-7_0_6_line_3 | NAYY 4x150 SE | 2 | 4 | 0.055005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1125-7_0_6_line_4 | NAYY 4x150 SE | 4 | 8 | 0.019596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1125-7_0_6_line_5 | NAYY 4x150 SE | 5 | 6 | 0.18414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1125-7_0_6_line_6 | NAYY 4x150 SE | 5 | 7 | 0.12852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1125-7_0_6_line_7 | NAYY 4x150 SE | 6 | 8 | 0.022125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1125-7_0_6_line_8 | NAYY 4x150 SE | 6 | 9 | 0.19286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1125-7_0_6_line_9 | NAYY 4x150 SE | 7 | 64 | 0.0082255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1125-7_0_6_line_10 | NAYY 4x150 SE | 9 | 108 | 0.040507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1125-7_0_6_line_11 | NAYY 4x150 SE | 10 | 11 | 0.1437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1125-7_0_6_line_12 | NAYY 4x150 SE | 11 | 12 | 0.086289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1125-7_0_6_line_13 | NAYY 4x150 SE | 11 | 13 | 0.025955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1125-7_0_6_line_14 | NAYY 4x150 SE | 12 | 17 | 0.049386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1125-7_0_6_line_15 | NAYY 4x150 SE | 12 | 18 | 0.081072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1125-7_0_6_line_16 | NAYY 4x150 SE | 13 | 19 | 0.0059849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1125-7_0_6_line_17 | NAYY 4x150 SE | 14 | 15 | 0.097585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_1125-7_0_6_line_18 | NAYY 4x150 SE | 14 | 16 | 0.22077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_1125-7_0_6_line_19 | NAYY 4x150 SE | 15 | 53 | 0.04585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_1125-7_0_6_line_20 | NAYY 4x150 SE | 16 | 107 | 0.020553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_1125-7_0_6_line_21 | NAYY 4x150 SE | 18 | 20 | 0.025481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1125-7_0_6_line_22 | NAYY 4x150 SE | 18 | 21 | 0.26424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1125-7_0_6_line_23 | NAYY 4x150 SE | 19 | 22 | 0.049528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1125-7_0_6_line_24 | NAYY 4x150 SE | 19 | 23 | 0.028901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1125-7_0_6_line_25 | NAYY 4x150 SE | 21 | 24 | 0.022204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1125-7_0_6_line_26 | NAYY 4x150 SE | 22 | 26 | 0.011958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1125-7_0_6_line_27 | NAYY 4x150 SE | 23 | 27 | 0.030072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1125-7_0_6_line_28 | NAYY 4x150 SE | 24 | 25 | 0.026655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1125-7_0_6_line_29 | NAYY 4x150 SE | 26 | 28 | 0.02225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1125-7_0_6_line_30 | NAYY 4x150 SE | 27 | 29 | 0.045737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1125-7_0_6_line_31 | NAYY 4x150 SE | 29 | 38 | 0.046081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1125-7_0_6_line_32 | NAYY 4x150 SE | 29 | 39 | 0.040165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_1125-7_0_6_line_33 | NAYY 4x150 SE | 29 | 34 | 0.013503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1125-7_0_6_line_34 | NAYY 4x150 SE | 30 | 31 | 0.017493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1125-7_0_6_line_35 | NAYY 4x150 SE | 31 | 32 | 0.015575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1125-7_0_6_line_36 | NAYY 4x150 SE | 32 | 33 | 0.049226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1125-7_0_6_line_37 | NAYY 4x150 SE | 32 | 34 | 0.0098138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1125-7_0_6_line_38 | NAYY 4x150 SE | 33 | 35 | 0.01655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1125-7_0_6_line_39 | NAYY 4x150 SE | 35 | 36 | 0.012586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1125-7_0_6_line_40 | NAYY 4x150 SE | 35 | 37 | 0.043169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1125-7_0_6_line_41 | NAYY 4x150 SE | 36 | 51 | 0.032365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1125-7_0_6_line_42 | NAYY 4x150 SE | 37 | 44 | 0.023619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1125-7_0_6_line_43 | NAYY 4x150 SE | 38 | 48 | 0.01508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1125-7_0_6_line_44 | NAYY 4x150 SE | 39 | 49 | 0.024553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
45 | LV_1125-7_0_6_line_45 | NAYY 4x150 SE | 40 | 41 | 0.020671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1125-7_0_6_line_46 | NAYY 4x150 SE | 41 | 48 | 0.004133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1125-7_0_6_line_47 | NAYY 4x150 SE | 42 | 43 | 0.01873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1125-7_0_6_line_48 | NAYY 4x150 SE | 42 | 44 | 0.07096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1125-7_0_6_line_49 | NAYY 4x150 SE | 44 | 45 | 0.025953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1125-7_0_6_line_50 | NAYY 4x150 SE | 45 | 46 | 0.0032937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1125-7_0_6_line_51 | NAYY 4x150 SE | 46 | 47 | 0.015609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1125-7_0_6_line_52 | NAYY 4x150 SE | 47 | 82 | 0.020477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1125-7_0_6_line_53 | NAYY 4x150 SE | 49 | 50 | 0.037924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
54 | LV_1125-7_0_6_line_54 | NAYY 4x150 SE | 50 | 94 | 0.047438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_1125-7_0_6_line_55 | NAYY 4x150 SE | 52 | 53 | 0.042976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1125-7_0_6_line_56 | NAYY 4x150 SE | 53 | 56 | 0.028754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
57 | LV_1125-7_0_6_line_57 | NAYY 4x150 SE | 54 | 55 | 0.053468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1125-7_0_6_line_58 | NAYY 4x150 SE | 55 | 57 | 0.011861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1125-7_0_6_line_59 | NAYY 4x150 SE | 55 | 58 | 0.016799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1125-7_0_6_line_60 | NAYY 4x150 SE | 56 | 59 | 0.013956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_1125-7_0_6_line_61 | NAYY 4x150 SE | 57 | 60 | 0.011908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1125-7_0_6_line_62 | NAYY 4x150 SE | 58 | 61 | 0.00076878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1125-7_0_6_line_63 | NAYY 4x150 SE | 59 | 62 | 0.021423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
64 | LV_1125-7_0_6_line_64 | NAYY 4x150 SE | 60 | 99 | 0.037812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1125-7_0_6_line_65 | NAYY 4x150 SE | 61 | 101 | 0.027392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1125-7_0_6_line_66 | NAYY 4x150 SE | 62 | 73 | 0.027388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
67 | LV_1125-7_0_6_line_67 | NAYY 4x150 SE | 63 | 64 | 0.017747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
68 | LV_1125-7_0_6_line_68 | NAYY 4x150 SE | 63 | 65 | 0.052068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
69 | LV_1125-7_0_6_line_69 | NAYY 4x150 SE | 65 | 66 | 0.010732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
70 | LV_1125-7_0_6_line_70 | NAYY 4x150 SE | 65 | 67 | 0.020687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
71 | LV_1125-7_0_6_line_71 | NAYY 4x150 SE | 66 | 68 | 0.047326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1125-7_0_6_line_72 | NAYY 4x150 SE | 66 | 69 | 0.011649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
73 | LV_1125-7_0_6_line_73 | NAYY 4x150 SE | 67 | 70 | 0.0022934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1125-7_0_6_line_74 | NAYY 4x150 SE | 69 | 71 | 0.038543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
75 | LV_1125-7_0_6_line_75 | NAYY 4x150 SE | 70 | 72 | 0.045088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1125-7_0_6_line_76 | NAYY 4x150 SE | 71 | 83 | 0.023549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
77 | LV_1125-7_0_6_line_77 | NAYY 4x150 SE | 72 | 99 | 0.011246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1125-7_0_6_line_78 | NAYY 4x150 SE | 72 | 100 | 0.047531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1125-7_0_6_line_79 | NAYY 4x150 SE | 72 | 97 | 0.042499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1125-7_0_6_line_80 | NAYY 4x150 SE | 73 | 74 | 0.032368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1125-7_0_6_line_81 | NAYY 4x150 SE | 73 | 75 | 0.007473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1125-7_0_6_line_82 | NAYY 4x150 SE | 73 | 76 | 0.015212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
83 | LV_1125-7_0_6_line_83 | NAYY 4x150 SE | 75 | 77 | 0.037097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1125-7_0_6_line_84 | NAYY 4x150 SE | 76 | 78 | 0.0081125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
85 | LV_1125-7_0_6_line_85 | NAYY 4x150 SE | 77 | 79 | 0.005764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1125-7_0_6_line_86 | NAYY 4x150 SE | 78 | 84 | 0.0099162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
87 | LV_1125-7_0_6_line_87 | NAYY 4x150 SE | 80 | 81 | 0.014769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1125-7_0_6_line_88 | NAYY 4x150 SE | 81 | 82 | 0.0016103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1125-7_0_6_line_89 | NAYY 4x150 SE | 83 | 84 | 0.0053071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
90 | LV_1125-7_0_6_line_90 | NAYY 4x150 SE | 85 | 86 | 0.017896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1125-7_0_6_line_91 | NAYY 4x150 SE | 85 | 87 | 0.0010861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1125-7_0_6_line_92 | NAYY 4x150 SE | 86 | 88 | 0.0014738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1125-7_0_6_line_93 | NAYY 4x150 SE | 87 | 89 | 0.029762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1125-7_0_6_line_94 | NAYY 4x150 SE | 88 | 90 | 0.015304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1125-7_0_6_line_95 | NAYY 4x150 SE | 89 | 91 | 0.018264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1125-7_0_6_line_96 | NAYY 4x150 SE | 89 | 92 | 0.014273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1125-7_0_6_line_97 | NAYY 4x150 SE | 90 | 93 | 0.016836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1125-7_0_6_line_98 | NAYY 4x150 SE | 93 | 103 | 0.019044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1125-7_0_6_line_99 | NAYY 4x150 SE | 94 | 95 | 0.030467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_1125-7_0_6_line_100 | NAYY 4x150 SE | 94 | 96 | 0.013503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1125-7_0_6_line_101 | NAYY 4x150 SE | 95 | 98 | 0.017139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
102 | LV_1125-7_0_6_line_102 | NAYY 4x150 SE | 98 | 104 | 0.019574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
103 | LV_1125-7_0_6_line_103 | NAYY 4x150 SE | 101 | 102 | 0.023549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1125-7_0_6_line_104 | NAYY 4x150 SE | 102 | 103 | 0.0019949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1125-7_0_6_line_105 | NAYY 4x150 SE | 104 | 105 | 0.017452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
106 | LV_1125-7_0_6_line_106 | NAYY 4x150 SE | 105 | 106 | 0.019532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
107 | LV_1125-7_0_6_line_107 | NAYY 4x150 SE | 106 | 107 | 0.024604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
108 | LV_1125-7_0_6_line_108 | NAYY 4x150 SE | 108 | 109 | 0.0093963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1125-7_0_6_line_109 | NAYY 4x150 SE | 109 | 110 | 0.007361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1125-7_0_6_line_110 | NAYY 4x150 SE | 110 | 111 | 0.008056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1125-7_0_6_line_111 | NAYY 4x150 SE | 111 | 112 | 0.047372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1125-7_0_6_line_112 | NAYY 4x150 SE | 112 | 121 | 0.025932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1125-7_0_6_line_113 | NAYY 4x150 SE | 112 | 117 | 0.006291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1125-7_0_6_line_114 | NAYY 4x150 SE | 113 | 114 | 0.0099677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1125-7_0_6_line_115 | NAYY 4x150 SE | 113 | 115 | 0.017447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1125-7_0_6_line_116 | NAYY 4x150 SE | 114 | 116 | 0.044833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1125-7_0_6_line_117 | NAYY 4x150 SE | 115 | 117 | 0.068203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1125-7_0_6_line_118 | NAYY 4x150 SE | 115 | 118 | 0.03034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1125-7_0_6_line_119 | NAYY 4x150 SE | 117 | 119 | 0.08112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1125-7_0_6_line_120 | NAYY 4x150 SE | 118 | 120 | 0.046264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1125-7_0_6_trafo_109 | 0.25 MVA 20/0.4 kV | 122 | 14 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2645743.099 | 1228432.0947 | 2645765.8697 | 1228424.9656
1 | 2645718.9876 | 1228441.4165 | 2645737.48 | 1228433.8539 | 2645743.099 | 1228432.0947
2 | 2645783.5475 | 1228419.4311 | 2645765.8697 | 1228424.9656
3 | 2645718.9876 | 1228441.4165 | 2645667.942 | 1228462.271
4 | 2645667.942 | 1228462.271 | 2645658.2348 | 1228471.3355 | 2645652.7271 | 1228474.4232
5 | 2645541.5697 | 1228325.6515 | 2645633.428 | 1228485.2428
6 | 2645541.5697 | 1228325.6515 | 2645527.0549 | 1228304.5163 | 2645503.8436 | 1228278.1781 | 2645460.4198 | 1228243.4915 | 2645450.8283 | 1228235.9495
7 | 2645633.428 | 1228485.2428 | 2645652.7271 | 1228474.4232
8 | 2645633.428 | 1228485.2428 | 2645442.606 | 1228513.2177
9 | 2645450.8283 | 1228235.9495 | 2645444.3624 | 1228230.8652
10 | 2645422.7021 | 1228548.2214 | 2645424.5741 | 1228542.0474 | 2645440.4189 | 1228517.9756 | 2645442.606 | 1228513.2177
11 | 2645263.7119 | 1227400.905 | 2645252.3445 | 1227311.2522 | 2645251.3702 | 1227290.8989 | 2645254.031 | 1227269.8617 | 2645256.7628 | 1227258.4318
12 | 2645263.7119 | 1227400.905 | 2645251.7762 | 1227401.9372 | 2645180.5496 | 1227423.921
13 | 2645263.7119 | 1227400.905 | 2645265.1837 | 1227426.8187
14 | 2645180.5496 | 1227423.921 | 2645145.9023 | 1227459.1145
15 | 2645180.5496 | 1227423.921 | 2645126.5122 | 1227437.6752 | 2645111.1559 | 1227444.0962 | 2645104.5962 | 1227449.7613
16 | 2645265.523 | 1227432.7941 | 2645265.1837 | 1227426.8187
17 | 2645230.5206 | 1227912.2243 | 2645235.1461 | 1228009.6992
18 | 2645230.5206 | 1227912.2243 | 2645240.6608 | 1227691.6906
19 | 2645237.3194 | 1228055.498 | 2645235.1461 | 1228009.6992
20 | 2645240.6608 | 1227691.6906 | 2645253.8944 | 1227675.9651
21 | 2645086.1945 | 1227467.3678 | 2645099.058 | 1227454.5443 | 2645104.5962 | 1227449.7613
22 | 2645104.5962 | 1227449.7613 | 2644917.7203 | 1227262.9392
23 | 2645299.0578 | 1227397.7052 | 2645291.4054 | 1227404.4734 | 2645283.6265 | 1227413.9312 | 2645274.7945 | 1227427.3501 | 2645271.2205 | 1227430.9585 | 2645265.523 | 1227432.7941
24 | 2645265.523 | 1227432.7941 | 2645263.9854 | 1227454.6181 | 2645262.7473 | 1227461.5305
25 | 2644895.9114 | 1227261.0453 | 2644902.3309 | 1227262.9616 | 2644908.7585 | 1227263.8106 | 2644914.869 | 1227263.4787 | 2644917.7203 | 1227262.9392
26 | 2645299.0578 | 1227397.7052 | 2645309.8638 | 1227402.8254
27 | 2645255.5266 | 1227490.6312 | 2645259.688 | 1227478.6113 | 2645262.7473 | 1227461.5305
28 | 2644895.9114 | 1227261.0453 | 2644884.1988 | 1227284.9892
29 | 2645329.971 | 1227412.3528 | 2645309.8638 | 1227402.8254
30 | 2645237.9892 | 1227532.8355 | 2645251.1883 | 1227503.1619 | 2645255.5266 | 1227490.6312
31 | 2645237.9892 | 1227532.8355 | 2645251.1756 | 1227527.7548 | 2645278.9675 | 1227511.9952
32 | 2645237.9892 | 1227532.8355 | 2645252.7949 | 1227534.0376 | 2645277.278 | 1227540.457
33 | 2645237.9892 | 1227532.8355 | 2645230.4526 | 1227544.0391
34 | 2645212.2922 | 1227543.1407 | 2645201.2029 | 1227535.2354 | 2645198.3488 | 1227532.6157
35 | 2645224.9749 | 1227552.1819 | 2645212.2922 | 1227543.1407
36 | 2645224.9749 | 1227552.1819 | 2645211.0268 | 1227568.764 | 2645192.6386 | 1227589.2893
37 | 2645224.9749 | 1227552.1819 | 2645230.4526 | 1227544.0391
38 | 2645181.595 | 1227601.6164 | 2645192.6386 | 1227589.2893
39 | 2645181.595 | 1227601.6164 | 2645191.9235 | 1227606.609 | 2645193.0374 | 1227606.5903
40 | 2645181.595 | 1227601.6164 | 2645149.9611 | 1227630.9909
41 | 2645193.0374 | 1227606.5903 | 2645201.0408 | 1227606.4559 | 2645223.148 | 1227596.2243
42 | 2645132.6537 | 1227647.0622 | 2645149.9611 | 1227630.9909
43 | 2645278.9675 | 1227511.9952 | 2645292.0856 | 1227504.5565
44 | 2645299.1285 | 1227550.6669 | 2645296.7851 | 1227547.9251 | 2645283.7571 | 1227542.1558 | 2645277.278 | 1227540.457
45 | 2645295.6809 | 1227502.5178 | 2645313.662 | 1227492.3215
46 | 2645295.6809 | 1227502.5178 | 2645292.0856 | 1227504.5565
47 | 2645074.5272 | 1227629.1444 | 2645062.4376 | 1227637.1131 | 2645058.59 | 1227638.9188
48 | 2645132.6537 | 1227647.0622 | 2645105.2765 | 1227620.8941 | 2645094.6914 | 1227619.7577 | 2645083.0156 | 1227623.5494 | 2645074.5272 | 1227629.1444
49 | 2645132.6537 | 1227647.0622 | 2645116.9703 | 1227667.7406
50 | 2645114.9799 | 1227670.3649 | 2645114.9799 | 1227670.3649 | 2645116.9703 | 1227667.7406
51 | 2645106.9679 | 1227683.7607 | 2645111.4954 | 1227676.1976 | 2645114.9799 | 1227670.3649
52 | 2645106.9679 | 1227683.7607 | 2645096.4503 | 1227701.33
53 | 2645285.1274 | 1227583.1582 | 2645285.0726 | 1227572.4289 | 2645287.4827 | 1227566.4102 | 2645296.7715 | 1227558.6761 | 2645299.2473 | 1227553.9809 | 2645299.1285 | 1227550.6669
54 | 2645332.0394 | 1227575.5216 | 2645310.4464 | 1227578.0032 | 2645285.1274 | 1227583.1582
55 | 2645237.3194 | 1228055.498 | 2645274.2103 | 1228059.8477 | 2645280.0153 | 1228059.312
56 | 2645237.3194 | 1228055.498 | 2645238.6847 | 1228084.215
57 | 2645435.6861 | 1228056.2645 | 2645431.429 | 1228038.232 | 2645427.0496 | 1228032.2393 | 2645418.5141 | 1228030.7066 | 2645399.6753 | 1228031.1916
58 | 2645435.6861 | 1228056.2645 | 2645435.3596 | 1228068.1214
59 | 2645435.6861 | 1228056.2645 | 2645451.4594 | 1228050.4853
60 | 2645238.6847 | 1228084.215 | 2645251.942 | 1228088.574
61 | 2645435.3596 | 1228068.1214 | 2645435.2352 | 1228072.6379 | 2645433.1855 | 1228079.7377
62 | 2645451.4594 | 1228050.4853 | 2645452.1812 | 1228050.2209
63 | 2645251.942 | 1228088.574 | 2645265.1548 | 1228097.7912 | 2645268.8427 | 1228101.616
64 | 2645418.3644 | 1228114.2718 | 2645423.2273 | 1228107.1232 | 2645430.8923 | 1228087.6807 | 2645433.1855 | 1228079.7377
65 | 2645452.1812 | 1228050.2209 | 2645477.9014 | 1228040.7972
66 | 2645286.4551 | 1228122.5686 | 2645272.7253 | 1228105.6426 | 2645268.8427 | 1228101.616
67 | 2645430.4093 | 1228219.8979 | 2645443.172 | 1228229.9292 | 2645444.3624 | 1228230.8652
68 | 2645389.4774 | 1228187.7157 | 2645427.3025 | 1228217.4559 | 2645430.4093 | 1228219.8979
69 | 2645389.4774 | 1228187.7157 | 2645380.0916 | 1228182.4631
70 | 2645389.4774 | 1228187.7157 | 2645397.1648 | 1228168.51
71 | 2645380.0916 | 1228182.4631 | 2645380.5778 | 1228195.208 | 2645385.7493 | 1228229.3909
72 | 2645380.0916 | 1228182.4631 | 2645370.0666 | 1228176.5302
73 | 2645398.017 | 1228166.3809 | 2645397.1648 | 1228168.51
74 | 2645370.0666 | 1228176.5302 | 2645364.4095 | 1228173.1823 | 2645335.6373 | 1228159.2458
75 | 2645412.039 | 1228123.5702 | 2645403.0491 | 1228153.8093 | 2645398.017 | 1228166.3809
76 | 2645314.8192 | 1228148.3351 | 2645318.8649 | 1228151.1218 | 2645335.6373 | 1228159.2458
77 | 2645412.039 | 1228123.5702 | 2645418.3644 | 1228114.2718
78 | 2645412.039 | 1228123.5702 | 2645425.4602 | 1228116.357 | 2645456.8501 | 1228108.7691
79 | 2645412.039 | 1228123.5702 | 2645369.5896 | 1228121.5222
80 | 2645286.4551 | 1228122.5686 | 2645290.9652 | 1228119.3564 | 2645296.8175 | 1228118.0112 | 2645317.6194 | 1228119.0149
81 | 2645286.4551 | 1228122.5686 | 2645278.9822 | 1228122.5423
82 | 2645286.4551 | 1228122.5686 | 2645293.5103 | 1228130.416 | 2645296.7106 | 1228133.803
83 | 2645278.9822 | 1228122.5423 | 2645272.8999 | 1228122.521 | 2645262.1354 | 1228123.1729 | 2645242.2319 | 1228119.5534
84 | 2645296.7106 | 1228133.803 | 2645302.2822 | 1228139.6996 | 2645302.2822 | 1228139.6996
85 | 2645236.5609 | 1228118.5221 | 2645242.2319 | 1228119.5534
86 | 2645302.2822 | 1228139.6996 | 2645310.4486 | 1228145.3246
87 | 2645088.0376 | 1227715.3833 | 2645095.6232 | 1227702.7117
88 | 2645095.6232 | 1227702.7117 | 2645096.4503 | 1227701.33
89 | 2645314.8192 | 1228148.3351 | 2645310.4486 | 1228145.3246
90 | 2645545.5207 | 1228054.0709 | 2645540.8707 | 1228036.7895
91 | 2645545.5207 | 1228054.0709 | 2645545.8028 | 1228055.1197
92 | 2645540.8707 | 1228036.7895 | 2645540.4877 | 1228035.3663
93 | 2645553.5361 | 1228083.8599 | 2645545.8028 | 1228055.1197
94 | 2645535.3462 | 1228021.4011 | 2645537.0546 | 1228022.607 | 2645540.4877 | 1228035.3663
95 | 2645553.5361 | 1228083.8599 | 2645547.975 | 1228086.7414 | 2645536.3104 | 1228089.5611
96 | 2645553.5361 | 1228083.8599 | 2645567.674 | 1228081.9011
97 | 2645519.7675 | 1228025.4578 | 2645533.8063 | 1228020.3141 | 2645535.3462 | 1228021.4011
98 | 2645519.7675 | 1228025.4578 | 2645501.8858 | 1228032.0095
99 | 2645332.0394 | 1227575.5216 | 2645332.3874 | 1227579.5823 | 2645330.8876 | 1227584.4739 | 2645317.1888 | 1227600.7522
100 | 2645332.0394 | 1227575.5216 | 2645345.5315 | 1227576.058
101 | 2645306.1535 | 1227613.8656 | 2645317.1888 | 1227600.7522
102 | 2645306.1535 | 1227613.8656 | 2645293.5498 | 1227628.8425
103 | 2645477.9014 | 1228040.7972 | 2645500.0126 | 1228032.6958
104 | 2645500.0126 | 1228032.6958 | 2645501.8858 | 1228032.0095
105 | 2645282.3131 | 1227642.1951 | 2645293.5498 | 1227628.8425
106 | 2645269.7367 | 1227657.1397 | 2645282.3131 | 1227642.1951
107 | 2645269.7367 | 1227657.1397 | 2645253.8944 | 1227675.9651
108 | 2645422.7021 | 1228548.2214 | 2645421.4497 | 1228552.3522 | 2645420.0018 | 1228557.2213
109 | 2645417.9037 | 1228564.277 | 2645420.0018 | 1228557.2213
110 | 2645417.0394 | 1228572.2864 | 2645417.9037 | 1228564.277 | 2645417.9037 | 1228564.277
111 | 2645420.6418 | 1228619.4654 | 2645418.7961 | 1228608.1554 | 2645417.0394 | 1228572.2864 | 2645417.0394 | 1228572.2864
112 | 2645420.6418 | 1228619.4654 | 2645399.7939 | 1228634.8869
113 | 2645420.6418 | 1228619.4654 | 2645423.6149 | 1228625.0138
114 | 2645465.2741 | 1228699.8476 | 2645470.6377 | 1228708.2492
115 | 2645455.8861 | 1228685.1418 | 2645465.2741 | 1228699.8476
116 | 2645470.6377 | 1228708.2492 | 2645476.8342 | 1228717.9555 | 2645485.1832 | 1228723.923 | 2645507.5833 | 1228729.3804
117 | 2645455.8861 | 1228685.1418 | 2645423.6149 | 1228625.0138
118 | 2645455.8861 | 1228685.1418 | 2645447.021 | 1228688.1983 | 2645427.5403 | 1228695.9408
119 | 2645423.6149 | 1228625.0138 | 2645380.8611 | 1228656.7296 | 2645368.3945 | 1228664.1058 | 2645357.4944 | 1228671.9025
120 | 2645406.6656 | 1228723.7727 | 2645401.3327 | 1228710.3412 | 2645401.3575 | 1228707.0949 | 2645402.9971 | 1228705.6954 | 2645427.5403 | 1228695.9408

## bus_geodata
| x | y | coords
0 | 2645743.099 | 1228432.0947
1 | 2645765.8697 | 1228424.9656
2 | 2645718.9876 | 1228441.4165
3 | 2645783.5475 | 1228419.4311
4 | 2645667.942 | 1228462.271
5 | 2645541.5697 | 1228325.6515
6 | 2645633.428 | 1228485.2428
7 | 2645450.8283 | 1228235.9495
8 | 2645652.7271 | 1228474.4232
9 | 2645442.606 | 1228513.2177
10 | 2645256.7628 | 1227258.4318
11 | 2645263.7119 | 1227400.905
12 | 2645180.5496 | 1227423.921
13 | 2645265.1837 | 1227426.8187
14 | 2645230.5206 | 1227912.2243
15 | 2645235.1461 | 1228009.6992
16 | 2645240.6608 | 1227691.6906
17 | 2645145.9023 | 1227459.1145
18 | 2645104.5962 | 1227449.7613
19 | 2645265.523 | 1227432.7941
20 | 2645086.1945 | 1227467.3678
21 | 2644917.7203 | 1227262.9392
22 | 2645299.0578 | 1227397.7052
23 | 2645262.7473 | 1227461.5305
24 | 2644895.9114 | 1227261.0453
25 | 2644884.1988 | 1227284.9892
26 | 2645309.8638 | 1227402.8254
27 | 2645255.5266 | 1227490.6312
28 | 2645329.971 | 1227412.3528
29 | 2645237.9892 | 1227532.8355
30 | 2645198.3488 | 1227532.6157
31 | 2645212.2922 | 1227543.1407
32 | 2645224.9749 | 1227552.1819
33 | 2645192.6386 | 1227589.2893
34 | 2645230.4526 | 1227544.0391
35 | 2645181.595 | 1227601.6164
36 | 2645193.0374 | 1227606.5903
37 | 2645149.9611 | 1227630.9909
38 | 2645278.9675 | 1227511.9952
39 | 2645277.278 | 1227540.457
40 | 2645313.662 | 1227492.3215
41 | 2645295.6809 | 1227502.5178
42 | 2645074.5272 | 1227629.1444
43 | 2645058.59 | 1227638.9188
44 | 2645132.6537 | 1227647.0622
45 | 2645116.9703 | 1227667.7406
46 | 2645114.9799 | 1227670.3649
47 | 2645106.9679 | 1227683.7607
48 | 2645292.0856 | 1227504.5565
49 | 2645299.1285 | 1227550.6669
50 | 2645285.1274 | 1227583.1582
51 | 2645223.148 | 1227596.2243
52 | 2645280.0153 | 1228059.312
53 | 2645237.3194 | 1228055.498
54 | 2645399.6753 | 1228031.1916
55 | 2645435.6861 | 1228056.2645
56 | 2645238.6847 | 1228084.215
57 | 2645435.3596 | 1228068.1214
58 | 2645451.4594 | 1228050.4853
59 | 2645251.942 | 1228088.574
60 | 2645433.1855 | 1228079.7377
61 | 2645452.1812 | 1228050.2209
62 | 2645268.8427 | 1228101.616
63 | 2645430.4093 | 1228219.8979
64 | 2645444.3624 | 1228230.8652
65 | 2645389.4774 | 1228187.7157
66 | 2645380.0916 | 1228182.4631
67 | 2645397.1648 | 1228168.51
68 | 2645385.7493 | 1228229.3909
69 | 2645370.0666 | 1228176.5302
70 | 2645398.017 | 1228166.3809
71 | 2645335.6373 | 1228159.2458
72 | 2645412.039 | 1228123.5702
73 | 2645286.4551 | 1228122.5686
74 | 2645317.6194 | 1228119.0149
75 | 2645278.9822 | 1228122.5423
76 | 2645296.7106 | 1228133.803
77 | 2645242.2319 | 1228119.5534
78 | 2645302.2822 | 1228139.6996
79 | 2645236.5609 | 1228118.5221
80 | 2645088.0376 | 1227715.3833
81 | 2645095.6232 | 1227702.7117
82 | 2645096.4503 | 1227701.33
83 | 2645314.8192 | 1228148.3351
84 | 2645310.4486 | 1228145.3246
85 | 2645545.5207 | 1228054.0709
86 | 2645540.8707 | 1228036.7895
87 | 2645545.8028 | 1228055.1197
88 | 2645540.4877 | 1228035.3663
89 | 2645553.5361 | 1228083.8599
90 | 2645535.3462 | 1228021.4011
91 | 2645536.3104 | 1228089.5611
92 | 2645567.674 | 1228081.9011
93 | 2645519.7675 | 1228025.4578
94 | 2645332.0394 | 1227575.5216
95 | 2645317.1888 | 1227600.7522
96 | 2645345.5315 | 1227576.058
97 | 2645369.5896 | 1228121.5222
98 | 2645306.1535 | 1227613.8656
99 | 2645418.3644 | 1228114.2718
100 | 2645456.8501 | 1228108.7691
101 | 2645477.9014 | 1228040.7972
102 | 2645500.0126 | 1228032.6958
103 | 2645501.8858 | 1228032.0095
104 | 2645293.5498 | 1227628.8425
105 | 2645282.3131 | 1227642.1951
106 | 2645269.7367 | 1227657.1397
107 | 2645253.8944 | 1227675.9651
108 | 2645422.7021 | 1228548.2214
109 | 2645420.0018 | 1228557.2213
110 | 2645417.9037 | 1228564.277
111 | 2645417.0394 | 1228572.2864
112 | 2645420.6418 | 1228619.4654
113 | 2645465.2741 | 1228699.8476
114 | 2645470.6377 | 1228708.2492
115 | 2645455.8861 | 1228685.1418
116 | 2645507.5833 | 1228729.3804
117 | 2645423.6149 | 1228625.0138
118 | 2645427.5403 | 1228695.9408
119 | 2645357.4944 | 1228671.9025
120 | 2645406.6656 | 1228723.7727
121 | 2645399.7939 | 1228634.8869
122 | 2645229.4159 | 1227888.0899

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97048 | -0.20804 | 0.0022308 | 0.00055908
1 | 0.97023 | -0.20982 | 0.0047149 | 0.0011817
2 | 0.97083 | -0.20551 | 0 | 0
3 | 0.97017 | -0.21027 | 0.0023013 | 0.00057677
4 | 0.97158 | -0.20012 | 0 | 0
5 | 0.977 | -0.1611 | 0 | 0
6 | 0.97228 | -0.19505 | 0 | 0
7 | 0.9803 | -0.13758 | 0.0013632 | 0.00034166
8 | 0.97184 | -0.1982 | 0.0042374 | 0.001062
9 | 0.97115 | -0.20326 | 0.00046643 | 0.0001169
10 | 0.97258 | -0.19316 | 0.0080685 | 0.0020222
11 | 0.97428 | -0.18094 | 0 | 0
12 | 0.97344 | -0.18703 | 0 | 0
13 | 0.97484 | -0.1769 | 0.0011864 | 0.00029733
14 | 1 | 0 | -0.20536 | -0.051807
15 | 0.99463 | -0.037002 | 0.00072 | 0.00018045
16 | 0.99068 | -0.064591 | 0.0019263 | 0.00048277
17 | 0.97339 | -0.18738 | 0.00066674 | 0.0001671
18 | 0.97272 | -0.19218 | 0.0014818 | 0.00037138
19 | 0.97498 | -0.1759 | 0 | 0
20 | 0.97269 | -0.19242 | 0.0008728 | 0.00021875
21 | 0.97131 | -0.20239 | 0.0029692 | 0.00074416
22 | 0.97447 | -0.17954 | 0 | 0
23 | 0.97595 | -0.16893 | 0.0019649 | 0.00049246
24 | 0.97129 | -0.20255 | 0 | 0
25 | 0.97126 | -0.20274 | 0.00067043 | 0.00016803
26 | 0.97435 | -0.18042 | 0.0025688 | 0.00064379
27 | 0.97704 | -0.16107 | 0.0014761 | 0.00036994
28 | 0.9742 | -0.18146 | 0.0044313 | 0.0011106
29 | 0.97881 | -0.14845 | 0 | 0
30 | 0.97766 | -0.15667 | 0.0010917 | 0.0002736
31 | 0.97769 | -0.15647 | 0.0028955 | 0.00072568
32 | 0.97778 | -0.15582 | 0 | 0
33 | 0.97623 | -0.16691 | 0.0058567 | 0.0014678
34 | 0.97814 | -0.15321 | 0.0082554 | 0.002069
35 | 0.97585 | -0.16963 | 0 | 0
36 | 0.97578 | -0.17016 | 0.0011769 | 0.00029495
37 | 0.97511 | -0.17494 | 0.0012657 | 0.00031721
38 | 0.97846 | -0.15095 | 0.0011794 | 0.00029557
39 | 0.98073 | -0.13479 | 0.0028509 | 0.0007145
40 | 0.9783 | -0.15207 | 0.0017306 | 0.00043374
41 | 0.97836 | -0.1517 | 0.0008576 | 0.00021494
42 | 0.97463 | -0.17843 | 0.00027029 | 6.774e-05
43 | 0.9746 | -0.17861 | 0.00092439 | 0.00023168
44 | 0.97475 | -0.17753 | 0 | 0
45 | 0.9744 | -0.18005 | 0.00079406 | 0.00019901
46 | 0.97436 | -0.18035 | 0.0022845 | 0.00057255
47 | 0.97422 | -0.18136 | 0.0023522 | 0.00058952
48 | 0.97837 | -0.15158 | 0.0014298 | 0.00035835
49 | 0.98195 | -0.1261 | 0.0036537 | 0.00091569
50 | 0.98327 | -0.11669 | 0 | 0
51 | 0.97565 | -0.1711 | 0.0027818 | 0.00069719
52 | 0.99211 | -0.054477 | 0.00014934 | 3.7428e-05
53 | 0.99212 | -0.054411 | 0 | 0
54 | 0.97149 | -0.20054 | 0.010722 | 0.0026871
55 | 0.97233 | -0.19448 | 0 | 0
56 | 0.99055 | -0.065358 | 0 | 0
57 | 0.97297 | -0.18989 | 0.0018858 | 0.00047264
58 | 0.97169 | -0.19908 | 0.0062249 | 0.0015601
59 | 0.98979 | -0.070683 | 0.00035784 | 8.9683e-05
60 | 0.97364 | -0.18505 | 0.0035544 | 0.00089082
61 | 0.97167 | -0.19925 | 0.0069664 | 0.001746
62 | 0.98862 | -0.078848 | 0.00026952 | 6.7548e-05
63 | 0.98078 | -0.13412 | 0.0011997 | 0.00030068
64 | 0.98052 | -0.13597 | 0.0011223 | 0.00028127
65 | 0.98132 | -0.13029 | 0 | 0
66 | 0.98177 | -0.1271 | 0 | 0
67 | 0.98066 | -0.13494 | 0.0037538 | 0.00094079
68 | 0.98145 | -0.12941 | 0.0047222 | 0.0011835
69 | 0.98229 | -0.12344 | 0.0035593 | 0.00089205
70 | 0.98046 | -0.1364 | 0.0044896 | 0.0011252
71 | 0.98406 | -0.11089 | 0.0026244 | 0.00065773
72 | 0.97671 | -0.16308 | 0 | 0
73 | 0.98713 | -0.089287 | 0 | 0
74 | 0.98705 | -0.089877 | 0.0017773 | 0.00044544
75 | 0.98709 | -0.089591 | 0.0015752 | 0.00039478
76 | 0.98635 | -0.0948 | 0.0019638 | 0.00049216
77 | 0.98696 | -0.090497 | 0.00094147 | 0.00023595
78 | 0.98594 | -0.097689 | 0.00092681 | 0.00023228
79 | 0.98695 | -0.090582 | 0.0014419 | 0.00036137
80 | 0.97408 | -0.18233 | 0.00075857 | 0.00019012
81 | 0.9741 | -0.18221 | 0.0013144 | 0.00032943
82 | 0.97411 | -0.18218 | 0.0017354 | 0.00043493
83 | 0.98518 | -0.10304 | 0.0042026 | 0.0010533
84 | 0.98544 | -0.10119 | 0.0017437 | 0.00043702
85 | 0.97011 | -0.21052 | 0.00092194 | 0.00023106
86 | 0.97019 | -0.20989 | 0.0011818 | 0.0002962
87 | 0.9701 | -0.21055 | 0.0010551 | 0.00026443
88 | 0.9702 | -0.20982 | 0.0013877 | 0.00034779
89 | 0.97004 | -0.21098 | 0 | 0
90 | 0.97034 | -0.20886 | 0.0013169 | 0.00033006
91 | 0.97003 | -0.21109 | 0.00057115 | 0.00014314
92 | 0.97003 | -0.2111 | 0.00079051 | 0.00019812
93 | 0.97051 | -0.20757 | 0.00093526 | 0.0002344
94 | 0.98493 | -0.10497 | 0 | 0
95 | 0.98603 | -0.097209 | 0.0014632 | 0.0003667
96 | 0.98489 | -0.10529 | 0.0023303 | 0.00058403
97 | 0.97639 | -0.16537 | 0.0051462 | 0.0012897
98 | 0.98666 | -0.092767 | 0.0018388 | 0.00046084
99 | 0.97598 | -0.16833 | 0.0024989 | 0.00062628
100 | 0.97623 | -0.16655 | 0.0069903 | 0.0017519
101 | 0.97116 | -0.20294 | 0.0015629 | 0.00039169
102 | 0.97077 | -0.20573 | 0.0021495 | 0.00053871
103 | 0.97074 | -0.20592 | 0.00086173 | 0.00021597
104 | 0.9874 | -0.087578 | 0.0015871 | 0.00039777
105 | 0.98807 | -0.082863 | 0.0018969 | 0.00047542
106 | 0.98884 | -0.077468 | 0.0018247 | 0.00045732
107 | 0.98983 | -0.07053 | 0.0021996 | 0.00055127
108 | 0.97094 | -0.20478 | 0.00014911 | 3.7371e-05
109 | 0.9709 | -0.20512 | 5.1067e-05 | 1.2799e-05
110 | 0.97086 | -0.20538 | 0.00012071 | 3.0253e-05
111 | 0.97082 | -0.20566 | 0.00040866 | 0.00010242
112 | 0.97063 | -0.20707 | 0 | 0
113 | 0.97042 | -0.20858 | 0.00036462 | 9.1382e-05
114 | 0.97042 | -0.20861 | 8.8509e-05 | 2.2183e-05
115 | 0.97044 | -0.20844 | 0 | 0
116 | 0.9704 | -0.20874 | 0.00027117 | 6.7963e-05
117 | 0.97061 | -0.20721 | 0 | 0
118 | 0.9704 | -0.20875 | 0.00072449 | 0.00018158
119 | 0.97056 | -0.2076 | 0.00045102 | 0.00011304
120 | 0.97038 | -0.20887 | 0.00023477 | 5.8838e-05
121 | 0.97061 | -0.20725 | 0.00064791 | 0.00016238
122 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0070181 | 0.0017586 | -0.0070164 | -0.0017583 | 1.724e-06 | 3.6834e-07 | 0.010761 | 0.010761 | 0.010761 | 0.97048 | -0.20804 | 0.97023 | -0.20982 | 3.9855
1 | -0.0092489 | -0.0023177 | 0.0092521 | 0.0023186 | 3.2459e-06 | 9.2871e-07 | 0.014181 | 0.014181 | 0.014181 | 0.97048 | -0.20804 | 0.97083 | -0.20551 | 5.2522
2 | 0.0023015 | 0.0005766 | -0.0023013 | -0.00057677 | 1.4401e-07 | -1.7336e-07 | 0.0035296 | 0.0035297 | 0.0035297 | 0.97023 | -0.20982 | 0.97017 | -0.21027 | 1.3073
3 | -0.0092521 | -0.0023186 | 0.009259 | 0.0023206 | 6.9022e-06 | 1.974e-06 | 0.014181 | 0.014181 | 0.014181 | 0.97083 | -0.20551 | 0.97158 | -0.20012 | 5.2522
4 | -0.009259 | -0.0023206 | 0.0092615 | 0.0023213 | 2.4589e-06 | 7.0297e-07 | 0.014181 | 0.014181 | 0.014181 | 0.97158 | -0.20012 | 0.97184 | -0.1982 | 5.2521
5 | 0.017572 | 0.0044064 | -0.01749 | -0.0043771 | 8.2309e-05 | 2.9362e-05 | 0.026764 | 0.026765 | 0.026765 | 0.977 | -0.1611 | 0.97228 | -0.19505 | 9.9129
6 | -0.017572 | -0.0044064 | 0.01763 | 0.0044269 | 5.7446e-05 | 2.048e-05 | 0.026764 | 0.026763 | 0.026764 | 0.977 | -0.1611 | 0.9803 | -0.13758 | 9.9126
7 | 0.013505 | 0.0033853 | -0.013499 | -0.0033833 | 5.8978e-06 | 1.9941e-06 | 0.020668 | 0.020669 | 0.020669 | 0.97228 | -0.19505 | 0.97184 | -0.1982 | 7.655
8 | 0.003985 | 0.00099176 | -0.0039806 | -0.00099243 | 4.4733e-06 | -6.6859e-07 | 0.0060964 | 0.0060972 | 0.0060972 | 0.97228 | -0.19505 | 0.97115 | -0.20326 | 2.2582
9 | -0.018993 | -0.0047686 | 0.018997 | 0.0047701 | 4.2669e-06 | 1.5374e-06 | 0.028833 | 0.028833 | 0.028833 | 0.9803 | -0.13758 | 0.98052 | -0.13597 | 10.6788
10 | 0.0035141 | 0.00087553 | -0.0035134 | -0.00087575 | 7.3232e-07 | -2.1943e-07 | 0.0053825 | 0.0053827 | 0.0053827 | 0.97115 | -0.20326 | 0.97094 | -0.20478 | 1.9936
11 | -0.0080685 | -0.0020222 | 0.0080822 | 0.0020256 | 1.3664e-05 | 3.4691e-06 | 0.012345 | 0.012344 | 0.012345 | 0.97258 | -0.19316 | 0.97428 | -0.18094 | 4.5721
12 | 0.0066761 | 0.0016683 | -0.0066705 | -0.0016672 | 5.5963e-06 | 1.0788e-06 | 0.010195 | 0.010195 | 0.010195 | 0.97428 | -0.18094 | 0.97344 | -0.18703 | 3.7759
13 | -0.014758 | -0.003694 | 0.014767 | 0.0036968 | 8.2275e-06 | 2.841e-06 | 0.022539 | 0.022539 | 0.022539 | 0.97428 | -0.18094 | 0.97484 | -0.1769 | 8.3476
14 | 0.00066677 | 0.0001665 | -0.00066674 | -0.0001671 | 3.2008e-08 | -6.0161e-07 | 0.001019 | 0.0010192 | 0.0010192 | 0.97344 | -0.18703 | 0.97339 | -0.18738 | 0.3775
15 | 0.0060037 | 0.0015007 | -0.0059995 | -0.0015001 | 4.2597e-06 | 6.3125e-07 | 0.009176 | 0.0091764 | 0.0091764 | 0.97344 | -0.18703 | 0.97272 | -0.19218 | 3.3987
16 | -0.015953 | -0.0039941 | 0.015955 | 0.0039949 | 2.2142e-06 | 7.77e-07 | 0.024349 | 0.024349 | 0.024349 | 0.97484 | -0.1769 | 0.97498 | -0.1759 | 9.0183
17 | 0.11577 | 0.029336 | -0.11517 | -0.029108 | 0.00060317 | 0.00022817 | 0.17238 | 0.17239 | 0.17239 | 1 | 0 | 0.99463 | -0.037002 | 21.2821
18 | 0.088789 | 0.022471 | -0.087987 | -0.022171 | 0.00080251 | 0.00030005 | 0.1322 | 0.1322 | 0.1322 | 1 | 0 | 0.99068 | -0.064591 | 16.321
19 | 0.11445 | 0.028927 | -0.11417 | -0.028821 | 0.00027987 | 0.00010586 | 0.17131 | 0.17131 | 0.17131 | 0.99463 | -0.037002 | 0.99212 | -0.054411 | 21.1492
20 | 0.086061 | 0.021688 | -0.085989 | -0.021662 | 7.1479e-05 | 2.6699e-05 | 0.12931 | 0.12931 | 0.12931 | 0.99068 | -0.064591 | 0.98983 | -0.07053 | 15.9638
21 | 0.00087283 | 0.00021844 | -0.0008728 | -0.00021875 | 2.8344e-08 | -3.0539e-07 | 0.0013351 | 0.0013352 | 0.0013352 | 0.97272 | -0.19218 | 0.97269 | -0.19242 | 0.49452
22 | 0.0036448 | 0.00091029 | -0.0036397 | -0.00091159 | 5.125e-06 | -1.3043e-06 | 0.0055745 | 0.0055757 | 0.0055757 | 0.97272 | -0.19218 | 0.97131 | -0.20239 | 2.0651
23 | 0.007005 | 0.0017553 | -0.0070015 | -0.0017545 | 3.5325e-06 | 7.4131e-07 | 0.010691 | 0.010691 | 0.010691 | 0.97498 | -0.1759 | 0.97447 | -0.17954 | 3.9597
24 | -0.02296 | -0.0057502 | 0.022982 | 0.0057583 | 2.2143e-05 | 8.1556e-06 | 0.03504 | 0.03504 | 0.03504 | 0.97498 | -0.1759 | 0.97595 | -0.16893 | 12.9779
25 | 0.00067047 | 0.00016743 | -0.00067045 | -0.0001677 | 1.4613e-08 | -2.692e-07 | 0.0010269 | 0.001027 | 0.001027 | 0.97131 | -0.20239 | 0.97129 | -0.20255 | 0.38038
26 | 0.0070015 | 0.0017545 | -0.0070007 | -0.0017543 | 8.5289e-07 | 1.7908e-07 | 0.010691 | 0.010691 | 0.010691 | 0.97447 | -0.17954 | 0.97435 | -0.18042 | 3.9597
27 | -0.024947 | -0.0062508 | 0.024974 | 0.0062608 | 2.7148e-05 | 1.0066e-05 | 0.038036 | 0.038036 | 0.038036 | 0.97595 | -0.16893 | 0.97704 | -0.16107 | 14.0875
28 | 0.00067045 | 0.0001677 | -0.00067043 | -0.00016803 | 1.7546e-08 | -3.2315e-07 | 0.001027 | 0.0010271 | 0.0010271 | 0.97129 | -0.20255 | 0.97126 | -0.20274 | 0.38042
29 | 0.0044319 | 0.0011105 | -0.0044313 | -0.0011106 | 6.3604e-07 | -3.2451e-08 | 0.0067683 | 0.0067684 | 0.0067684 | 0.97435 | -0.18042 | 0.9742 | -0.18146 | 2.5068
30 | -0.02645 | -0.0066308 | 0.026497 | 0.006648 | 4.6314e-05 | 1.7239e-05 | 0.040284 | 0.040284 | 0.040284 | 0.97704 | -0.16107 | 0.97881 | -0.14845 | 14.92
31 | 0.0051997 | 0.0013024 | -0.0051979 | -0.0013023 | 1.7966e-06 | 1.1203e-07 | 0.0079045 | 0.0079047 | 0.0079047 | 0.97881 | -0.14845 | 0.97846 | -0.15095 | 2.9277
32 | -0.065543 | -0.01644 | 0.065667 | 0.016487 | 0.00012443 | 4.6845e-05 | 0.099645 | 0.099645 | 0.099645 | 0.97881 | -0.14845 | 0.98073 | -0.13479 | 18.4528
33 | 0.033847 | 0.0084896 | -0.033824 | -0.0084812 | 2.231e-05 | 8.4111e-06 | 0.051457 | 0.051457 | 0.051457 | 0.97881 | -0.14845 | 0.97814 | -0.15321 | 19.0582
34 | -0.0010917 | -0.0002736 | 0.0010917 | 0.0002734 | 3.0134e-08 | -2.0777e-07 | 0.0016616 | 0.0016615 | 0.0016616 | 0.97766 | -0.15667 | 0.97769 | -0.15647 | 0.6154
35 | -0.0039872 | -0.00099908 | 0.0039876 | 0.00099902 | 3.579e-07 | -5.7685e-08 | 0.0060684 | 0.0060683 | 0.0060684 | 0.97769 | -0.15647 | 0.97778 | -0.15582 | 2.2475
36 | 0.021572 | 0.0054097 | -0.021539 | -0.0053976 | 3.3108e-05 | 1.2117e-05 | 0.03283 | 0.03283 | 0.03283 | 0.97778 | -0.15582 | 0.97623 | -0.16691 | 12.1594
37 | -0.02556 | -0.0064088 | 0.025569 | 0.0064122 | 9.2659e-06 | 3.4407e-06 | 0.038898 | 0.038898 | 0.038898 | 0.97778 | -0.15582 | 0.97814 | -0.15321 | 14.4068
38 | 0.015682 | 0.0039298 | -0.015676 | -0.0039277 | 5.9008e-06 | 2.0627e-06 | 0.023903 | 0.023903 | 0.023903 | 0.97623 | -0.16691 | 0.97585 | -0.16963 | 8.8531
39 | 0.0039593 | 0.00099183 | -0.003959 | -0.00099187 | 2.8625e-07 | -4.7133e-08 | 0.0060372 | 0.0060372 | 0.0060372 | 0.97585 | -0.16963 | 0.97578 | -0.17016 | 2.236
40 | 0.011717 | 0.0029359 | -0.011708 | -0.0029331 | 8.5985e-06 | 2.7682e-06 | 0.017866 | 0.017866 | 0.017866 | 0.97585 | -0.16963 | 0.97511 | -0.17494 | 6.6172
41 | 0.0027822 | 0.00069692 | -0.0027818 | -0.00069719 | 3.6352e-07 | -2.6441e-07 | 0.0042425 | 0.0042427 | 0.0042427 | 0.97578 | -0.17016 | 0.97565 | -0.1711 | 1.5714
42 | 0.010443 | 0.0026159 | -0.010439 | -0.0026148 | 3.7423e-06 | 1.1448e-06 | 0.015935 | 0.015935 | 0.015935 | 0.97511 | -0.17494 | 0.97475 | -0.17753 | 5.9019
43 | 0.0040186 | 0.0010067 | -0.0040182 | -0.0010068 | 3.5144e-07 | -5.4226e-08 | 0.0061112 | 0.0061112 | 0.0061112 | 0.97846 | -0.15095 | 0.97837 | -0.15158 | 2.2634
44 | -0.068518 | -0.017201 | 0.068601 | 0.017233 | 8.281e-05 | 3.123e-05 | 0.10397 | 0.10397 | 0.10397 | 0.98073 | -0.13479 | 0.98195 | -0.1261 | 19.2538
45 | -0.0017306 | -0.00043374 | 0.0017307 | 0.00043351 | 8.9373e-08 | -2.2519e-07 | 0.0026323 | 0.0026322 | 0.0026323 | 0.9783 | -0.15207 | 0.97836 | -0.1517 | 0.97494
46 | -0.0025883 | -0.00064845 | 0.0025884 | 0.00064841 | 3.9966e-08 | -3.653e-08 | 0.0039366 | 0.0039366 | 0.0039366 | 0.97836 | -0.1517 | 0.97837 | -0.15158 | 1.458
47 | 0.00092442 | 0.00023145 | -0.00092439 | -0.00023168 | 2.3279e-08 | -2.2445e-07 | 0.0014113 | 0.0014114 | 0.0014114 | 0.97463 | -0.17843 | 0.9746 | -0.17861 | 0.52273
48 | -0.0011947 | -0.00029919 | 0.0011949 | 0.00029836 | 1.4728e-07 | -8.2777e-07 | 0.0018239 | 0.0018236 | 0.0018239 | 0.97463 | -0.17843 | 0.97475 | -0.17753 | 0.67553
49 | 0.009244 | 0.0023164 | -0.0092408 | -0.0023155 | 3.2249e-06 | 9.1697e-07 | 0.014111 | 0.014112 | 0.014112 | 0.97475 | -0.17753 | 0.9744 | -0.18005 | 5.2265
50 | 0.0084468 | 0.0021165 | -0.0084464 | -0.0021164 | 3.4196e-07 | 9.0498e-08 | 0.012899 | 0.012899 | 0.012899 | 0.9744 | -0.18005 | 0.97436 | -0.18035 | 4.7774
51 | 0.0061619 | 0.0015438 | -0.006161 | -0.0015437 | 8.6249e-07 | 1.3734e-07 | 0.0094101 | 0.0094102 | 0.0094102 | 0.97436 | -0.18035 | 0.97422 | -0.18136 | 3.4853
52 | 0.0038088 | 0.00095419 | -0.0038084 | -0.00095428 | 4.3243e-07 | -8.8618e-08 | 0.0058175 | 0.0058175 | 0.0058175 | 0.97422 | -0.18136 | 0.97411 | -0.18218 | 2.1546
53 | -0.072255 | -0.018148 | 0.072349 | 0.018183 | 9.4593e-05 | 3.4941e-05 | 0.10951 | 0.10951 | 0.10951 | 0.98195 | -0.1261 | 0.98327 | -0.11669 | 13.5194
54 | -0.072349 | -0.018183 | 0.072468 | 0.018227 | 0.00011832 | 4.37e-05 | 0.10951 | 0.10951 | 0.10951 | 0.98327 | -0.11669 | 0.98493 | -0.10497 | 13.5193
55 | -0.00014934 | -3.7428e-05 | 0.00014934 | 3.6874e-05 | 1.3443e-09 | -5.5444e-07 | 0.00022399 | 0.00022379 | 0.00022399 | 0.99211 | -0.054477 | 0.99212 | -0.054411 | 0.082959
56 | 0.11402 | 0.028784 | -0.11384 | -0.028718 | 0.00017506 | 6.6219e-05 | 0.17109 | 0.17109 | 0.17109 | 0.99212 | -0.054411 | 0.99055 | -0.065358 | 21.1217
57 | -0.010722 | -0.0026871 | 0.010731 | 0.0026899 | 8.998e-06 | 2.7982e-06 | 0.016422 | 0.016422 | 0.016422 | 0.97149 | -0.20054 | 0.97233 | -0.19448 | 6.0824
58 | -0.036689 | -0.0091975 | 0.036712 | 0.0092063 | 2.3334e-05 | 8.8275e-06 | 0.056148 | 0.056148 | 0.056148 | 0.97233 | -0.19448 | 0.97297 | -0.18989 | 20.7957
59 | 0.025958 | 0.0065076 | -0.025942 | -0.0065014 | 1.6543e-05 | 6.1545e-06 | 0.039726 | 0.039726 | 0.039726 | 0.97233 | -0.19448 | 0.97169 | -0.19908 | 14.7134
60 | 0.11384 | 0.028718 | -0.11376 | -0.028686 | 8.4964e-05 | 3.214e-05 | 0.17109 | 0.17109 | 0.17109 | 0.99055 | -0.065358 | 0.98979 | -0.070683 | 21.1217
61 | -0.038598 | -0.009679 | 0.038624 | 0.0096888 | 2.5894e-05 | 9.8114e-06 | 0.059033 | 0.059032 | 0.059033 | 0.97297 | -0.18989 | 0.97364 | -0.18505 | 21.8639
62 | 0.019717 | 0.0049413 | -0.019716 | -0.0049411 | 4.3734e-07 | 1.5868e-07 | 0.030194 | 0.030194 | 0.030194 | 0.97169 | -0.19908 | 0.97167 | -0.19925 | 11.1828
63 | 0.1134 | 0.028596 | -0.11327 | -0.028547 | 0.00012961 | 4.9025e-05 | 0.17055 | 0.17055 | 0.17055 | 0.98979 | -0.070683 | 0.98862 | -0.078848 | 21.0553
64 | -0.042179 | -0.01058 | 0.042277 | 0.010617 | 9.8052e-05 | 3.7241e-05 | 0.064465 | 0.064465 | 0.064465 | 0.97364 | -0.18505 | 0.97598 | -0.16833 | 23.8758
65 | 0.01275 | 0.0031952 | -0.012743 | -0.003193 | 6.5164e-06 | 2.1672e-06 | 0.019525 | 0.019525 | 0.019525 | 0.97167 | -0.19925 | 0.97116 | -0.20294 | 7.2316
66 | 0.113 | 0.02848 | -0.11284 | -0.028417 | 0.00016491 | 6.2375e-05 | 0.17014 | 0.17014 | 0.17014 | 0.98862 | -0.078848 | 0.98713 | -0.089287 | 21.0053
67 | 0.020124 | 0.0050529 | -0.020119 | -0.0050514 | 5.1631e-06 | 1.538e-06 | 0.030536 | 0.030536 | 0.030536 | 0.98078 | -0.13412 | 0.98052 | -0.13597 | 5.6548
68 | -0.021324 | -0.0053536 | 0.021336 | 0.005356 | 1.1338e-05 | 2.3884e-06 | 0.032356 | 0.032355 | 0.032356 | 0.98078 | -0.13412 | 0.98132 | -0.13029 | 3.9946
69 | -0.086795 | -0.021821 | 0.086834 | 0.021836 | 3.8681e-05 | 1.447e-05 | 0.13164 | 0.13164 | 0.13164 | 0.98132 | -0.13029 | 0.98177 | -0.1271 | 16.2513
70 | 0.06546 | 0.016465 | -0.065417 | -0.01645 | 4.2412e-05 | 1.5529e-05 | 0.099281 | 0.099281 | 0.099281 | 0.98132 | -0.13029 | 0.98066 | -0.13494 | 12.2569
71 | 0.0047237 | 0.0011835 | -0.0047222 | -0.0011835 | 1.5137e-06 | -1.6061e-08 | 0.0071593 | 0.0071595 | 0.0071595 | 0.98177 | -0.1271 | 0.98145 | -0.12941 | 2.6517
72 | -0.091558 | -0.023019 | 0.091604 | 0.023037 | 4.6677e-05 | 1.751e-05 | 0.1388 | 0.13879 | 0.1388 | 0.98177 | -0.1271 | 0.98229 | -0.12344 | 17.1352
73 | 0.061664 | 0.015509 | -0.061651 | -0.015504 | 1.2533e-05 | 4.7916e-06 | 0.093585 | 0.093585 | 0.093585 | 0.98066 | -0.13494 | 0.98046 | -0.1364 | 34.6612
74 | -0.095164 | -0.023929 | 0.09533 | 0.023991 | 0.00016667 | 6.2638e-05 | 0.14419 | 0.14419 | 0.14419 | 0.98229 | -0.12344 | 0.98406 | -0.11089 | 17.8008
75 | 0.057162 | 0.014379 | -0.05695 | -0.014298 | 0.00021184 | 8.091e-05 | 0.086772 | 0.086772 | 0.086772 | 0.98046 | -0.1364 | 0.97671 | -0.16308 | 32.1377
76 | -0.097955 | -0.024649 | 0.098062 | 0.02469 | 0.00010751 | 4.0453e-05 | 0.14815 | 0.14815 | 0.14815 | 0.98406 | -0.11089 | 0.98518 | -0.10304 | 18.2907
77 | 0.044808 | 0.011256 | -0.044775 | -0.011243 | 3.2711e-05 | 1.2441e-05 | 0.068274 | 0.068274 | 0.068274 | 0.97671 | -0.16308 | 0.97598 | -0.16833 | 25.2868
78 | 0.0069937 | 0.0017526 | -0.0069903 | -0.0017519 | 3.3671e-06 | 7.0048e-07 | 0.010655 | 0.010655 | 0.010655 | 0.97671 | -0.16308 | 0.97623 | -0.16655 | 3.9463
79 | 0.0051478 | 0.0012898 | -0.0051462 | -0.0012897 | 1.6311e-06 | 9.5639e-08 | 0.0078425 | 0.0078427 | 0.0078427 | 0.97671 | -0.16308 | 0.97639 | -0.16537 | 2.9047
80 | 0.0017775 | 0.00044508 | -0.0017773 | -0.00044544 | 1.4499e-07 | -3.5799e-07 | 0.0026792 | 0.0026794 | 0.0026794 | 0.98713 | -0.089287 | 0.98705 | -0.089877 | 0.99236
81 | 0.003959 | 0.00099164 | -0.0039588 | -0.00099167 | 1.6607e-07 | -3.1656e-08 | 0.0059677 | 0.0059677 | 0.0059677 | 0.98713 | -0.089287 | 0.98709 | -0.089591 | 2.2103
82 | 0.1071 | 0.026981 | -0.10702 | -0.026949 | 8.2525e-05 | 3.1157e-05 | 0.1615 | 0.1615 | 0.1615 | 0.98713 | -0.089287 | 0.98635 | -0.0948 | 19.9378
83 | 0.0023837 | 0.0005969 | -0.0023834 | -0.00059726 | 2.9887e-07 | -3.5918e-07 | 0.0035931 | 0.0035933 | 0.0035933 | 0.98709 | -0.089591 | 0.98696 | -0.090497 | 1.3309
84 | 0.10506 | 0.026457 | -0.10501 | -0.026441 | 4.2409e-05 | 1.6001e-05 | 0.15853 | 0.15853 | 0.15853 | 0.98635 | -0.0948 | 0.98594 | -0.097689 | 19.572
85 | 0.0014419 | 0.0003613 | -0.0014419 | -0.00036137 | 1.6997e-08 | -6.7122e-08 | 0.0021739 | 0.0021739 | 0.0021739 | 0.98696 | -0.090497 | 0.98695 | -0.090582 | 0.80515
86 | 0.10409 | 0.026209 | -0.10404 | -0.02619 | 5.0928e-05 | 1.9208e-05 | 0.15713 | 0.15713 | 0.15713 | 0.98594 | -0.097689 | 0.98544 | -0.10119 | 19.3994
87 | -0.00075857 | -0.00019012 | 0.00075858 | 0.00018994 | 1.2374e-08 | -1.7908e-07 | 0.0011588 | 0.0011587 | 0.0011588 | 0.97408 | -0.18233 | 0.9741 | -0.18221 | 0.42918
88 | -0.002073 | -0.00051936 | 0.002073 | 0.00051935 | 1.0076e-08 | -1.6171e-08 | 0.0031666 | 0.0031666 | 0.0031666 | 0.9741 | -0.18221 | 0.97411 | -0.18218 | 1.1728
89 | -0.10227 | -0.025743 | 0.10229 | 0.025753 | 2.635e-05 | 9.932e-06 | 0.1545 | 0.1545 | 0.1545 | 0.98518 | -0.10304 | 0.98544 | -0.10119 | 19.0743
90 | -0.0033388 | -0.00083601 | 0.0033391 | 0.00083591 | 2.9285e-07 | -1.0834e-07 | 0.005121 | 0.0051209 | 0.005121 | 0.97011 | -0.21052 | 0.97019 | -0.20989 | 1.8967
91 | 0.0024169 | 0.00060496 | -0.0024169 | -0.00060497 | 9.3123e-09 | -9.8276e-09 | 0.0037069 | 0.0037069 | 0.0037069 | 0.97011 | -0.21052 | 0.9701 | -0.21055 | 1.3729
92 | -0.0045209 | -0.0011321 | 0.004521 | 0.0011321 | 4.4212e-08 | -1.1955e-09 | 0.0069335 | 0.0069335 | 0.0069335 | 0.97019 | -0.20989 | 0.9702 | -0.20982 | 2.568
93 | 0.0013618 | 0.00034053 | -0.0013617 | -0.00034087 | 8.1013e-08 | -3.3628e-07 | 0.0020885 | 0.0020886 | 0.0020886 | 0.9701 | -0.21055 | 0.97004 | -0.21098 | 0.77357
94 | -0.0059087 | -0.0014799 | 0.0059094 | 0.00148 | 7.842e-07 | 1.126e-07 | 0.0090619 | 0.0090618 | 0.0090619 | 0.9702 | -0.20982 | 0.97034 | -0.20886 | 3.3562
95 | 0.00057116 | 0.00014292 | -0.00057115 | -0.00014314 | 8.7474e-09 | -2.221e-07 | 0.00087606 | 0.00087614 | 0.00087614 | 0.97004 | -0.21098 | 0.97003 | -0.21109 | 0.3245
96 | 0.00079053 | 0.00019795 | -0.00079051 | -0.00019812 | 1.3096e-08 | -1.7116e-07 | 0.0012126 | 0.0012126 | 0.0012126 | 0.97004 | -0.21098 | 0.97003 | -0.2111 | 0.44913
97 | -0.0072264 | -0.0018101 | 0.0072277 | 0.0018103 | 1.2901e-06 | 2.8817e-07 | 0.011081 | 0.011081 | 0.011081 | 0.97034 | -0.20886 | 0.97051 | -0.20757 | 4.1042
98 | -0.0081629 | -0.0020447 | 0.0081648 | 0.0020452 | 1.8613e-06 | 4.8051e-07 | 0.012515 | 0.012515 | 0.012515 | 0.97051 | -0.20757 | 0.97074 | -0.20592 | 4.6353
99 | -0.074798 | -0.018811 | 0.074879 | 0.018841 | 8.0957e-05 | 2.9973e-05 | 0.11303 | 0.11303 | 0.11303 | 0.98493 | -0.10497 | 0.98603 | -0.097209 | 13.9539
100 | 0.0023304 | 0.0005839 | -0.0023303 | -0.00058403 | 1.0444e-07 | -1.3167e-07 | 0.0035207 | 0.0035208 | 0.0035208 | 0.98493 | -0.10497 | 0.98489 | -0.10529 | 1.304
101 | -0.076342 | -0.019208 | 0.07639 | 0.019225 | 4.7337e-05 | 1.755e-05 | 0.11523 | 0.11523 | 0.11523 | 0.98603 | -0.097209 | 0.98666 | -0.092767 | 14.2264
102 | -0.078228 | -0.019686 | 0.078285 | 0.019707 | 5.6698e-05 | 2.1056e-05 | 0.11801 | 0.11801 | 0.11801 | 0.98666 | -0.092767 | 0.9874 | -0.087578 | 14.5688
103 | 0.011181 | 0.0028013 | -0.011176 | -0.0028 | 4.3122e-06 | 1.3673e-06 | 0.017131 | 0.017131 | 0.017131 | 0.97116 | -0.20294 | 0.97077 | -0.20573 | 6.3447
104 | 0.0090268 | 0.0022613 | -0.0090265 | -0.0022612 | 2.3831e-07 | 6.6993e-08 | 0.013836 | 0.013836 | 0.013836 | 0.97077 | -0.20573 | 0.97074 | -0.20592 | 5.1245
105 | -0.079872 | -0.020105 | 0.079925 | 0.020124 | 5.2618e-05 | 1.9568e-05 | 0.1204 | 0.1204 | 0.1204 | 0.9874 | -0.087578 | 0.98807 | -0.082863 | 14.864
106 | -0.081822 | -0.0206 | 0.081883 | 0.020623 | 6.172e-05 | 2.2987e-05 | 0.12326 | 0.12325 | 0.12326 | 0.98807 | -0.082863 | 0.98884 | -0.077468 | 15.2167
107 | -0.083708 | -0.02108 | 0.083789 | 0.02111 | 8.125e-05 | 3.0302e-05 | 0.126 | 0.126 | 0.126 | 0.98884 | -0.077468 | 0.98983 | -0.07053 | 15.5556
108 | 0.0033643 | 0.00083838 | -0.0033641 | -0.00083843 | 1.5576e-07 | -5.6298e-08 | 0.0051542 | 0.0051542 | 0.0051542 | 0.97094 | -0.20478 | 0.9709 | -0.20512 | 1.909
109 | 0.0033131 | 0.00082564 | -0.003313 | -0.00082568 | 1.1835e-07 | -4.551e-08 | 0.005076 | 0.005076 | 0.005076 | 0.9709 | -0.20512 | 0.97086 | -0.20538 | 1.88
110 | 0.0031922 | 0.00079543 | -0.0031921 | -0.00079548 | 1.2025e-07 | -5.3364e-08 | 0.004891 | 0.004891 | 0.004891 | 0.97086 | -0.20538 | 0.97082 | -0.20566 | 1.8115
111 | 0.0027835 | 0.00069306 | -0.0027829 | -0.00069344 | 5.3764e-07 | -3.7884e-07 | 0.0042647 | 0.0042649 | 0.0042649 | 0.97082 | -0.20566 | 0.97063 | -0.20707 | 1.5796
112 | 0.00064793 | 0.00016207 | -0.00064791 | -0.00016238 | 1.5963e-08 | -3.1437e-07 | 0.00099318 | 0.0009933 | 0.0009933 | 0.97063 | -0.20707 | 0.97061 | -0.20725 | 0.36789
113 | 0.002135 | 0.00053137 | -0.002135 | -0.00053144 | 4.202e-08 | -6.1594e-08 | 0.0032717 | 0.0032717 | 0.0032717 | 0.97063 | -0.20707 | 0.97061 | -0.20721 | 1.2117
114 | 0.00035969 | 8.9471e-05 | -0.00035969 | -8.9593e-05 | 1.8905e-09 | -1.2242e-07 | 0.00055129 | 0.00055134 | 0.00055134 | 0.97042 | -0.20858 | 0.97042 | -0.20861 | 0.2042
115 | -0.00072431 | -0.00018085 | 0.00072432 | 0.00018064 | 1.3422e-08 | -2.1039e-07 | 0.0011104 | 0.0011103 | 0.0011104 | 0.97042 | -0.20858 | 0.97044 | -0.20844 | 0.41125
116 | 0.00027118 | 6.7411e-05 | -0.00027117 | -6.7963e-05 | 4.8349e-09 | -5.5203e-07 | 0.00041562 | 0.00041582 | 0.00041582 | 0.97042 | -0.20861 | 0.9704 | -0.20874 | 0.15401
117 | -0.0016836 | -0.00042013 | 0.0016839 | 0.00041939 | 2.8345e-07 | -7.3379e-07 | 0.0025809 | 0.0025806 | 0.0025809 | 0.97044 | -0.20844 | 0.97061 | -0.20721 | 0.95589
118 | 0.00095931 | 0.00023948 | -0.00095926 | -0.00023984 | 4.0948e-08 | -3.5909e-07 | 0.0014706 | 0.0014707 | 0.0014707 | 0.97044 | -0.20844 | 0.9704 | -0.20875 | 0.54472
119 | 0.00045104 | 0.00011204 | -0.00045102 | -0.00011304 | 2.4191e-08 | -9.9325e-07 | 0.00069112 | 0.00069148 | 0.00069148 | 0.97061 | -0.20721 | 0.97056 | -0.2076 | 0.2561
120 | 0.00023477 | 5.8268e-05 | -0.00023477 | -5.8838e-05 | 3.7392e-09 | -5.7011e-07 | 0.00035979 | 0.00036 | 0.00036 | 0.9704 | -0.20875 | 0.97038 | -0.20887 | 0.13333

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.20536 | 0.051807

## res_load
| p_mw | q_mvar
0 | 0.0022308 | 0.00055908
1 | 0.0047149 | 0.0011817
2 | 0.0023013 | 0.00057677
3 | 0.0013632 | 0.00034166
4 | 0.0042374 | 0.001062
5 | 0.00046643 | 0.0001169
6 | 0.0080685 | 0.0020222
7 | 0.0011864 | 0.00029733
8 | 0.00072 | 0.00018045
9 | 0.0019263 | 0.00048277
10 | 0.00066674 | 0.0001671
11 | 0.0014818 | 0.00037138
12 | 0.0008728 | 0.00021875
13 | 0.0029692 | 0.00074416
14 | 0.0019649 | 0.00049246
15 | 0.00067043 | 0.00016803
16 | 0.0025688 | 0.00064379
17 | 0.0014761 | 0.00036994
18 | 0.0044313 | 0.0011106
19 | 0.0010917 | 0.0002736
20 | 0.0028955 | 0.00072568
21 | 0.0058567 | 0.0014678
22 | 0.0082554 | 0.002069
23 | 0.0011769 | 0.00029495
24 | 0.0012657 | 0.00031721
25 | 0.0011794 | 0.00029557
26 | 0.0028509 | 0.0007145
27 | 0.0017306 | 0.00043374
28 | 0.0008576 | 0.00021494
29 | 0.00027029 | 6.774e-05
30 | 0.00092439 | 0.00023168
31 | 0.00079406 | 0.00019901
32 | 0.0022845 | 0.00057255
33 | 0.0023522 | 0.00058952
34 | 0.0014298 | 0.00035835
35 | 0.0036537 | 0.00091569
36 | 0.0027818 | 0.00069719
37 | 0.00014934 | 3.7428e-05
38 | 0.010722 | 0.0026871
39 | 0.0018858 | 0.00047264
40 | 0.0062249 | 0.0015601
41 | 0.00035784 | 8.9683e-05
42 | 0.0035544 | 0.00089082
43 | 0.0069664 | 0.001746
44 | 0.00026952 | 6.7548e-05
45 | 0.0011997 | 0.00030068
46 | 0.0011223 | 0.00028127
47 | 0.0037538 | 0.00094079
48 | 0.0047222 | 0.0011835
49 | 0.0035593 | 0.00089205
50 | 0.0044896 | 0.0011252
51 | 0.0026244 | 0.00065773
52 | 0.0017773 | 0.00044544
53 | 0.0015752 | 0.00039478
54 | 0.0019638 | 0.00049216
55 | 0.00094147 | 0.00023595
56 | 0.00092681 | 0.00023228
57 | 0.0014419 | 0.00036137
58 | 0.00075857 | 0.00019012
59 | 0.0013144 | 0.00032943
60 | 0.0017354 | 0.00043493
61 | 0.0042026 | 0.0010533
62 | 0.0017437 | 0.00043702
63 | 0.00092194 | 0.00023106
64 | 0.0011818 | 0.0002962
65 | 0.0010551 | 0.00026443
66 | 0.0013877 | 0.00034779
67 | 0.0013169 | 0.00033006
68 | 0.00057115 | 0.00014314
69 | 0.00079051 | 0.00019812
70 | 0.00093526 | 0.0002344
71 | 0.0014632 | 0.0003667
72 | 0.0023303 | 0.00058403
73 | 0.0051462 | 0.0012897
74 | 0.0018388 | 0.00046084
75 | 0.0024989 | 0.00062628
76 | 0.0069903 | 0.0017519
77 | 0.0015629 | 0.00039169
78 | 0.0021495 | 0.00053871
79 | 0.00086173 | 0.00021597
80 | 0.0015871 | 0.00039777
81 | 0.0018969 | 0.00047542
82 | 0.0018247 | 0.00045732
83 | 0.0021996 | 0.00055127
84 | 0.00014911 | 3.7371e-05
85 | 5.1067e-05 | 1.2799e-05
86 | 0.00012071 | 3.0253e-05
87 | 0.00040866 | 0.00010242
88 | 0.00036462 | 9.1382e-05
89 | 8.8509e-05 | 2.2183e-05
90 | 0.00027117 | 6.7963e-05
91 | 0.00072449 | 0.00018158
92 | 0.00045102 | 0.00011304
93 | 0.00023477 | 5.8838e-05
94 | 0.00064791 | 0.00016238

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1