## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1139-13_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1139-13_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1139-13_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1139-13_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1139-13_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1139-13_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1139-13_0_4_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_1139-13_0_4_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_1139-13_0_4_node_23 | 0.4 | n |  | TRUE
9 | bus_LV_1139-13_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1139-13_0_4_node_21 | 0.4 | n |  | TRUE
11 | bus_LV_1139-13_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1139-13_0_4_node_59 | 0.4 | n |  | TRUE
13 | bus_LV_1139-13_0_4_node_63 | 0.4 | n |  | TRUE
14 | bus_LV_1139-13_0_4_node_62 | 0.4 | n |  | TRUE
15 | bus_LV_1139-13_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1139-13_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1139-13_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1139-13_0_4_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_1139-13_0_4_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_1139-13_0_4_node_60 | 0.4 | n |  | TRUE
21 | bus_LV_1139-13_0_4_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_1139-13_0_4_node_39 | 0.4 | n |  | TRUE
23 | bus_LV_1139-13_0_4_node_8 | 0.4 | n |  | TRUE
24 | bus_LV_1139-13_0_4_node_9 | 0.4 | n |  | TRUE
25 | bus_LV_1139-13_0_4_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_1139-13_0_4_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1139-13_0_4_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1139-13_0_4_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_1139-13_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1139-13_0_4_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_1139-13_0_4_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_1139-13_0_4_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_1139-13_0_4_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_1139-13_0_4_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_1139-13_0_4_node_75 | 0.4 | n |  | TRUE
36 | bus_LV_1139-13_0_4_node_74 | 0.4 | n |  | TRUE
37 | bus_LV_1139-13_0_4_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_1139-13_0_4_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_1139-13_0_4_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_1139-13_0_4_node_64 | 0.4 | n |  | TRUE
41 | bus_LV_1139-13_0_4_node_65 | 0.4 | n |  | TRUE
42 | bus_LV_1139-13_0_4_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_1139-13_0_4_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_1139-13_0_4_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_1139-13_0_4_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_1139-13_0_4_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_1139-13_0_4_node_52 | 0.4 | n |  | TRUE
48 | bus_LV_1139-13_0_4_node_51 | 0.4 | n |  | TRUE
49 | bus_LV_1139-13_0_4_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_1139-13_0_4_node_41 | 0.4 | n |  | TRUE
51 | bus_LV_1139-13_0_4_node_42 | 0.4 | n |  | TRUE
52 | bus_LV_1139-13_0_4_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_1139-13_0_4_node_44 | 0.4 | n |  | TRUE
54 | bus_LV_1139-13_0_4_node_50 | 0.4 | n |  | TRUE
55 | bus_LV_1139-13_0_4_node_57 | 0.4 | n |  | TRUE
56 | bus_LV_1139-13_0_4_node_56 | 0.4 | n |  | TRUE
57 | bus_LV_1139-13_0_4_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_1139-13_0_4_node_46 | 0.4 | n |  | TRUE
59 | bus_LV_1139-13_0_4_node_47 | 0.4 | n |  | TRUE
60 | bus_LV_1139-13_0_4_node_48 | 0.4 | n |  | TRUE
61 | bus_LV_1139-13_0_4_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_1139-13_0_4_node_71 | 0.4 | n |  | TRUE
63 | bus_LV_1139-13_0_4_node_61 | 0.4 | n |  | TRUE
64 | bus_LV_1139-13_0_4_node_70 | 0.4 | n |  | TRUE
65 | bus_LV_1139-13_0_4_node_72 | 0.4 | n |  | TRUE
66 | bus_LV_1139-13_0_4_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_1139-13_0_4_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_1139-13_0_4_node_55 | 0.4 | n |  | TRUE
69 | bus_LV_1139-13_0_4_node_58 | 0.4 | n |  | TRUE
70 | bus_LV_1139-13_0_4_node_69 | 0.4 | n |  | TRUE
71 | bus_LV_1139-13_0_4_node_82 | 0.4 | n |  | TRUE
72 | bus_LV_1139-13_0_4_node_67 | 0.4 | n |  | TRUE
73 | bus_LV_1139-13_0_4_node_77 | 0.4 | n |  | TRUE
74 | bus_LV_1139-13_0_4_node_81 | 0.4 | n |  | TRUE
75 | bus_LV_1139-13_0_4_node_66 | 0.4 | n |  | TRUE
76 | bus_LV_1139-13_0_4_node_68 | 0.4 | n |  | TRUE
77 | bus_LV_1139-13_0_4_node_78 | 0.4 | n |  | TRUE
78 | bus_LV_1139-13_0_4_node_76 | 0.4 | n |  | TRUE
79 | bus_MV_475_1_node_278 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1139-13_0_4_load_0 | 0 | 0.0046188 | 0.0011576 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1139-13_0_4_load_4 | 4 | 0.0059981 | 0.0015033 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1139-13_0_4_load_16 | 6 | 0.0024225 | 0.00060715 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1139-13_0_4_load_23 | 8 | 0.0084953 | 0.0021291 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1139-13_0_4_load_21 | 10 | 0.0090906 | 0.0022783 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1139-13_0_4_load_59 | 12 | 0.01091 | 0.0027343 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1139-13_0_4_load_63 | 13 | 0.0029111 | 0.00072959 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1139-13_0_4_load_62 | 14 | 0.0014089 | 0.00035312 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1139-13_0_4_load_13 | 15 | 0.0060695 | 0.0015212 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1139-13_0_4_load_15 | 18 | 0.0091792 | 0.0023005 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1139-13_0_4_load_8 | 23 | 0.0020494 | 0.00051363 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1139-13_0_4_load_9 | 24 | 0.0019561 | 0.00049025 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1139-13_0_4_load_27 | 28 | 0.0007359 | 0.00018443 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1139-13_0_4_load_17 | 29 | 0.002444 | 0.00061252 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1139-13_0_4_load_18 | 30 | 0.0013447 | 0.000337 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1139-13_0_4_load_20 | 31 | 0.0026938 | 0.00067513 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1139-13_0_4_load_32 | 32 | 0.0015129 | 0.00037917 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1139-13_0_4_load_31 | 33 | 0.0022052 | 0.00055266 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1139-13_0_4_load_25 | 34 | 0.0037352 | 0.00093614 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1139-13_0_4_load_75 | 35 | 0.003741 | 0.00093758 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1139-13_0_4_load_74 | 36 | 0.0010544 | 0.00026427 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1139-13_0_4_load_28 | 37 | 0.0018104 | 0.00045372 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1139-13_0_4_load_29 | 38 | 0.0037105 | 0.00092993 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1139-13_0_4_load_30 | 39 | 0.0032287 | 0.00080918 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1139-13_0_4_load_64 | 40 | 0.0087455 | 0.0021918 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1139-13_0_4_load_34 | 42 | 0.0015202 | 0.00038099 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1139-13_0_4_load_35 | 43 | 0.0058875 | 0.0014755 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1139-13_0_4_load_37 | 45 | 0.00085686 | 0.00021475 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1139-13_0_4_load_38 | 46 | 0.0040515 | 0.0010154 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1139-13_0_4_load_52 | 47 | 0.0023821 | 0.000597 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1139-13_0_4_load_51 | 48 | 0.0010935 | 0.00027405 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1139-13_0_4_load_40 | 49 | 0.0021913 | 0.0005492 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1139-13_0_4_load_41 | 50 | 0.00080939 | 0.00020285 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1139-13_0_4_load_42 | 51 | 0.0010883 | 0.00027276 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1139-13_0_4_load_43 | 52 | 0.00067847 | 0.00017004 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1139-13_0_4_load_44 | 53 | 0.0010727 | 0.00026884 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1139-13_0_4_load_50 | 54 | 0.0014567 | 0.00036508 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1139-13_0_4_load_57 | 55 | 0.0010207 | 0.0002558 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1139-13_0_4_load_45 | 57 | 0.0020469 | 0.00051299 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1139-13_0_4_load_46 | 58 | 0.00070363 | 0.00017635 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1139-13_0_4_load_47 | 59 | 0.0008019 | 0.00020097 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1139-13_0_4_load_48 | 60 | 0.0026633 | 0.00066748 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1139-13_0_4_load_71 | 62 | 0.0062502 | 0.0015664 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1139-13_0_4_load_70 | 64 | 0.00078044 | 0.0001956 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1139-13_0_4_load_72 | 65 | 0.00032581 | 8.1655e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1139-13_0_4_load_53 | 66 | 0.00051104 | 0.00012808 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1139-13_0_4_load_54 | 67 | 0.0017678 | 0.00044304 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1139-13_0_4_load_55 | 68 | 0.0017151 | 0.00042985 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1139-13_0_4_load_58 | 69 | 0.00059858 | 0.00015002 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1139-13_0_4_load_82 | 71 | 0.004271 | 0.0010704 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1139-13_0_4_load_67 | 72 | 0.00093082 | 0.00023329 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1139-13_0_4_load_81 | 74 | 0.00067579 | 0.00016937 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1139-13_0_4_load_66 | 75 | 0.00058754 | 0.00014725 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1139-13_0_4_load_68 | 76 | 0.00094816 | 0.00023763 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1139-13_0_4_load_78 | 77 | 0.0024651 | 0.0006178 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1139-13_0_4_load_76 | 78 | 0.0032822 | 0.00082259 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1139-13_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.025578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1139-13_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0039409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1139-13_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.019983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1139-13_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.023026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1139-13_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.04998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1139-13_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.022576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1139-13_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.011611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1139-13_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.016288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1139-13_0_4_line_8 | NAYY 4x150 SE | 5 | 9 | 0.066543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1139-13_0_4_line_9 | NAYY 4x150 SE | 5 | 10 | 0.0012702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1139-13_0_4_line_10 | NAYY 4x150 SE | 6 | 17 | 0.041539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1139-13_0_4_line_11 | NAYY 4x150 SE | 7 | 18 | 0.020843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1139-13_0_4_line_12 | NAYY 4x150 SE | 9 | 11 | 0.04118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1139-13_0_4_line_13 | NAYY 4x150 SE | 9 | 12 | 0.010236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1139-13_0_4_line_14 | NAYY 4x150 SE | 10 | 21 | 0.01748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1139-13_0_4_line_15 | NAYY 4x150 SE | 11 | 13 | 0.045723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1139-13_0_4_line_16 | NAYY 4x150 SE | 11 | 14 | 0.020417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1139-13_0_4_line_17 | NAYY 4x150 SE | 12 | 19 | 0.0054898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1139-13_0_4_line_18 | NAYY 4x150 SE | 14 | 22 | 0.018062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1139-13_0_4_line_19 | NAYY 4x150 SE | 15 | 16 | 0.027933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1139-13_0_4_line_20 | NAYY 4x150 SE | 16 | 17 | 0.009852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1139-13_0_4_line_21 | NAYY 4x150 SE | 16 | 23 | 0.008342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1139-13_0_4_line_22 | NAYY 4x150 SE | 19 | 20 | 0.064927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1139-13_0_4_line_23 | NAYY 4x150 SE | 20 | 35 | 0.025615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1139-13_0_4_line_24 | NAYY 4x150 SE | 20 | 36 | 0.042986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1139-13_0_4_line_25 | NAYY 4x150 SE | 21 | 34 | 0.018182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1139-13_0_4_line_26 | NAYY 4x150 SE | 22 | 47 | 0.010929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1139-13_0_4_line_27 | NAYY 4x150 SE | 22 | 44 | 0.029771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1139-13_0_4_line_28 | NAYY 4x150 SE | 23 | 24 | 0.028897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1139-13_0_4_line_29 | NAYY 4x150 SE | 24 | 25 | 0.022801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1139-13_0_4_line_30 | NAYY 4x150 SE | 25 | 26 | 0.035356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1139-13_0_4_line_31 | NAYY 4x150 SE | 25 | 27 | 0.007346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1139-13_0_4_line_32 | NAYY 4x150 SE | 26 | 28 | 0.010037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1139-13_0_4_line_33 | NAYY 4x150 SE | 27 | 29 | 0.066901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1139-13_0_4_line_34 | NAYY 4x150 SE | 28 | 37 | 0.025415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1139-13_0_4_line_35 | NAYY 4x150 SE | 29 | 30 | 0.053207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1139-13_0_4_line_36 | NAYY 4x150 SE | 30 | 31 | 0.0042439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1139-13_0_4_line_37 | NAYY 4x150 SE | 31 | 32 | 0.015907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1139-13_0_4_line_38 | NAYY 4x150 SE | 32 | 33 | 0.0050775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1139-13_0_4_line_39 | NAYY 4x150 SE | 35 | 73 | 0.029486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1139-13_0_4_line_40 | NAYY 4x150 SE | 36 | 63 | 0.04407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1139-13_0_4_line_41 | NAYY 4x150 SE | 37 | 38 | 0.030665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1139-13_0_4_line_42 | NAYY 4x150 SE | 37 | 39 | 0.015603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1139-13_0_4_line_43 | NAYY 4x150 SE | 39 | 40 | 0.035527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1139-13_0_4_line_44 | NAYY 4x150 SE | 40 | 41 | 0.035271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1139-13_0_4_line_45 | NAYY 4x150 SE | 41 | 74 | 0.014603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1139-13_0_4_line_46 | NAYY 4x150 SE | 42 | 43 | 0.01018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1139-13_0_4_line_47 | NAYY 4x150 SE | 42 | 44 | 0.013605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1139-13_0_4_line_48 | NAYY 4x150 SE | 43 | 45 | 0.0090854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1139-13_0_4_line_49 | NAYY 4x150 SE | 44 | 46 | 0.029461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1139-13_0_4_line_50 | NAYY 4x150 SE | 47 | 48 | 0.010016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1139-13_0_4_line_51 | NAYY 4x150 SE | 48 | 54 | 0.022736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1139-13_0_4_line_52 | NAYY 4x150 SE | 49 | 50 | 0.030296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1139-13_0_4_line_53 | NAYY 4x150 SE | 49 | 51 | 0.013588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1139-13_0_4_line_54 | NAYY 4x150 SE | 50 | 52 | 0.0005261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1139-13_0_4_line_55 | NAYY 4x150 SE | 51 | 53 | 0.0056246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1139-13_0_4_line_56 | NAYY 4x150 SE | 52 | 54 | 0.002563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1139-13_0_4_line_57 | NAYY 4x150 SE | 53 | 55 | 0.0054058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1139-13_0_4_line_58 | NAYY 4x150 SE | 55 | 56 | 0.017691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1139-13_0_4_line_59 | NAYY 4x150 SE | 56 | 69 | 0.020945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1139-13_0_4_line_60 | NAYY 4x150 SE | 56 | 68 | 0.024614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1139-13_0_4_line_61 | NAYY 4x150 SE | 57 | 58 | 0.036533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1139-13_0_4_line_62 | NAYY 4x150 SE | 57 | 59 | 0.049971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1139-13_0_4_line_63 | NAYY 4x150 SE | 58 | 60 | 0.019686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1139-13_0_4_line_64 | NAYY 4x150 SE | 59 | 61 | 0.017845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1139-13_0_4_line_65 | NAYY 4x150 SE | 60 | 62 | 0.14825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1139-13_0_4_line_66 | NAYY 4x150 SE | 61 | 63 | 0.088684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1139-13_0_4_line_67 | NAYY 4x150 SE | 62 | 64 | 0.011414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1139-13_0_4_line_68 | NAYY 4x150 SE | 64 | 65 | 0.012528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1139-13_0_4_line_69 | NAYY 4x150 SE | 66 | 67 | 0.010465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1139-13_0_4_line_70 | NAYY 4x150 SE | 66 | 68 | 0.01886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1139-13_0_4_line_71 | NAYY 4x150 SE | 69 | 70 | 0.0061781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1139-13_0_4_line_72 | NAYY 4x150 SE | 70 | 71 | 0.041982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1139-13_0_4_line_73 | NAYY 4x150 SE | 70 | 72 | 0.018649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1139-13_0_4_line_74 | NAYY 4x150 SE | 72 | 75 | 0.0081095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1139-13_0_4_line_75 | NAYY 4x150 SE | 73 | 77 | 0.015751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1139-13_0_4_line_76 | NAYY 4x150 SE | 73 | 78 | 0.014692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1139-13_0_4_line_77 | NAYY 4x150 SE | 75 | 76 | 0.014682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1139-13_0_4_trafo_7 | 0.25 MVA 20/0.4 kV | 79 | 11 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2634650.0673 | 1230755.5403 | 2634646.2043 | 1230762.1218 | 2634644.3087 | 1230766.3912 | 2634640.0367 | 1230778.9599
1 | 2634638.7684 | 1230782.6912 | 2634640.0367 | 1230778.9599
2 | 2634650.0673 | 1230755.5403 | 2634666.3127 | 1230767.242
3 | 2634638.7684 | 1230782.6912 | 2634618.3386 | 1230772.0697
4 | 2634638.7684 | 1230782.6912 | 2634628.5354 | 1230812.8057 | 2634635.1053 | 1230816.0904 | 2634638.7883 | 1230818.3131 | 2634643.7393 | 1230822.5668
5 | 2634666.3127 | 1230767.242 | 2634673.4882 | 1230766.6835 | 2634676.2213 | 1230766.855 | 2634678.8754 | 1230767.5709 | 2634685.5045 | 1230772.3903 | 2634686.8638 | 1230773.4045
6 | 2634608.0368 | 1230766.7138 | 2634618.3386 | 1230772.0697
7 | 2634638.4617 | 1230837.9789 | 2634643.7393 | 1230822.5668
8 | 2634604.7864 | 1230842.4858 | 2634617.139 | 1230846.3489 | 2634628.5354 | 1230812.8057 | 2634635.1053 | 1230816.0904 | 2634638.7883 | 1230818.3131 | 2634643.7393 | 1230822.5668
9 | 2634643.7393 | 1230822.5668 | 2634644.7032 | 1230823.3941
10 | 2634718.8271 | 1230799.868 | 2634708.4235 | 1230791.6579 | 2634696.122 | 1230780.3126 | 2634686.8638 | 1230773.4045
11 | 2634608.0368 | 1230766.7138 | 2634604.1888 | 1230773.3399 | 2634601.6108 | 1230776.4602 | 2634599.312 | 1230781.0496 | 2634596.6356 | 1230784.0218
12 | 2634608.3416 | 1230873.1808 | 2634612.5437 | 1230860.353 | 2634617.139 | 1230846.3489 | 2634604.7864 | 1230842.4858
13 | 2634604.7864 | 1230842.4858 | 2634600.3865 | 1230841.1149 | 2634601.5145 | 1230838.5977 | 2634598.8137 | 1230837.6279
14 | 2634657.967 | 1230834.7793 | 2634644.7032 | 1230823.3941
15 | 2634563.9736 | 1230869.7099 | 2634581.9674 | 1230865.9343 | 2634584.3984 | 1230865.9484 | 2634586.343 | 1230866.2488 | 2634608.3416 | 1230873.1808
16 | 2634608.3416 | 1230873.1808 | 2634601.8355 | 1230892.534
17 | 2634593.6469 | 1230835.7725 | 2634598.8137 | 1230837.6279
18 | 2634596.0801 | 1230909.6542 | 2634601.8355 | 1230892.534
19 | 2634723.1652 | 1230807.9205 | 2634718.4282 | 1230804.6353 | 2634700.3984 | 1230791.7373
20 | 2634718.8271 | 1230799.868 | 2634722.4282 | 1230803.1355 | 2634723.2145 | 1230804.6632 | 2634723.3798 | 1230806.1985 | 2634723.1652 | 1230807.9205
21 | 2634723.1652 | 1230807.9205 | 2634727.9229 | 1230811.5505 | 2634729.7811 | 1230813.0015
22 | 2634542.9857 | 1230804.7816 | 2634566.0221 | 1230828.6633 | 2634576.7654 | 1230833.184 | 2634577.7 | 1230830.0541 | 2634593.6469 | 1230835.7725
23 | 2634555.7312 | 1230782.7643 | 2634552.8327 | 1230790.1964 | 2634550.8371 | 1230793.4646 | 2634547.9633 | 1230796.6499 | 2634542.9857 | 1230804.7816
24 | 2634542.9857 | 1230804.7816 | 2634532.6058 | 1230793.7479 | 2634530.4363 | 1230782.5952 | 2634528.0195 | 1230778.8344 | 2634520.5341 | 1230769.4486
25 | 2634657.967 | 1230834.7793 | 2634674.6937 | 1230827.5389
26 | 2634596.0801 | 1230909.6542 | 2634592.6644 | 1230920.0357
27 | 2634596.0801 | 1230909.6542 | 2634620.2054 | 1230927.1941
28 | 2634729.7811 | 1230813.0015 | 2634739.6991 | 1230820.747 | 2634749.9365 | 1230828.8784 | 2634752.4189 | 1230830.959
29 | 2634769.8935 | 1230845.6052 | 2634752.4189 | 1230830.959
30 | 2634769.8935 | 1230845.6052 | 2634764.4696 | 1230861.3832 | 2634763.3549 | 1230862.911 | 2634762.1078 | 1230863.7709 | 2634760.795 | 1230864.2191 | 2634758.9024 | 1230864.0857 | 2634755.7418 | 1230863.2112 | 2634747.4731 | 1230860.35
31 | 2634775.4394 | 1230850.4406 | 2634769.8935 | 1230845.6052
32 | 2634747.4731 | 1230860.35 | 2634737.9985 | 1230857.0363
33 | 2634775.4394 | 1230850.4406 | 2634776.9693 | 1230845.2352 | 2634777.0142 | 1230844.0458 | 2634776.6802 | 1230842.8654 | 2634775.3368 | 1230840.7674 | 2634773.9709 | 1230838.647 | 2634772.1367 | 1230835.0007 | 2634770.8077 | 1230831.7243 | 2634768.8248 | 1230825.0086 | 2634763.05 | 1230803.6173 | 2634763.3678 | 1230786.3521
34 | 2634713.6736 | 1230849.7908 | 2634720.5473 | 1230851.6098 | 2634725.5547 | 1230852.6841 | 2634737.9985 | 1230857.0363
35 | 2634788.0971 | 1230771.038 | 2634782.1316 | 1230760.2132 | 2634780.0314 | 1230758.0218 | 2634777.8177 | 1230757.0972 | 2634775.9333 | 1230756.8527 | 2634773.4283 | 1230757.8276 | 2634771.3943 | 1230759.8503 | 2634768.3376 | 1230765.8138 | 2634765.5437 | 1230773.4578 | 2634763.9535 | 1230779.908 | 2634763.3829 | 1230785.5303 | 2634763.3678 | 1230786.3521
36 | 2634790.1455 | 1230774.7549 | 2634788.0971 | 1230771.038
37 | 2634790.1455 | 1230774.7549 | 2634791.9789 | 1230778.0817 | 2634797.0925 | 1230789.0568
38 | 2634799.2369 | 1230793.6593 | 2634797.0925 | 1230789.0568
39 | 2634555.7312 | 1230782.7643 | 2634562.683 | 1230784.1944 | 2634565.8259 | 1230785.5245 | 2634568.0145 | 1230786.8492 | 2634570.0453 | 1230789.2736 | 2634572.9579 | 1230792.4257 | 2634575.4394 | 1230794.1968 | 2634577.8481 | 1230795.4449 | 2634580.9165 | 1230796.5634
40 | 2634506.3468 | 1230730.001 | 2634504.5156 | 1230733.6371 | 2634507.7211 | 1230741.1492 | 2634508.5865 | 1230749.9596 | 2634514.711 | 1230762.147 | 2634520.5341 | 1230769.4486
41 | 2634713.6736 | 1230849.7908 | 2634683.0098 | 1230852.158
42 | 2634713.6736 | 1230849.7908 | 2634712.4528 | 1230865.3455
43 | 2634712.4528 | 1230865.3455 | 2634711.8655 | 1230872.8277 | 2634709.2535 | 1230883.0632 | 2634703.444 | 1230889.6668 | 2634701.701 | 1230898.1529
44 | 2634696.3395 | 1230932.6295 | 2634698.8632 | 1230906.3503 | 2634700.4196 | 1230904.3915 | 2634701.701 | 1230898.1529
45 | 2634696.3395 | 1230932.6295 | 2634695.9596 | 1230947.2279
46 | 2634631.2113 | 1230935.1913 | 2634639.4469 | 1230941.1755
47 | 2634620.2054 | 1230927.1941 | 2634631.2113 | 1230935.1913
48 | 2634646.7968 | 1230946.5162 | 2634639.4469 | 1230941.1755
49 | 2634620.2054 | 1230927.1941 | 2634632.0651 | 1230906.4281 | 2634633.4345 | 1230905.3687 | 2634635.1803 | 1230904.7007 | 2634637.1266 | 1230904.712
50 | 2634589.5338 | 1230929.5504 | 2634592.6644 | 1230920.0357
51 | 2634582.4281 | 1230951.1471 | 2634589.5338 | 1230929.5504
52 | 2634572.0218 | 1230982.8685 | 2634573.6298 | 1230977.8879 | 2634581.4626 | 1230954.0814
53 | 2634572.0218 | 1230982.8685 | 2634567.8472 | 1230995.799
54 | 2634581.627 | 1230953.5816 | 2634581.4626 | 1230954.0814
55 | 2634566.1191 | 1231001.1516 | 2634567.8472 | 1230995.799
56 | 2634582.4281 | 1230951.1471 | 2634581.627 | 1230953.5816
57 | 2634566.1191 | 1231001.1516 | 2634564.4582 | 1231006.2959
58 | 2634559.0231 | 1231023.1308 | 2634564.4582 | 1231006.2959
59 | 2634559.0231 | 1231023.1308 | 2634579.7859 | 1231025.8872
60 | 2634559.0231 | 1231023.1308 | 2634551.2409 | 1231046.4824
61 | 2634423.3659 | 1230804.3199 | 2634422.4119 | 1230809.1748 | 2634422.0096 | 1230822.4362 | 2634424.3865 | 1230840.5993
62 | 2634423.3659 | 1230804.3199 | 2634426.9769 | 1230785.9425 | 2634433.0062 | 1230755.288
63 | 2634424.3865 | 1230840.5993 | 2634425.8608 | 1230851.8654 | 2634425.7894 | 1230860.1891
64 | 2634436.45 | 1230737.7789 | 2634433.0062 | 1230755.288
65 | 2634425.7894 | 1230860.1891 | 2634353.5325 | 1230989.6421
66 | 2634436.45 | 1230737.7789 | 2634449.5964 | 1230736.721 | 2634467.1548 | 1230729.7072 | 2634498.2002 | 1230711.2535 | 2634500.8854 | 1230717.0837 | 2634504.4657 | 1230726.5769 | 2634506.3468 | 1230730.001
67 | 2634347.8435 | 1230999.5375 | 2634353.5325 | 1230989.6421
68 | 2634347.8435 | 1230999.5375 | 2634341.5995 | 1231010.3982
69 | 2634545.2779 | 1231064.3754 | 2634541.9694 | 1231074.3031
70 | 2634545.2779 | 1231064.3754 | 2634551.2409 | 1231046.4824
71 | 2634585.9102 | 1231026.7003 | 2634579.7859 | 1231025.8872
72 | 2634585.9102 | 1231026.7003 | 2634627.487 | 1231032.521
73 | 2634585.9102 | 1231026.7003 | 2634582.0675 | 1231040.2529 | 2634581.265 | 1231044.744
74 | 2634579.8384 | 1231052.727 | 2634581.265 | 1231044.744
75 | 2634580.9165 | 1230796.5634 | 2634582.5444 | 1230794.0157 | 2634588.518 | 1230786.5347 | 2634590.285 | 1230783.9216
76 | 2634580.9165 | 1230796.5634 | 2634578.5415 | 1230802.531 | 2634577.2758 | 1230805.3032 | 2634574.3397 | 1230809.6207
77 | 2634579.8384 | 1231052.727 | 2634579.8288 | 1231052.7809 | 2634578.3536 | 1231064.2238 | 2634578.1914 | 1231067.3095

## bus_geodata
| x | y | coords
0 | 2634640.0367 | 1230778.9599
1 | 2634650.0673 | 1230755.5403
2 | 2634638.7684 | 1230782.6912
3 | 2634666.3127 | 1230767.242
4 | 2634618.3386 | 1230772.0697
5 | 2634643.7393 | 1230822.5668
6 | 2634686.8638 | 1230773.4045
7 | 2634608.0368 | 1230766.7138
8 | 2634638.4617 | 1230837.9789
9 | 2634604.7864 | 1230842.4858
10 | 2634644.7032 | 1230823.3941
11 | 2634608.3416 | 1230873.1808
12 | 2634598.8137 | 1230837.6279
13 | 2634563.9736 | 1230869.7099
14 | 2634601.8355 | 1230892.534
15 | 2634700.3984 | 1230791.7373
16 | 2634723.1652 | 1230807.9205
17 | 2634718.8271 | 1230799.868
18 | 2634596.6356 | 1230784.0218
19 | 2634593.6469 | 1230835.7725
20 | 2634542.9857 | 1230804.7816
21 | 2634657.967 | 1230834.7793
22 | 2634596.0801 | 1230909.6542
23 | 2634729.7811 | 1230813.0015
24 | 2634752.4189 | 1230830.959
25 | 2634769.8935 | 1230845.6052
26 | 2634747.4731 | 1230860.35
27 | 2634775.4394 | 1230850.4406
28 | 2634737.9985 | 1230857.0363
29 | 2634763.3678 | 1230786.3521
30 | 2634788.0971 | 1230771.038
31 | 2634790.1455 | 1230774.7549
32 | 2634797.0925 | 1230789.0568
33 | 2634799.2369 | 1230793.6593
34 | 2634674.6937 | 1230827.5389
35 | 2634555.7312 | 1230782.7643
36 | 2634520.5341 | 1230769.4486
37 | 2634713.6736 | 1230849.7908
38 | 2634683.0098 | 1230852.158
39 | 2634712.4528 | 1230865.3455
40 | 2634701.701 | 1230898.1529
41 | 2634696.3395 | 1230932.6295
42 | 2634631.2113 | 1230935.1913
43 | 2634639.4469 | 1230941.1755
44 | 2634620.2054 | 1230927.1941
45 | 2634646.7968 | 1230946.5162
46 | 2634637.1266 | 1230904.712
47 | 2634592.6644 | 1230920.0357
48 | 2634589.5338 | 1230929.5504
49 | 2634572.0218 | 1230982.8685
50 | 2634581.4626 | 1230954.0814
51 | 2634567.8472 | 1230995.799
52 | 2634581.627 | 1230953.5816
53 | 2634566.1191 | 1231001.1516
54 | 2634582.4281 | 1230951.1471
55 | 2634564.4582 | 1231006.2959
56 | 2634559.0231 | 1231023.1308
57 | 2634423.3659 | 1230804.3199
58 | 2634424.3865 | 1230840.5993
59 | 2634433.0062 | 1230755.288
60 | 2634425.7894 | 1230860.1891
61 | 2634436.45 | 1230737.7789
62 | 2634353.5325 | 1230989.6421
63 | 2634506.3468 | 1230730.001
64 | 2634347.8435 | 1230999.5375
65 | 2634341.5995 | 1231010.3982
66 | 2634545.2779 | 1231064.3754
67 | 2634541.9694 | 1231074.3031
68 | 2634551.2409 | 1231046.4824
69 | 2634579.7859 | 1231025.8872
70 | 2634585.9102 | 1231026.7003
71 | 2634627.487 | 1231032.521
72 | 2634581.265 | 1231044.744
73 | 2634580.9165 | 1230796.5634
74 | 2634695.9596 | 1230947.2279
75 | 2634579.8384 | 1231052.727
76 | 2634578.1914 | 1231067.3095
77 | 2634590.285 | 1230783.9216
78 | 2634574.3397 | 1230809.6207
79 | 2634612.5437 | 1230860.353

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98373 | -0.11353 | 0.0046188 | 0.0011576
1 | 0.98217 | -0.12454 | 0 | 0
2 | 0.98399 | -0.11165 | 0 | 0
3 | 0.98095 | -0.13316 | 0 | 0
4 | 0.98349 | -0.11526 | 0.0059981 | 0.0015033
5 | 0.98847 | -0.080133 | 0 | 0
6 | 0.97958 | -0.14293 | 0.0024225 | 0.00060715
7 | 0.98333 | -0.11636 | 0 | 0
8 | 0.98827 | -0.081546 | 0.0084953 | 0.0021291
9 | 0.99648 | -0.02431 | 0 | 0
10 | 0.98845 | -0.080299 | 0.0090906 | 0.0022783
11 | 1 | 0 | -0.1604 | -0.040255
12 | 0.99597 | -0.027922 | 0.01091 | 0.0027343
13 | 0.99981 | -0.0013297 | 0.0029111 | 0.00072959
14 | 0.99892 | -0.0075247 | 0.0014089 | 0.00035312
15 | 0.97638 | -0.16573 | 0.0060695 | 0.0015212
16 | 0.97663 | -0.16396 | 0 | 0
17 | 0.97719 | -0.15992 | 0 | 0
18 | 0.98306 | -0.11833 | 0.0091792 | 0.0023005
19 | 0.99578 | -0.029258 | 0 | 0
20 | 0.99352 | -0.045089 | 0 | 0
21 | 0.98836 | -0.080966 | 0 | 0
22 | 0.99801 | -0.013939 | 0 | 0
23 | 0.97622 | -0.16685 | 0.0020494 | 0.00051363
24 | 0.9749 | -0.17628 | 0.0019561 | 0.00049025
25 | 0.97393 | -0.18326 | 0 | 0
26 | 0.97295 | -0.19031 | 0 | 0
27 | 0.97382 | -0.18405 | 0 | 0
28 | 0.97267 | -0.19231 | 0.0007359 | 0.00018443
29 | 0.97282 | -0.19125 | 0.002444 | 0.00061252
30 | 0.97222 | -0.1956 | 0.0013447 | 0.000337
31 | 0.97218 | -0.19589 | 0.0026938 | 0.00067513
32 | 0.97209 | -0.19652 | 0.0015129 | 0.00037917
33 | 0.97207 | -0.19663 | 0.0022052 | 0.00055266
34 | 0.98826 | -0.081661 | 0.0037352 | 0.00093614
35 | 0.99318 | -0.047549 | 0.003741 | 0.00093758
36 | 0.99262 | -0.051471 | 0.0010544 | 0.00026427
37 | 0.97199 | -0.19719 | 0.0018104 | 0.00045372
38 | 0.97183 | -0.19839 | 0.0037105 | 0.00092993
39 | 0.9717 | -0.19928 | 0.0032287 | 0.00080918
40 | 0.97121 | -0.20282 | 0.0087455 | 0.0021918
41 | 0.97118 | -0.20307 | 0 | 0
42 | 0.99732 | -0.018746 | 0.0015202 | 0.00038099
43 | 0.99723 | -0.019435 | 0.0058875 | 0.0014755
44 | 0.99748 | -0.017618 | 0 | 0
45 | 0.99721 | -0.019513 | 0.00085686 | 0.00021475
46 | 0.99731 | -0.018816 | 0.0040515 | 0.0010154
47 | 0.99765 | -0.016476 | 0.0023821 | 0.000597
48 | 0.99735 | -0.018562 | 0.0010935 | 0.00027405
49 | 0.9959 | -0.028709 | 0.0021913 | 0.0005492
50 | 0.99663 | -0.023614 | 0.00080939 | 0.00020285
51 | 0.99562 | -0.030696 | 0.0010883 | 0.00027276
52 | 0.99664 | -0.023521 | 0.00067847 | 0.00017004
53 | 0.99551 | -0.031458 | 0.0010727 | 0.00026884
54 | 0.99671 | -0.023052 | 0.0014567 | 0.00036508
55 | 0.99542 | -0.032131 | 0.0010207 | 0.0002558
56 | 0.99513 | -0.034153 | 0 | 0
57 | 0.98874 | -0.078809 | 0.0020469 | 0.00051299
58 | 0.98818 | -0.082818 | 0.00070363 | 0.00017635
59 | 0.98967 | -0.072288 | 0.0008019 | 0.00020097
60 | 0.98789 | -0.084838 | 0.0026633 | 0.00066748
61 | 0.99002 | -0.069816 | 0 | 0
62 | 0.98632 | -0.096023 | 0.0062502 | 0.0015664
63 | 0.99175 | -0.057552 | 0 | 0
64 | 0.9863 | -0.096153 | 0.00078044 | 0.0001956
65 | 0.98629 | -0.096195 | 0.00032581 | 8.1655e-05
66 | 0.99493 | -0.035579 | 0.00051104 | 0.00012808
67 | 0.9949 | -0.035766 | 0.0017678 | 0.00044304
68 | 0.99499 | -0.035145 | 0.0017151 | 0.00042985
69 | 0.99491 | -0.035704 | 0.00059858 | 0.00015002
70 | 0.99485 | -0.036125 | 0 | 0
71 | 0.99459 | -0.037934 | 0.004271 | 0.0010704
72 | 0.99479 | -0.036589 | 0.00093082 | 0.00023329
73 | 0.99293 | -0.049266 | 0 | 0
74 | 0.97116 | -0.20318 | 0.00067579 | 0.00016937
75 | 0.99477 | -0.036715 | 0.00058754 | 0.00014725
76 | 0.99475 | -0.036855 | 0.00094816 | 0.00023763
77 | 0.99288 | -0.049659 | 0.0024651 | 0.0006178
78 | 0.99286 | -0.049754 | 0.0032822 | 0.00082259
79 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.042037 | 0.010587 | -0.041973 | -0.010562 | 6.457e-05 | 2.451e-05 | 0.063605 | 0.063605 | 0.063605 | 0.98373 | -0.11353 | 0.98217 | -0.12454 | 23.5575
1 | -0.046656 | -0.011744 | 0.046668 | 0.011749 | 1.2254e-05 | 4.6631e-06 | 0.070592 | 0.070592 | 0.070592 | 0.98373 | -0.11353 | 0.98399 | -0.11165 | 26.1451
2 | 0.041973 | 0.010562 | -0.041922 | -0.010543 | 5.0447e-05 | 1.915e-05 | 0.063605 | 0.063605 | 0.063605 | 0.98217 | -0.12454 | 0.98095 | -0.13316 | 23.5576
3 | 0.015189 | 0.0038075 | -0.015181 | -0.0038049 | 7.5804e-06 | 2.6232e-06 | 0.022969 | 0.022969 | 0.022969 | 0.98399 | -0.11165 | 0.98349 | -0.11526 | 8.5071
4 | -0.061857 | -0.015556 | 0.06213 | 0.015661 | 0.000273 | 0.00010436 | 0.093561 | 0.093561 | 0.093561 | 0.98399 | -0.11165 | 0.98847 | -0.080133 | 34.6522
5 | 0.041922 | 0.010543 | -0.041865 | -0.010521 | 5.6994e-05 | 2.1636e-05 | 0.063605 | 0.063606 | 0.063606 | 0.98095 | -0.13316 | 0.97958 | -0.14293 | 23.5576
6 | 0.0091831 | 0.0023016 | -0.0091817 | -0.0023012 | 1.3987e-06 | 3.9063e-07 | 0.013894 | 0.013894 | 0.013894 | 0.98349 | -0.11526 | 0.98333 | -0.11636 | 5.146
7 | 0.008497 | 0.0021296 | -0.0084953 | -0.0021291 | 1.6629e-06 | 4.3084e-07 | 0.012791 | 0.012791 | 0.012791 | 0.98847 | -0.080133 | 0.98827 | -0.081546 | 4.7375
8 | -0.083454 | -0.021005 | 0.08411 | 0.021256 | 0.00065567 | 0.00025132 | 0.12566 | 0.12566 | 0.12566 | 0.98847 | -0.080133 | 0.99648 | -0.02431 | 46.541
9 | 0.012827 | 0.0032144 | -0.012827 | -0.0032143 | 2.9552e-07 | 9.738e-08 | 0.019309 | 0.019309 | 0.019309 | 0.98847 | -0.080133 | 0.98845 | -0.080299 | 7.1515
10 | 0.039443 | 0.0099141 | -0.03935 | -0.0098788 | 9.3082e-05 | 3.5279e-05 | 0.059926 | 0.059926 | 0.059926 | 0.97958 | -0.14293 | 0.97719 | -0.15992 | 22.1947
11 | 0.0091817 | 0.0023012 | -0.0091792 | -0.0023005 | 2.5107e-06 | 7.0134e-07 | 0.013894 | 0.013894 | 0.013894 | 0.98333 | -0.11636 | 0.98306 | -0.11833 | 5.146
12 | -0.1193 | -0.030089 | 0.11971 | 0.030245 | 0.00040805 | 0.00015587 | 0.17821 | 0.17821 | 0.17821 | 0.99648 | -0.02431 | 1 | 0 | 33.0022
13 | 0.035189 | 0.008833 | -0.035171 | -0.0088264 | 1.764e-05 | 6.6514e-06 | 0.052551 | 0.052551 | 0.052551 | 0.99648 | -0.02431 | 0.99597 | -0.027922 | 19.4635
14 | 0.0037359 | 0.00093595 | -0.0037356 | -0.00093604 | 3.45e-07 | -9.1346e-08 | 0.005624 | 0.005624 | 0.005624 | 0.98845 | -0.080299 | 0.98836 | -0.080966 | 2.083
15 | 0.0029116 | 0.0007292 | -0.0029111 | -0.00072959 | 5.3554e-07 | -3.9376e-07 | 0.0043324 | 0.0043326 | 0.0043326 | 1 | 0 | 0.99981 | -0.0013297 | 1.6047
16 | 0.03698 | 0.0092805 | -0.036942 | -0.0092659 | 3.8585e-05 | 1.4573e-05 | 0.055032 | 0.055032 | 0.055032 | 1 | 0 | 0.99892 | -0.0075247 | 20.3822
17 | 0.024262 | 0.0060921 | -0.024257 | -0.0060904 | 4.5019e-06 | 1.6601e-06 | 0.036252 | 0.036252 | 0.036252 | 0.99597 | -0.027922 | 0.99578 | -0.029258 | 13.4266
18 | 0.035533 | 0.0089128 | -0.035501 | -0.0089009 | 3.1579e-05 | 1.191e-05 | 0.052933 | 0.052933 | 0.052933 | 0.99892 | -0.0075247 | 0.99801 | -0.013939 | 19.6049
19 | -0.0060695 | -0.0015212 | 0.006071 | 0.0015214 | 1.4914e-06 | 2.2416e-07 | 0.0092501 | 0.0092499 | 0.0092501 | 0.97638 | -0.16573 | 0.97663 | -0.16396 | 3.4259
20 | -0.039328 | -0.0098704 | 0.03935 | 0.0098788 | 2.2077e-05 | 8.3677e-06 | 0.059926 | 0.059926 | 0.059926 | 0.97663 | -0.16396 | 0.97719 | -0.15992 | 22.1947
21 | 0.033257 | 0.008349 | -0.033243 | -0.008344 | 1.3368e-05 | 5.0371e-06 | 0.050676 | 0.050676 | 0.050676 | 0.97663 | -0.16396 | 0.97622 | -0.16685 | 18.7689
22 | 0.024257 | 0.0060904 | -0.024204 | -0.0060708 | 5.3244e-05 | 1.9636e-05 | 0.036252 | 0.036252 | 0.036252 | 0.99578 | -0.029258 | 0.99352 | -0.045089 | 13.4267
23 | 0.0094932 | 0.0023788 | -0.0094899 | -0.0023779 | 3.2311e-06 | 9.1115e-07 | 0.014218 | 0.014218 | 0.014218 | 0.99352 | -0.045089 | 0.99318 | -0.047549 | 5.2659
24 | 0.014711 | 0.003692 | -0.014698 | -0.0036876 | 1.3023e-05 | 4.4526e-06 | 0.022034 | 0.022034 | 0.022034 | 0.99352 | -0.045089 | 0.99262 | -0.051471 | 8.1609
25 | 0.0037356 | 0.00093604 | -0.0037352 | -0.00093614 | 3.5886e-07 | -9.4964e-08 | 0.005624 | 0.0056241 | 0.0056241 | 0.98836 | -0.080966 | 0.98826 | -0.081661 | 2.083
26 | 0.023176 | 0.005812 | -0.023168 | -0.005809 | 8.144e-06 | 2.9895e-06 | 0.034557 | 0.034557 | 0.034557 | 0.99801 | -0.013939 | 0.99765 | -0.016476 | 12.7989
27 | 0.012325 | 0.0030889 | -0.012319 | -0.0030869 | 6.2733e-06 | 2.024e-06 | 0.018376 | 0.018376 | 0.018376 | 0.99801 | -0.013939 | 0.99748 | -0.017618 | 6.8061
28 | 0.031194 | 0.0078304 | -0.031153 | -0.007815 | 4.0773e-05 | 1.5321e-05 | 0.047552 | 0.047552 | 0.047552 | 0.97622 | -0.16685 | 0.9749 | -0.17628 | 17.6119
29 | 0.029197 | 0.0073248 | -0.029169 | -0.0073142 | 2.8259e-05 | 1.0585e-05 | 0.044567 | 0.044567 | 0.044567 | 0.9749 | -0.17628 | 0.97393 | -0.18326 | 16.5062
30 | 0.018952 | 0.0047532 | -0.018933 | -0.0047466 | 1.8499e-05 | 6.6753e-06 | 0.028956 | 0.028957 | 0.028957 | 0.97393 | -0.18326 | 0.97295 | -0.19031 | 10.7247
31 | 0.010217 | 0.002561 | -0.010216 | -0.0025606 | 1.117e-06 | 3.3821e-07 | 0.01561 | 0.01561 | 0.01561 | 0.97393 | -0.18326 | 0.97382 | -0.18405 | 5.7816
32 | 0.018933 | 0.0047466 | -0.018928 | -0.0047447 | 5.2517e-06 | 1.8953e-06 | 0.028957 | 0.028957 | 0.028957 | 0.97295 | -0.19031 | 0.97267 | -0.19231 | 10.7247
33 | 0.010216 | 0.0025606 | -0.010206 | -0.0025575 | 1.0173e-05 | 3.0812e-06 | 0.01561 | 0.015611 | 0.015611 | 0.97382 | -0.18405 | 0.97282 | -0.19125 | 5.7817
34 | 0.018192 | 0.0045602 | -0.01818 | -0.0045558 | 1.2284e-05 | 4.4092e-06 | 0.027831 | 0.027831 | 0.027831 | 0.97267 | -0.19231 | 0.97199 | -0.19719 | 10.3078
35 | 0.0077618 | 0.001945 | -0.0077571 | -0.0019439 | 4.6798e-06 | 1.1397e-06 | 0.011872 | 0.011872 | 0.011872 | 0.97282 | -0.19125 | 0.97222 | -0.1956 | 4.3972
36 | 0.0064124 | 0.0016069 | -0.0064122 | -0.0016068 | 2.5508e-07 | 4.5485e-08 | 0.0098144 | 0.0098145 | 0.0098145 | 0.97222 | -0.1956 | 0.97218 | -0.19589 | 3.635
37 | 0.0037184 | 0.00093171 | -0.0037181 | -0.00093178 | 3.2151e-07 | -7.3556e-08 | 0.0056913 | 0.0056914 | 0.0056914 | 0.97218 | -0.19589 | 0.97209 | -0.19652 | 2.1079
38 | 0.0022052 | 0.00055262 | -0.0022052 | -0.00055266 | 3.6102e-08 | -4.906e-08 | 0.0033756 | 0.0033756 | 0.0033756 | 0.97209 | -0.19652 | 0.97207 | -0.19663 | 1.2502
39 | 0.0057489 | 0.0014403 | -0.0057476 | -0.0014401 | 1.365e-06 | 1.4351e-07 | 0.0086131 | 0.0086132 | 0.0086132 | 0.99318 | -0.047549 | 0.99293 | -0.049266 | 3.1901
40 | 0.013643 | 0.0034233 | -0.013632 | -0.0034195 | 1.1505e-05 | 3.8557e-06 | 0.020454 | 0.020454 | 0.020454 | 0.99262 | -0.051471 | 0.99175 | -0.057552 | 7.5755
41 | 0.0037111 | 0.00092979 | -0.0037105 | -0.00092993 | 6.1761e-07 | -1.4248e-07 | 0.0056812 | 0.0056813 | 0.0056813 | 0.97199 | -0.19719 | 0.97183 | -0.19839 | 2.1042
42 | 0.012658 | 0.0031723 | -0.012655 | -0.0031711 | 3.6561e-06 | 1.2128e-06 | 0.019378 | 0.019378 | 0.019378 | 0.97199 | -0.19719 | 0.9717 | -0.19928 | 7.1772
43 | 0.0094259 | 0.0023619 | -0.0094213 | -0.0023606 | 4.6189e-06 | 1.3366e-06 | 0.014434 | 0.014434 | 0.014434 | 0.9717 | -0.19928 | 0.97121 | -0.20282 | 5.346
44 | 0.00067582 | 0.00016876 | -0.0006758 | -0.00016919 | 2.359e-08 | -4.2738e-07 | 0.0010352 | 0.0010354 | 0.0010354 | 0.97121 | -0.20282 | 0.97118 | -0.20307 | 0.38347
45 | 0.0006758 | 0.00016919 | -0.00067579 | -0.00016937 | 9.7692e-09 | -1.7694e-07 | 0.0010354 | 0.0010354 | 0.0010354 | 0.97118 | -0.20307 | 0.97116 | -0.20318 | 0.3835
46 | 0.006745 | 0.0016903 | -0.0067443 | -0.0016902 | 6.4334e-07 | 1.1461e-07 | 0.010064 | 0.010064 | 0.010064 | 0.99732 | -0.018746 | 0.99723 | -0.019435 | 3.7272
47 | -0.0082651 | -0.0020713 | 0.0082664 | 0.0020716 | 1.2909e-06 | 3.1896e-07 | 0.012332 | 0.012332 | 0.012332 | 0.99732 | -0.018746 | 0.99748 | -0.017618 | 4.5673
48 | 0.00085687 | 0.00021463 | -0.00085686 | -0.00021475 | 9.2677e-09 | -1.1497e-07 | 0.0012785 | 0.0012786 | 0.0012786 | 0.99723 | -0.019435 | 0.99721 | -0.019513 | 0.47355
49 | 0.0040522 | 0.0010153 | -0.0040515 | -0.0010154 | 6.7174e-07 | -1.2613e-07 | 0.0060448 | 0.0060449 | 0.0060449 | 0.99748 | -0.017618 | 0.99731 | -0.018816 | 2.2389
50 | 0.020786 | 0.005212 | -0.02078 | -0.0052098 | 6.0081e-06 | 2.1801e-06 | 0.031004 | 0.031004 | 0.031004 | 0.99765 | -0.016476 | 0.99735 | -0.018562 | 11.483
51 | 0.019687 | 0.0049358 | -0.019674 | -0.0049314 | 1.224e-05 | 4.4112e-06 | 0.029373 | 0.029373 | 0.029373 | 0.99735 | -0.018562 | 0.99671 | -0.023052 | 10.8788
52 | -0.016717 | -0.0041888 | 0.016729 | 0.0041929 | 1.1793e-05 | 4.1414e-06 | 0.024977 | 0.024977 | 0.024977 | 0.9959 | -0.028709 | 0.99663 | -0.023614 | 9.2506
53 | 0.014525 | 0.0036396 | -0.014521 | -0.0036382 | 3.9935e-06 | 1.3592e-06 | 0.021703 | 0.021703 | 0.021703 | 0.9959 | -0.028709 | 0.99562 | -0.030696 | 8.038
54 | -0.017538 | -0.0043957 | 0.017538 | 0.0043958 | 2.2509e-07 | 7.9718e-08 | 0.026185 | 0.026185 | 0.026185 | 0.99663 | -0.023614 | 0.99664 | -0.023521 | 9.6982
55 | 0.013433 | 0.0033654 | -0.013432 | -0.003365 | 1.4146e-06 | 4.7094e-07 | 0.020076 | 0.020076 | 0.020076 | 0.99562 | -0.030696 | 0.99551 | -0.031458 | 7.4356
56 | -0.018217 | -0.0045659 | 0.018218 | 0.0045663 | 1.1831e-06 | 4.2162e-07 | 0.027198 | 0.027198 | 0.027198 | 0.99664 | -0.023521 | 0.99671 | -0.023052 | 10.0733
57 | 0.012359 | 0.0030961 | -0.012358 | -0.0030958 | 1.1511e-06 | 3.7245e-07 | 0.018473 | 0.018473 | 0.018473 | 0.99551 | -0.031458 | 0.99542 | -0.032131 | 6.8418
58 | 0.011337 | 0.00284 | -0.011334 | -0.002839 | 3.1704e-06 | 9.8949e-07 | 0.016947 | 0.016947 | 0.016947 | 0.99542 | -0.032131 | 0.99513 | -0.034153 | 6.2767
59 | 0.0073393 | 0.0018384 | -0.0073378 | -0.0018381 | 1.574e-06 | 3.3334e-07 | 0.010974 | 0.010974 | 0.010974 | 0.99513 | -0.034153 | 0.99491 | -0.035704 | 4.0645
60 | 0.0039947 | 0.0010006 | -0.0039941 | -0.0010007 | 5.4798e-07 | -1.0898e-07 | 0.005973 | 0.0059731 | 0.0059731 | 0.99513 | -0.034153 | 0.99499 | -0.035145 | 2.2123
61 | 0.010744 | 0.0026924 | -0.010738 | -0.0026905 | 5.9595e-06 | 1.8238e-06 | 0.016168 | 0.016169 | 0.016169 | 0.98874 | -0.078809 | 0.98818 | -0.082818 | 5.9884
62 | -0.01279 | -0.0032054 | 0.012802 | 0.0032092 | 1.1553e-05 | 3.802e-06 | 0.019249 | 0.019249 | 0.019249 | 0.98874 | -0.078809 | 0.98967 | -0.072288 | 7.1292
63 | 0.010034 | 0.0025142 | -0.010031 | -0.0025134 | 2.8043e-06 | 8.2644e-07 | 0.015109 | 0.015109 | 0.015109 | 0.98818 | -0.082818 | 0.98789 | -0.084838 | 5.596
64 | -0.013604 | -0.0034101 | 0.013608 | 0.0034117 | 4.6586e-06 | 1.5624e-06 | 0.020454 | 0.020454 | 0.020454 | 0.98967 | -0.072288 | 0.99002 | -0.069816 | 7.5757
65 | 0.0073678 | 0.0018459 | -0.0073564 | -0.0018434 | 1.1394e-05 | 2.4871e-06 | 0.011098 | 0.011098 | 0.011098 | 0.98789 | -0.084838 | 0.98632 | -0.096023 | 4.1105
66 | -0.013608 | -0.0034117 | 0.013632 | 0.0034195 | 2.3152e-05 | 7.7622e-06 | 0.020454 | 0.020454 | 0.020454 | 0.99002 | -0.069816 | 0.99175 | -0.057552 | 7.5756
67 | 0.0011063 | 0.00027696 | -0.0011063 | -0.00027709 | 1.9838e-08 | -1.3804e-07 | 0.0016689 | 0.0016689 | 0.0016689 | 0.98632 | -0.096023 | 0.9863 | -0.096153 | 0.61812
68 | 0.00032581 | 8.1496e-05 | -0.00032581 | -8.1655e-05 | 1.8886e-09 | -1.5915e-07 | 0.00049149 | 0.00049155 | 0.00049155 | 0.9863 | -0.096153 | 0.98629 | -0.096195 | 0.18205
69 | 0.0017678 | 0.00044292 | -0.0017678 | -0.00044304 | 4.5645e-08 | -1.1834e-07 | 0.0026439 | 0.0026439 | 0.0026439 | 0.99493 | -0.035579 | 0.9949 | -0.035766 | 0.97923
70 | -0.0022788 | -0.000571 | 0.002279 | 0.00057081 | 1.367e-07 | -1.9237e-07 | 0.0034082 | 0.0034081 | 0.0034082 | 0.99493 | -0.035579 | 0.99499 | -0.035145 | 1.2623
71 | 0.0067392 | 0.0016881 | -0.0067388 | -0.001688 | 3.9163e-07 | 7.0401e-08 | 0.010079 | 0.010079 | 0.010079 | 0.99491 | -0.035704 | 0.99485 | -0.036125 | 3.733
72 | 0.0042721 | 0.0010703 | -0.004271 | -0.0010704 | 1.0696e-06 | -1.336e-07 | 0.0063897 | 0.0063898 | 0.0063898 | 0.99485 | -0.036125 | 0.99459 | -0.037934 | 2.3666
73 | 0.0024667 | 0.00061771 | -0.0024666 | -0.00061789 | 1.584e-07 | -1.8121e-07 | 0.0036893 | 0.0036894 | 0.0036894 | 0.99485 | -0.036125 | 0.99479 | -0.036589 | 1.3665
74 | 0.0015357 | 0.0003846 | -0.0015357 | -0.0003847 | 2.6702e-08 | -9.5012e-08 | 0.0022971 | 0.0022971 | 0.0022971 | 0.99479 | -0.036589 | 0.99477 | -0.036715 | 0.85079
75 | 0.0024652 | 0.00061765 | -0.0024651 | -0.0006178 | 1.3414e-07 | -1.5213e-07 | 0.0036943 | 0.0036944 | 0.0036944 | 0.99293 | -0.049266 | 0.99288 | -0.049659 | 1.3683
76 | 0.0032824 | 0.00082248 | -0.0032822 | -0.00082259 | 2.2182e-07 | -1.047e-07 | 0.0049189 | 0.004919 | 0.004919 | 0.99293 | -0.049266 | 0.99286 | -0.049754 | 1.8219
77 | 0.00094817 | 0.00023745 | -0.00094816 | -0.00023763 | 1.8429e-08 | -1.8352e-07 | 0.0014183 | 0.0014183 | 0.0014183 | 0.99477 | -0.036715 | 0.99475 | -0.036855 | 0.5253

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.1604 | 0.040255

## res_load
| p_mw | q_mvar
0 | 0.0046188 | 0.0011576
1 | 0.0059981 | 0.0015033
2 | 0.0024225 | 0.00060715
3 | 0.0084953 | 0.0021291
4 | 0.0090906 | 0.0022783
5 | 0.01091 | 0.0027343
6 | 0.0029111 | 0.00072959
7 | 0.0014089 | 0.00035312
8 | 0.0060695 | 0.0015212
9 | 0.0091792 | 0.0023005
10 | 0.0020494 | 0.00051363
11 | 0.0019561 | 0.00049025
12 | 0.0007359 | 0.00018443
13 | 0.002444 | 0.00061252
14 | 0.0013447 | 0.000337
15 | 0.0026938 | 0.00067513
16 | 0.0015129 | 0.00037917
17 | 0.0022052 | 0.00055266
18 | 0.0037352 | 0.00093614
19 | 0.003741 | 0.00093758
20 | 0.0010544 | 0.00026427
21 | 0.0018104 | 0.00045372
22 | 0.0037105 | 0.00092993
23 | 0.0032287 | 0.00080918
24 | 0.0087455 | 0.0021918
25 | 0.0015202 | 0.00038099
26 | 0.0058875 | 0.0014755
27 | 0.00085686 | 0.00021475
28 | 0.0040515 | 0.0010154
29 | 0.0023821 | 0.000597
30 | 0.0010935 | 0.00027405
31 | 0.0021913 | 0.0005492
32 | 0.00080939 | 0.00020285
33 | 0.0010883 | 0.00027276
34 | 0.00067847 | 0.00017004
35 | 0.0010727 | 0.00026884
36 | 0.0014567 | 0.00036508
37 | 0.0010207 | 0.0002558
38 | 0.0020469 | 0.00051299
39 | 0.00070363 | 0.00017635
40 | 0.0008019 | 0.00020097
41 | 0.0026633 | 0.00066748
42 | 0.0062502 | 0.0015664
43 | 0.00078044 | 0.0001956
44 | 0.00032581 | 8.1655e-05
45 | 0.00051104 | 0.00012808
46 | 0.0017678 | 0.00044304
47 | 0.0017151 | 0.00042985
48 | 0.00059858 | 0.00015002
49 | 0.004271 | 0.0010704
50 | 0.00093082 | 0.00023329
51 | 0.00067579 | 0.00016937
52 | 0.00058754 | 0.00014725
53 | 0.00094816 | 0.00023763
54 | 0.0024651 | 0.0006178
55 | 0.0032822 | 0.00082259

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1