## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1139-16_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1139-16_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1139-16_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1139-16_0_3_node_41 | 0.4 | n |  | TRUE
4 | bus_LV_1139-16_0_3_node_16 | 0.4 | n |  | TRUE
5 | bus_LV_1139-16_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1139-16_0_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1139-16_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1139-16_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1139-16_0_3_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_1139-16_0_3_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_1139-16_0_3_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_1139-16_0_3_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_1139-16_0_3_node_40 | 0.4 | n |  | TRUE
14 | bus_LV_1139-16_0_3_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_1139-16_0_3_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_1139-16_0_3_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1139-16_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1139-16_0_3_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1139-16_0_3_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1139-16_0_3_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1139-16_0_3_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_1139-16_0_3_node_43 | 0.4 | n |  | TRUE
23 | bus_LV_1139-16_0_3_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1139-16_0_3_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_1139-16_0_3_node_42 | 0.4 | n |  | TRUE
26 | bus_LV_1139-16_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1139-16_0_3_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_1139-16_0_3_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1139-16_0_3_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_1139-16_0_3_node_48 | 0.4 | n |  | TRUE
31 | bus_LV_1139-16_0_3_node_47 | 0.4 | n |  | TRUE
32 | bus_LV_1139-16_0_3_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_1139-16_0_3_node_39 | 0.4 | n |  | TRUE
34 | bus_LV_1139-16_0_3_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_1139-16_0_3_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_1139-16_0_3_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_1139-16_0_3_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_1139-16_0_3_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_1139-16_0_3_node_50 | 0.4 | n |  | TRUE
40 | bus_LV_1139-16_0_3_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_1139-16_0_3_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_1139-16_0_3_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_1139-16_0_3_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_1139-16_0_3_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_1139-16_0_3_node_45 | 0.4 | n |  | TRUE
46 | bus_LV_1139-16_0_3_node_46 | 0.4 | n |  | TRUE
47 | bus_MV_475_1_node_14 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1139-16_0_3_load_0 | 0 | 0.0038667 | 0.00096907 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1139-16_0_3_load_41 | 3 | 0.001719 | 0.00043083 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1139-16_0_3_load_16 | 4 | 0.0017096 | 0.00042848 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1139-16_0_3_load_4 | 5 | 0.0038141 | 0.0009559 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1139-16_0_3_load_5 | 6 | 0.0052112 | 0.0013061 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1139-16_0_3_load_6 | 7 | 0.0079572 | 0.0019943 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1139-16_0_3_load_7 | 8 | 0.0029 | 0.00072682 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1139-16_0_3_load_17 | 10 | 0.0025407 | 0.00063675 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1139-16_0_3_load_18 | 11 | 0.0020754 | 0.00052013 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1139-16_0_3_load_13 | 12 | 0.002076 | 0.0005203 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1139-16_0_3_load_14 | 14 | 0.0020225 | 0.00050689 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1139-16_0_3_load_24 | 15 | 0.0041624 | 0.0010432 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1139-16_0_3_load_8 | 16 | 0.0038551 | 0.00096618 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1139-16_0_3_load_9 | 17 | 0.010779 | 0.0027014 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1139-16_0_3_load_10 | 18 | 0.0016888 | 0.00042325 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1139-16_0_3_load_11 | 19 | 0.013292 | 0.0033314 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1139-16_0_3_load_25 | 21 | 0.011447 | 0.0028689 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1139-16_0_3_load_43 | 22 | 0.0032583 | 0.0008166 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1139-16_0_3_load_21 | 23 | 0.0034484 | 0.00086426 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1139-16_0_3_load_42 | 25 | 0.0033117 | 0.00083 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1139-16_0_3_load_19 | 26 | 0.0013469 | 0.00033756 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1139-16_0_3_load_23 | 27 | 0.0020521 | 0.00051431 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1139-16_0_3_load_22 | 28 | 0.0024624 | 0.00061713 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1139-16_0_3_load_20 | 29 | 0.0018182 | 0.0004557 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1139-16_0_3_load_39 | 33 | 0.016938 | 0.004245 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1139-16_0_3_load_28 | 34 | 0.0021983 | 0.00055094 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1139-16_0_3_load_29 | 35 | 0.0016383 | 0.00041061 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1139-16_0_3_load_30 | 36 | 0.0017674 | 0.00044294 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1139-16_0_3_load_31 | 37 | 0.0021331 | 0.0005346 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1139-16_0_3_load_50 | 39 | 0.002459 | 0.00061628 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1139-16_0_3_load_37 | 40 | 0.013527 | 0.0033903 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1139-16_0_3_load_33 | 41 | 0.0072742 | 0.0018231 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1139-16_0_3_load_34 | 42 | 0.0042465 | 0.0010643 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1139-16_0_3_load_35 | 43 | 0.0055694 | 0.0013958 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1139-16_0_3_load_44 | 44 | 0.0070596 | 0.0017693 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1139-16_0_3_load_45 | 45 | 0.0050917 | 0.0012761 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1139-16_0_3_load_46 | 46 | 0.0048894 | 0.0012254 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1139-16_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.060082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1139-16_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.055903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1139-16_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.045734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1139-16_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.021075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1139-16_0_3_line_4 | NAYY 4x150 SE | 4 | 14 | 0.02813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1139-16_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.0026911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1139-16_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.020034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1139-16_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.016203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1139-16_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.028296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1139-16_0_3_line_9 | NAYY 4x150 SE | 8 | 13 | 0.036969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1139-16_0_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.029186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1139-16_0_3_line_11 | NAYY 4x150 SE | 9 | 11 | 0.010725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1139-16_0_3_line_12 | NAYY 4x150 SE | 9 | 12 | 0.024099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1139-16_0_3_line_13 | NAYY 4x150 SE | 10 | 29 | 0.00425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1139-16_0_3_line_14 | NAYY 4x150 SE | 11 | 30 | 0.02836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1139-16_0_3_line_15 | NAYY 4x150 SE | 12 | 14 | 0.025041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1139-16_0_3_line_16 | NAYY 4x150 SE | 13 | 15 | 0.019122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1139-16_0_3_line_17 | NAYY 4x150 SE | 15 | 27 | 0.024919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1139-16_0_3_line_18 | NAYY 4x150 SE | 16 | 17 | 0.035793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1139-16_0_3_line_19 | NAYY 4x150 SE | 16 | 18 | 0.020969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1139-16_0_3_line_20 | NAYY 4x150 SE | 17 | 19 | 0.020432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1139-16_0_3_line_21 | NAYY 4x150 SE | 18 | 20 | 0.012288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_1139-16_0_3_line_22 | NAYY 4x150 SE | 19 | 21 | 0.011928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1139-16_0_3_line_23 | NAYY 4x150 SE | 20 | 22 | 0.0060819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1139-16_0_3_line_24 | NAYY 4x150 SE | 20 | 23 | 0.014958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1139-16_0_3_line_25 | NAYY 4x150 SE | 21 | 24 | 0.033502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1139-16_0_3_line_26 | NAYY 4x150 SE | 22 | 25 | 0.011349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1139-16_0_3_line_27 | NAYY 4x150 SE | 23 | 26 | 0.0053488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1139-16_0_3_line_28 | NAYY 4x150 SE | 24 | 32 | 0.029667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1139-16_0_3_line_29 | NAYY 4x150 SE | 25 | 37 | 0.008969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1139-16_0_3_line_30 | NAYY 4x150 SE | 26 | 29 | 0.015907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1139-16_0_3_line_31 | NAYY 4x150 SE | 27 | 28 | 0.017243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1139-16_0_3_line_32 | NAYY 4x150 SE | 30 | 31 | 0.052998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1139-16_0_3_line_33 | NAYY 4x150 SE | 31 | 46 | 0.0057332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1139-16_0_3_line_34 | NAYY 4x150 SE | 32 | 33 | 0.01318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1139-16_0_3_line_35 | NAYY 4x150 SE | 34 | 35 | 0.0019401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1139-16_0_3_line_36 | NAYY 4x150 SE | 34 | 36 | 0.027113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1139-16_0_3_line_37 | NAYY 4x150 SE | 35 | 37 | 0.027194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1139-16_0_3_line_38 | NAYY 4x150 SE | 36 | 38 | 0.015498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1139-16_0_3_line_39 | NAYY 4x150 SE | 36 | 39 | 0.063327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1139-16_0_3_line_40 | NAYY 4x150 SE | 38 | 40 | 0.032954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1139-16_0_3_line_41 | NAYY 4x150 SE | 41 | 42 | 0.0013104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1139-16_0_3_line_42 | NAYY 4x150 SE | 42 | 43 | 0.026714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1139-16_0_3_line_43 | NAYY 4x150 SE | 43 | 44 | 0.00092626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1139-16_0_3_line_44 | NAYY 4x150 SE | 44 | 45 | 0.02739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1139-16_0_3_line_45 | NAYY 4x150 SE | 45 | 46 | 0.053758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1139-16_0_3_trafo_8 | 0.25 MVA 20/0.4 kV | 47 | 16 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2635187.9466 | 1230761.9433 | 2635175.5049 | 1230768.0513 | 2635152.1016 | 1230774.5949 | 2635130.7451 | 1230779.5386
1 | 2635200.1852 | 1230805.5313 | 2635211.0051 | 1230784.2267 | 2635187.9466 | 1230761.9433
2 | 2635200.1852 | 1230805.5313 | 2635196.5918 | 1230808.6787 | 2635182.8214 | 1230823.0617 | 2635170.0052 | 1230839.754
3 | 2635170.0052 | 1230839.754 | 2635157.1708 | 1230856.4703
4 | 2635140.0399 | 1230878.7825 | 2635157.1708 | 1230856.4703
5 | 2635129.4642 | 1230932.5915 | 2635127.5468 | 1230934.4797
6 | 2635143.7384 | 1230918.5339 | 2635129.4642 | 1230932.5915
7 | 2635127.5468 | 1230934.4797 | 2635125.1435 | 1230936.8465 | 2635121.8707 | 1230940.8853 | 2635120.5429 | 1230946.4253 | 2635121.0946 | 1230948.2793
8 | 2635106.9672 | 1230915.0593 | 2635127.5468 | 1230934.4797
9 | 2635138.3888 | 1230980.5515 | 2635136.5052 | 1230973.7696 | 2635122.2064 | 1230952.0163 | 2635121.0946 | 1230948.2793
10 | 2635106.9672 | 1230915.0593 | 2635085.3821 | 1230934.7043
11 | 2635106.9672 | 1230915.0593 | 2635103.2964 | 1230904.9824
12 | 2635106.9672 | 1230915.0593 | 2635123.63 | 1230897.6496
13 | 2635082.239 | 1230937.565 | 2635085.3821 | 1230934.7043
14 | 2635093.5895 | 1230878.3356 | 2635103.2964 | 1230904.9824
15 | 2635140.0399 | 1230878.7825 | 2635133.3568 | 1230887.4869 | 2635123.63 | 1230897.6496
16 | 2635138.3888 | 1230980.5515 | 2635133.2006 | 1230980.6209 | 2635121.3637 | 1230987.9712
17 | 2635121.3637 | 1230987.9712 | 2635100.1944 | 1231001.1163
18 | 2635030.7469 | 1230942.1341 | 2635026.3721 | 1230943.1351 | 2635022.3053 | 1230943.1112 | 2634995.8034 | 1230936.819
19 | 2635030.7469 | 1230942.1341 | 2635032.53 | 1230941.7261 | 2635036.8736 | 1230942.3186 | 2635040.5725 | 1230945.6536 | 2635047.1672 | 1230952.8697
20 | 2634975.9235 | 1230932.0991 | 2634995.8034 | 1230936.819
21 | 2635055.4567 | 1230961.9401 | 2635047.1672 | 1230952.8697
22 | 2634975.9235 | 1230932.0991 | 2634966.3176 | 1230929.8184 | 2634964.3091 | 1230929.381
23 | 2635055.4567 | 1230961.9401 | 2635051.0249 | 1230966.1052
24 | 2635055.4567 | 1230961.9401 | 2635066.5193 | 1230951.8718
25 | 2634931.8645 | 1230921.0663 | 2634954.6165 | 1230927.2703 | 2634964.3091 | 1230929.381
26 | 2635042.7547 | 1230973.8775 | 2635051.0249 | 1230966.1052
27 | 2635066.5193 | 1230951.8718 | 2635070.475 | 1230948.2716
28 | 2634931.8645 | 1230921.0663 | 2634928.8399 | 1230926.7076 | 2634921.8096 | 1230943.8547 | 2634918.887 | 1230947.5954
29 | 2635036.2191 | 1230980.0199 | 2635042.7547 | 1230973.8775
30 | 2635082.239 | 1230937.565 | 2635070.475 | 1230948.2716
31 | 2635100.1944 | 1231001.1163 | 2635085.5462 | 1231010.2121
32 | 2635054.7654 | 1230905.746 | 2635058.7378 | 1230902.5118 | 2635074.7642 | 1230903.6291 | 2635085.9086 | 1230892.6881 | 2635093.5895 | 1230878.3356
33 | 2635054.7654 | 1230905.746 | 2635055.3746 | 1230900.0452
34 | 2634918.887 | 1230947.5954 | 2634926.0636 | 1230958.6508
35 | 2635016.4032 | 1230998.643 | 2635014.9895 | 1230999.9717
36 | 2634994.1891 | 1231017.2725 | 2635004.3873 | 1231009.9357 | 2635014.9895 | 1230999.9717
37 | 2635016.4032 | 1230998.643 | 2635036.2191 | 1230980.0199
38 | 2634981.6089 | 1231026.323 | 2634994.1891 | 1231017.2725
39 | 2634994.1891 | 1231017.2725 | 2635037.2493 | 1231063.7065
40 | 2634981.6089 | 1231026.323 | 2634972.8675 | 1231015.0425 | 2634960.1451 | 1231001.3608
41 | 2634966.7657 | 1230863.7987 | 2634965.5177 | 1230863.3994
42 | 2634992.2087 | 1230871.9398 | 2634966.7657 | 1230863.7987
43 | 2634992.2087 | 1230871.9398 | 2634993.0909 | 1230872.2221
44 | 2635019.8247 | 1230877.9034 | 2635000.9718 | 1230874.7438 | 2634993.0909 | 1230872.2221
45 | 2635019.8247 | 1230877.9034 | 2635057.0738 | 1230884.1463 | 2635055.3746 | 1230900.0452

## bus_geodata
| x | y | coords
0 | 2635130.7451 | 1230779.5386
1 | 2635187.9466 | 1230761.9433
2 | 2635200.1852 | 1230805.5313
3 | 2635170.0052 | 1230839.754
4 | 2635157.1708 | 1230856.4703
5 | 2635129.4642 | 1230932.5915
6 | 2635127.5468 | 1230934.4797
7 | 2635143.7384 | 1230918.5339
8 | 2635121.0946 | 1230948.2793
9 | 2635106.9672 | 1230915.0593
10 | 2635085.3821 | 1230934.7043
11 | 2635103.2964 | 1230904.9824
12 | 2635123.63 | 1230897.6496
13 | 2635138.3888 | 1230980.5515
14 | 2635140.0399 | 1230878.7825
15 | 2635121.3637 | 1230987.9712
16 | 2635030.7469 | 1230942.1341
17 | 2634995.8034 | 1230936.819
18 | 2635047.1672 | 1230952.8696
19 | 2634975.9235 | 1230932.0991
20 | 2635055.4567 | 1230961.9401
21 | 2634964.3091 | 1230929.381
22 | 2635051.0249 | 1230966.1052
23 | 2635066.5193 | 1230951.8718
24 | 2634931.8645 | 1230921.0663
25 | 2635042.7547 | 1230973.8775
26 | 2635070.475 | 1230948.2716
27 | 2635100.1944 | 1231001.1163
28 | 2635085.5462 | 1231010.2121
29 | 2635082.239 | 1230937.565
30 | 2635093.5895 | 1230878.3356
31 | 2635054.7654 | 1230905.746
32 | 2634918.887 | 1230947.5954
33 | 2634926.0636 | 1230958.6508
34 | 2635014.9895 | 1230999.9717
35 | 2635016.4032 | 1230998.643
36 | 2634994.1891 | 1231017.2725
37 | 2635036.2191 | 1230980.0199
38 | 2634981.6089 | 1231026.323
39 | 2635037.2493 | 1231063.7065
40 | 2634960.1451 | 1231001.3608
41 | 2634965.5177 | 1230863.3994
42 | 2634966.7657 | 1230863.7987
43 | 2634992.2087 | 1230871.9398
44 | 2634993.0909 | 1230872.2221
45 | 2635019.8247 | 1230877.9034
46 | 2635055.3746 | 1230900.0452
47 | 2635055.4567 | 1230961.9401

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98707 | -0.090569 | 0.0038667 | 0.00096907
1 | 0.9874 | -0.088189 | 0 | 0
2 | 0.98772 | -0.085972 | 0 | 0
3 | 0.98797 | -0.084157 | 0.001719 | 0.00043083
4 | 0.98814 | -0.08295 | 0.0017096 | 0.00042848
5 | 0.98796 | -0.084233 | 0.0038141 | 0.0009559
6 | 0.988 | -0.083909 | 0.0052112 | 0.0013061
7 | 0.98773 | -0.085863 | 0.0079572 | 0.0019943
8 | 0.98773 | -0.085829 | 0.0029 | 0.00072682
9 | 0.98917 | -0.075652 | 0 | 0
10 | 0.99239 | -0.053034 | 0.0025407 | 0.00063675
11 | 0.98861 | -0.079617 | 0.0020754 | 0.00052013
12 | 0.98877 | -0.07846 | 0.002076 | 0.0005203
13 | 0.98727 | -0.089115 | 0 | 0
14 | 0.98844 | -0.080848 | 0.0020225 | 0.00050689
15 | 0.98703 | -0.090815 | 0.0041624 | 0.0010432
16 | 1 | 0 | -0.17212 | -0.043134
17 | 0.99731 | -0.018794 | 0.010779 | 0.0027014
18 | 0.99823 | -0.012305 | 0.0016888 | 0.00042325
19 | 0.99609 | -0.027351 | 0.013292 | 0.0033314
20 | 0.9972 | -0.019432 | 0 | 0
21 | 0.99561 | -0.030759 | 0.011447 | 0.0028689
22 | 0.99694 | -0.021282 | 0.0032583 | 0.0008166
23 | 0.99536 | -0.032273 | 0.0034484 | 0.00086426
24 | 0.99479 | -0.036479 | 0 | 0
25 | 0.9965 | -0.024367 | 0.0033117 | 0.00083
26 | 0.99472 | -0.036691 | 0.0013469 | 0.00033756
27 | 0.98687 | -0.091968 | 0.0020521 | 0.00051431
28 | 0.98681 | -0.092404 | 0.0024624 | 0.00061713
29 | 0.99287 | -0.049644 | 0.0018182 | 0.0004557
30 | 0.9872 | -0.08952 | 0 | 0
31 | 0.98457 | -0.1081 | 0 | 0
32 | 0.99407 | -0.041551 | 0 | 0
33 | 0.99375 | -0.043807 | 0.016938 | 0.004245
34 | 0.9953 | -0.032811 | 0.0021983 | 0.00055094
35 | 0.99535 | -0.032421 | 0.0016383 | 0.00041061
36 | 0.99461 | -0.037667 | 0.0017674 | 0.00044294
37 | 0.99619 | -0.026507 | 0.0021331 | 0.0005346
38 | 0.9943 | -0.039784 | 0 | 0
39 | 0.99438 | -0.039241 | 0.002459 | 0.00061628
40 | 0.99367 | -0.044287 | 0.013527 | 0.0033903
41 | 0.98056 | -0.13666 | 0.0072742 | 0.0018231
42 | 0.98057 | -0.13656 | 0.0042465 | 0.0010643
43 | 0.98102 | -0.13337 | 0.0055694 | 0.0013958
44 | 0.98104 | -0.13321 | 0.0070596 | 0.0017693
45 | 0.982 | -0.12635 | 0.0050917 | 0.0012761
46 | 0.98429 | -0.11012 | 0.0048894 | 0.0012254
47 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0038667 | -0.00096907 | 0.0038679 | 0.0009688 | 1.2738e-06 | -2.7832e-07 | 0.005829 | 0.0058288 | 0.005829 | 0.98707 | -0.090569 | 0.9874 | -0.088189 | 2.1589
1 | -0.0038679 | -0.0009688 | 0.0038691 | 0.00096854 | 1.1851e-06 | -2.5947e-07 | 0.0058288 | 0.0058285 | 0.0058288 | 0.9874 | -0.088189 | 0.98772 | -0.085972 | 2.1588
2 | -0.0038691 | -0.00096854 | 0.0038701 | 0.00096832 | 9.6944e-07 | -2.1264e-07 | 0.0058285 | 0.0058283 | 0.0058285 | 0.98772 | -0.085972 | 0.98797 | -0.084157 | 2.1587
3 | -0.0055891 | -0.0013992 | 0.00559 | 0.0013992 | 9.3175e-07 | 8.8442e-08 | 0.0084174 | 0.0084173 | 0.0084174 | 0.98797 | -0.084157 | 0.98814 | -0.08295 | 3.1175
4 | -0.0072997 | -0.0018277 | 0.0073018 | 0.0018282 | 2.1207e-06 | 4.5521e-07 | 0.010992 | 0.010992 | 0.010992 | 0.98814 | -0.08295 | 0.98844 | -0.080848 | 4.071
5 | -0.011773 | -0.0029506 | 0.011774 | 0.0029508 | 5.2799e-07 | 1.6861e-07 | 0.017732 | 0.017732 | 0.017732 | 0.98796 | -0.084233 | 0.988 | -0.083909 | 6.5674
6 | 0.007959 | 0.0019947 | -0.0079572 | -0.0019943 | 1.7965e-06 | 4.3446e-07 | 0.011987 | 0.011988 | 0.011988 | 0.98796 | -0.084233 | 0.98773 | -0.085863 | 4.4398
7 | 0.011587 | 0.0029038 | -0.011584 | -0.0029028 | 3.079e-06 | 9.7678e-07 | 0.017451 | 0.017451 | 0.017451 | 0.988 | -0.083909 | 0.98773 | -0.085829 | 6.4633
8 | -0.028572 | -0.0071606 | 0.028604 | 0.0071729 | 3.2695e-05 | 1.2212e-05 | 0.043031 | 0.043031 | 0.043031 | 0.988 | -0.083909 | 0.98917 | -0.075652 | 15.9376
9 | 0.0086838 | 0.002176 | -0.0086799 | -0.002175 | 3.948e-06 | 1.0455e-06 | 0.013082 | 0.013082 | 0.013082 | 0.98773 | -0.085829 | 0.98727 | -0.089115 | 4.8452
10 | -0.076479 | -0.019202 | 0.07672 | 0.019294 | 0.00024111 | 9.2358e-05 | 0.11506 | 0.11506 | 0.11506 | 0.98917 | -0.075652 | 0.99239 | -0.053034 | 42.6147
11 | 0.036466 | 0.0091715 | -0.036446 | -0.0091639 | 2.0147e-05 | 7.6112e-06 | 0.054868 | 0.054868 | 0.054868 | 0.98917 | -0.075652 | 0.98861 | -0.079617 | 20.3215
12 | 0.011408 | 0.0028576 | -0.011403 | -0.0028562 | 4.4283e-06 | 1.394e-06 | 0.01716 | 0.017161 | 0.017161 | 0.98917 | -0.075652 | 0.98877 | -0.07846 | 6.3558
13 | -0.07926 | -0.019931 | 0.079298 | 0.019945 | 3.7473e-05 | 1.4358e-05 | 0.11887 | 0.11887 | 0.11887 | 0.99239 | -0.053034 | 0.99287 | -0.049644 | 44.0256
14 | 0.034371 | 0.0086438 | -0.034323 | -0.0086259 | 4.7382e-05 | 1.7861e-05 | 0.051744 | 0.051744 | 0.051744 | 0.98861 | -0.079617 | 0.9872 | -0.08952 | 19.1646
15 | 0.0093274 | 0.0023359 | -0.0093243 | -0.0023351 | 3.0786e-06 | 8.6299e-07 | 0.014036 | 0.014036 | 0.014036 | 0.98877 | -0.07846 | 0.98844 | -0.080848 | 5.1987
16 | 0.0086799 | 0.002175 | -0.0086778 | -0.0021744 | 2.0421e-06 | 5.4097e-07 | 0.013082 | 0.013082 | 0.013082 | 0.98727 | -0.089115 | 0.98703 | -0.090815 | 4.8453
17 | 0.0045154 | 0.0011312 | -0.0045146 | -0.0011313 | 7.205e-07 | -4.1319e-08 | 0.0068071 | 0.0068072 | 0.0068072 | 0.98703 | -0.090815 | 0.98687 | -0.091968 | 2.5212
18 | 0.052687 | 0.013234 | -0.052549 | -0.013181 | 0.00013731 | 5.2345e-05 | 0.078409 | 0.078409 | 0.078409 | 1 | 0 | 0.99731 | -0.018794 | 29.0403
19 | 0.11864 | 0.0299 | -0.11843 | -0.029822 | 0.00020402 | 7.792e-05 | 0.17659 | 0.17659 | 0.17659 | 1 | 0 | 0.99823 | -0.012305 | 32.7022
20 | 0.041771 | 0.01048 | -0.041721 | -0.010461 | 4.9529e-05 | 1.8783e-05 | 0.062327 | 0.062327 | 0.062327 | 0.99731 | -0.018794 | 0.99609 | -0.027351 | 23.084
21 | 0.11674 | 0.029399 | -0.11663 | -0.029355 | 0.00011617 | 4.436e-05 | 0.17407 | 0.17407 | 0.17407 | 0.99823 | -0.012305 | 0.9972 | -0.019432 | 32.236
22 | 0.028429 | 0.0071297 | -0.028415 | -0.0071247 | 1.3426e-05 | 5.0085e-06 | 0.04247 | 0.04247 | 0.04247 | 0.99609 | -0.027351 | 0.99561 | -0.030759 | 15.7297
23 | 0.030363 | 0.0076167 | -0.030356 | -0.0076137 | 7.7915e-06 | 2.9174e-06 | 0.04531 | 0.045311 | 0.045311 | 0.9972 | -0.019432 | 0.99694 | -0.021282 | 16.7817
24 | 0.086264 | 0.021738 | -0.086109 | -0.021679 | 0.00015476 | 5.9328e-05 | 0.12876 | 0.12876 | 0.12876 | 0.9972 | -0.019432 | 0.99536 | -0.032273 | 47.6904
25 | 0.016968 | 0.0042558 | -0.016955 | -0.004251 | 1.3447e-05 | 4.7365e-06 | 0.025362 | 0.025362 | 0.025362 | 0.99561 | -0.030759 | 0.99479 | -0.036479 | 9.3933
26 | 0.027097 | 0.0067972 | -0.027086 | -0.0067928 | 1.1586e-05 | 4.3082e-06 | 0.040447 | 0.040447 | 0.040447 | 0.99694 | -0.021282 | 0.9965 | -0.024367 | 14.9805
27 | 0.082661 | 0.020815 | -0.08261 | -0.020795 | 5.0996e-05 | 1.9544e-05 | 0.12361 | 0.12361 | 0.12361 | 0.99536 | -0.032273 | 0.99472 | -0.036691 | 45.7811
28 | 0.016955 | 0.004251 | -0.016943 | -0.0042468 | 1.1908e-05 | 4.1949e-06 | 0.025362 | 0.025362 | 0.025362 | 0.99479 | -0.036479 | 0.99407 | -0.041551 | 9.3933
29 | 0.023774 | 0.0059628 | -0.023767 | -0.0059603 | 7.054e-06 | 2.5963e-06 | 0.035502 | 0.035502 | 0.035502 | 0.9965 | -0.024367 | 0.99619 | -0.026507 | 13.1489
30 | 0.081263 | 0.020457 | -0.081116 | -0.020401 | 0.00014675 | 5.6238e-05 | 0.12159 | 0.12159 | 0.12159 | 0.99472 | -0.036691 | 0.99287 | -0.049644 | 45.0349
31 | 0.0024625 | 0.00061697 | -0.0024624 | -0.00061713 | 1.4833e-07 | -1.6324e-07 | 0.003713 | 0.003713 | 0.003713 | 0.98687 | -0.091968 | 0.98681 | -0.092404 | 1.3752
32 | 0.034323 | 0.0086259 | -0.034235 | -0.0085925 | 8.8547e-05 | 3.3381e-05 | 0.051744 | 0.051745 | 0.051745 | 0.9872 | -0.08952 | 0.98457 | -0.1081 | 19.1647
33 | 0.034235 | 0.0085925 | -0.034225 | -0.0085889 | 9.5788e-06 | 3.6113e-06 | 0.051745 | 0.051745 | 0.051745 | 0.98457 | -0.1081 | 0.98429 | -0.11012 | 19.1647
34 | 0.016943 | 0.0042468 | -0.016938 | -0.004245 | 5.2903e-06 | 1.8639e-06 | 0.025362 | 0.025362 | 0.025362 | 0.99407 | -0.041551 | 0.99375 | -0.043807 | 9.3933
35 | -0.019977 | -0.0050082 | 0.019978 | 0.0050086 | 1.0799e-06 | 3.9013e-07 | 0.029867 | 0.029867 | 0.029867 | 0.9953 | -0.032811 | 0.99535 | -0.032421 | 11.0618
36 | 0.017778 | 0.0044572 | -0.017767 | -0.004453 | 1.1953e-05 | 4.2452e-06 | 0.02658 | 0.02658 | 0.02658 | 0.9953 | -0.032811 | 0.99461 | -0.037667 | 9.8446
37 | -0.021616 | -0.0054192 | 0.021634 | 0.0054256 | 1.7721e-05 | 6.462e-06 | 0.032316 | 0.032316 | 0.032316 | 0.99535 | -0.032421 | 0.99619 | -0.026507 | 11.9689
38 | 0.01354 | 0.0033944 | -0.013536 | -0.0033931 | 3.9682e-06 | 1.3252e-06 | 0.020257 | 0.020257 | 0.020257 | 0.99461 | -0.037667 | 0.9943 | -0.039784 | 7.5026
39 | 0.0024595 | 0.00061566 | -0.002459 | -0.00061628 | 5.35e-07 | -6.1591e-07 | 0.0036794 | 0.0036797 | 0.0036797 | 0.99461 | -0.037667 | 0.99438 | -0.039241 | 1.3628
40 | 0.013536 | 0.0033931 | -0.013527 | -0.0033903 | 8.4381e-06 | 2.8183e-06 | 0.020257 | 0.020257 | 0.020257 | 0.9943 | -0.039784 | 0.99367 | -0.044287 | 7.5026
41 | -0.0072742 | -0.0018231 | 0.0072743 | 0.0018231 | 9.9639e-08 | 2.1793e-08 | 0.011039 | 0.011039 | 0.011039 | 0.98056 | -0.13666 | 0.98057 | -0.13656 | 4.0884
42 | -0.011521 | -0.0028874 | 0.011526 | 0.002889 | 5.0949e-06 | 1.6224e-06 | 0.017483 | 0.017483 | 0.017483 | 0.98057 | -0.13656 | 0.98102 | -0.13337 | 6.4751
43 | -0.017095 | -0.0042848 | 0.017096 | 0.004285 | 3.8863e-07 | 1.3778e-07 | 0.02593 | 0.02593 | 0.02593 | 0.98102 | -0.13337 | 0.98104 | -0.13321 | 9.6038
44 | -0.024155 | -0.0060543 | 0.024178 | 0.0060627 | 2.2943e-05 | 8.478e-06 | 0.036638 | 0.036638 | 0.036638 | 0.98104 | -0.13321 | 0.982 | -0.12635 | 13.5697
45 | -0.02927 | -0.0073388 | 0.029336 | 0.0073635 | 6.599e-05 | 2.4699e-05 | 0.044353 | 0.044353 | 0.044353 | 0.982 | -0.12635 | 0.98429 | -0.11012 | 16.4272

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.17598 | 0.0441

## res_load
| p_mw | q_mvar
0 | 0.0038667 | 0.00096907
1 | 0.001719 | 0.00043083
2 | 0.0017096 | 0.00042848
3 | 0.0038141 | 0.0009559
4 | 0.0052112 | 0.0013061
5 | 0.0079572 | 0.0019943
6 | 0.0029 | 0.00072682
7 | 0.0025407 | 0.00063675
8 | 0.0020754 | 0.00052013
9 | 0.002076 | 0.0005203
10 | 0.0020225 | 0.00050689
11 | 0.0041624 | 0.0010432
12 | 0.0038551 | 0.00096618
13 | 0.010779 | 0.0027014
14 | 0.0016888 | 0.00042325
15 | 0.013292 | 0.0033314
16 | 0.011447 | 0.0028689
17 | 0.0032583 | 0.0008166
18 | 0.0034484 | 0.00086426
19 | 0.0033117 | 0.00083
20 | 0.0013469 | 0.00033756
21 | 0.0020521 | 0.00051431
22 | 0.0024624 | 0.00061713
23 | 0.0018182 | 0.0004557
24 | 0.016938 | 0.004245
25 | 0.0021983 | 0.00055094
26 | 0.0016383 | 0.00041061
27 | 0.0017674 | 0.00044294
28 | 0.0021331 | 0.0005346
29 | 0.002459 | 0.00061628
30 | 0.013527 | 0.0033903
31 | 0.0072742 | 0.0018231
32 | 0.0042465 | 0.0010643
33 | 0.0055694 | 0.0013958
34 | 0.0070596 | 0.0017693
35 | 0.0050917 | 0.0012761
36 | 0.0048894 | 0.0012254

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1