## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1139-8_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1139-8_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1139-8_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1139-8_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1139-8_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1139-8_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1139-8_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1139-8_0_3_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_1139-8_0_3_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_1139-8_0_3_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_1139-8_0_3_node_23 | 0.4 | n |  | TRUE
11 | bus_LV_1139-8_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1139-8_0_3_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_1139-8_0_3_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_1139-8_0_3_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1139-8_0_3_node_71 | 0.4 | n |  | TRUE
16 | bus_LV_1139-8_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1139-8_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1139-8_0_3_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_1139-8_0_3_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1139-8_0_3_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1139-8_0_3_node_57 | 0.4 | n |  | TRUE
22 | bus_LV_1139-8_0_3_node_42 | 0.4 | n |  | TRUE
23 | bus_LV_1139-8_0_3_node_41 | 0.4 | n |  | TRUE
24 | bus_LV_1139-8_0_3_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1139-8_0_3_node_37 | 0.4 | n |  | TRUE
26 | bus_LV_1139-8_0_3_node_38 | 0.4 | n |  | TRUE
27 | bus_LV_1139-8_0_3_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_1139-8_0_3_node_40 | 0.4 | n |  | TRUE
29 | bus_LV_1139-8_0_3_node_72 | 0.4 | n |  | TRUE
30 | bus_LV_1139-8_0_3_node_54 | 0.4 | n |  | TRUE
31 | bus_LV_1139-8_0_3_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_1139-8_0_3_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_1139-8_0_3_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_1139-8_0_3_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_1139-8_0_3_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_1139-8_0_3_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_1139-8_0_3_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_1139-8_0_3_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_1139-8_0_3_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_1139-8_0_3_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_1139-8_0_3_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_1139-8_0_3_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_1139-8_0_3_node_32 | 0.4 | n |  | TRUE
44 | bus_LV_1139-8_0_3_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_1139-8_0_3_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_1139-8_0_3_node_55 | 0.4 | n |  | TRUE
47 | bus_LV_1139-8_0_3_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_1139-8_0_3_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_1139-8_0_3_node_45 | 0.4 | n |  | TRUE
50 | bus_LV_1139-8_0_3_node_46 | 0.4 | n |  | TRUE
51 | bus_LV_1139-8_0_3_node_47 | 0.4 | n |  | TRUE
52 | bus_LV_1139-8_0_3_node_48 | 0.4 | n |  | TRUE
53 | bus_LV_1139-8_0_3_node_63 | 0.4 | n |  | TRUE
54 | bus_LV_1139-8_0_3_node_60 | 0.4 | n |  | TRUE
55 | bus_LV_1139-8_0_3_node_61 | 0.4 | n |  | TRUE
56 | bus_LV_1139-8_0_3_node_62 | 0.4 | n |  | TRUE
57 | bus_LV_1139-8_0_3_node_64 | 0.4 | n |  | TRUE
58 | bus_LV_1139-8_0_3_node_65 | 0.4 | n |  | TRUE
59 | bus_LV_1139-8_0_3_node_59 | 0.4 | n |  | TRUE
60 | bus_LV_1139-8_0_3_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_1139-8_0_3_node_50 | 0.4 | n |  | TRUE
62 | bus_LV_1139-8_0_3_node_52 | 0.4 | n |  | TRUE
63 | bus_LV_1139-8_0_3_node_53 | 0.4 | n |  | TRUE
64 | bus_LV_1139-8_0_3_node_66 | 0.4 | n |  | TRUE
65 | bus_LV_1139-8_0_3_node_56 | 0.4 | n |  | TRUE
66 | bus_LV_1139-8_0_3_node_58 | 0.4 | n |  | TRUE
67 | bus_LV_1139-8_0_3_node_68 | 0.4 | n |  | TRUE
68 | bus_LV_1139-8_0_3_node_67 | 0.4 | n |  | TRUE
69 | bus_LV_1139-8_0_3_node_69 | 0.4 | n |  | TRUE
70 | bus_MV_475_1_node_13 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1139-8_0_3_load_0 | 0 | 0.006148 | 0.0015408 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1139-8_0_3_load_3 | 3 | 0.0057494 | 0.0014409 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1139-8_0_3_load_4 | 4 | 0.021215 | 0.0053171 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1139-8_0_3_load_5 | 5 | 0.0012682 | 0.00031785 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1139-8_0_3_load_6 | 6 | 0.0017667 | 0.00044278 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1139-8_0_3_load_16 | 8 | 0.019905 | 0.0049887 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1139-8_0_3_load_18 | 9 | 0.00079447 | 0.00019911 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1139-8_0_3_load_23 | 10 | 0.0012983 | 0.00032537 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1139-8_0_3_load_8 | 11 | 0.0062675 | 0.0015708 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1139-8_0_3_load_19 | 12 | 0.0020202 | 0.00050632 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1139-8_0_3_load_22 | 13 | 0.0013198 | 0.00033077 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1139-8_0_3_load_7 | 14 | 0.014252 | 0.003572 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1139-8_0_3_load_71 | 15 | 0.017809 | 0.0044634 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1139-8_0_3_load_11 | 16 | 0.0065054 | 0.0016304 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1139-8_0_3_load_12 | 17 | 0.011124 | 0.002788 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1139-8_0_3_load_13 | 18 | 0.013159 | 0.0032981 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1139-8_0_3_load_57 | 21 | 0.0061886 | 0.001551 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1139-8_0_3_load_42 | 22 | 0.002248 | 0.0005634 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1139-8_0_3_load_41 | 23 | 0.0020691 | 0.00051856 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1139-8_0_3_load_37 | 25 | 0.0034432 | 0.00086294 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1139-8_0_3_load_25 | 27 | 0.00052817 | 0.00013237 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1139-8_0_3_load_72 | 29 | 0.0058299 | 0.0014611 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1139-8_0_3_load_20 | 32 | 0.0025149 | 0.0006303 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1139-8_0_3_load_21 | 33 | 0.0014764 | 0.00037002 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1139-8_0_3_load_39 | 34 | 0.0088678 | 0.0022225 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1139-8_0_3_load_26 | 35 | 0.0012004 | 0.00030085 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1139-8_0_3_load_30 | 36 | 0.0016604 | 0.00041614 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1139-8_0_3_load_28 | 37 | 0.0025146 | 0.00063023 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1139-8_0_3_load_27 | 38 | 0.0016973 | 0.00042537 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1139-8_0_3_load_29 | 39 | 0.0011557 | 0.00028965 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1139-8_0_3_load_31 | 40 | 0.0012158 | 0.0003047 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1139-8_0_3_load_34 | 42 | 0.0021715 | 0.00054423 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1139-8_0_3_load_32 | 43 | 0.0022499 | 0.00056387 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1139-8_0_3_load_33 | 44 | 0.0025953 | 0.00065044 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1139-8_0_3_load_35 | 45 | 0.0039535 | 0.00099085 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1139-8_0_3_load_55 | 46 | 0.0035909 | 0.00089995 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1139-8_0_3_load_44 | 47 | 0.0023128 | 0.00057965 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1139-8_0_3_load_43 | 48 | 0.0030645 | 0.00076805 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1139-8_0_3_load_45 | 49 | 0.0010382 | 0.00026019 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1139-8_0_3_load_46 | 50 | 0.0033667 | 0.00084377 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1139-8_0_3_load_47 | 51 | 0.0015635 | 0.00039184 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1139-8_0_3_load_48 | 52 | 0.0038888 | 0.00097464 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1139-8_0_3_load_63 | 53 | 0.0010946 | 0.00027433 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1139-8_0_3_load_60 | 54 | 0.00089809 | 0.00022508 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1139-8_0_3_load_61 | 55 | 0.0016536 | 0.00041442 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1139-8_0_3_load_62 | 56 | 0.0014838 | 0.00037188 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1139-8_0_3_load_64 | 57 | 0.00086734 | 0.00021737 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1139-8_0_3_load_65 | 58 | 0.0011112 | 0.00027849 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1139-8_0_3_load_59 | 59 | 0.0030717 | 0.00076985 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1139-8_0_3_load_49 | 60 | 0.0015156 | 0.00037984 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1139-8_0_3_load_53 | 63 | 0.0025406 | 0.00063674 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1139-8_0_3_load_56 | 65 | 0.0013967 | 0.00035005 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1139-8_0_3_load_58 | 66 | 0.00091076 | 0.00022826 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1139-8_0_3_load_68 | 67 | 0.0023222 | 0.00058199 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1139-8_0_3_load_67 | 68 | 0.00083101 | 0.00020827 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1139-8_0_3_load_69 | 69 | 0.01446 | 0.003624 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1139-8_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.01032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_1139-8_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.011335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_1139-8_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.016682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1139-8_0_3_line_3 | NAYY 4x150 SE | 1 | 4 | 0.020598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_1139-8_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.019925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1139-8_0_3_line_5 | NAYY 4x150 SE | 2 | 6 | 0.019903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_1139-8_0_3_line_6 | NAYY 4x150 SE | 3 | 7 | 0.048818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1139-8_0_3_line_7 | NAYY 4x150 SE | 4 | 8 | 0.026956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_1139-8_0_3_line_8 | NAYY 4x150 SE | 5 | 9 | 0.0029512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1139-8_0_3_line_9 | NAYY 4x150 SE | 6 | 10 | 0.019142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_1139-8_0_3_line_10 | NAYY 4x150 SE | 7 | 11 | 0.021417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1139-8_0_3_line_11 | NAYY 4x150 SE | 9 | 12 | 0.033091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1139-8_0_3_line_12 | NAYY 4x150 SE | 10 | 13 | 0.02904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_1139-8_0_3_line_13 | NAYY 4x150 SE | 11 | 15 | 0.046532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1139-8_0_3_line_14 | NAYY 4x150 SE | 11 | 14 | 0.018936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1139-8_0_3_line_15 | NAYY 4x150 SE | 13 | 31 | 0.022844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_1139-8_0_3_line_16 | NAYY 4x150 SE | 16 | 17 | 0.0026069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1139-8_0_3_line_17 | NAYY 4x150 SE | 17 | 18 | 0.0072235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1139-8_0_3_line_18 | NAYY 4x150 SE | 18 | 19 | 0.032169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1139-8_0_3_line_19 | NAYY 4x150 SE | 19 | 20 | 0.011193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1139-8_0_3_line_20 | NAYY 4x150 SE | 20 | 21 | 0.020093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1139-8_0_3_line_21 | NAYY 4x150 SE | 20 | 22 | 0.018985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1139-8_0_3_line_22 | NAYY 4x150 SE | 22 | 23 | 0.0067669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1139-8_0_3_line_23 | NAYY 4x150 SE | 23 | 48 | 0.020897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1139-8_0_3_line_24 | NAYY 4x150 SE | 24 | 25 | 0.027572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1139-8_0_3_line_25 | NAYY 4x150 SE | 24 | 26 | 0.025491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_1139-8_0_3_line_26 | NAYY 4x150 SE | 24 | 27 | 0.021462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_1139-8_0_3_line_27 | NAYY 4x150 SE | 25 | 28 | 0.011514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1139-8_0_3_line_28 | NAYY 4x150 SE | 26 | 29 | 0.04862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1139-8_0_3_line_29 | NAYY 4x150 SE | 26 | 30 | 0.025334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_1139-8_0_3_line_30 | NAYY 4x150 SE | 27 | 31 | 0.031667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_1139-8_0_3_line_31 | NAYY 4x150 SE | 28 | 34 | 0.010137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1139-8_0_3_line_32 | NAYY 4x150 SE | 30 | 46 | 0.026096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1139-8_0_3_line_33 | NAYY 4x150 SE | 30 | 47 | 0.042839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1139-8_0_3_line_34 | NAYY 4x150 SE | 31 | 35 | 0.022436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1139-8_0_3_line_35 | NAYY 4x150 SE | 31 | 33 | 0.032453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1139-8_0_3_line_36 | NAYY 4x150 SE | 32 | 33 | 0.02136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1139-8_0_3_line_37 | NAYY 4x150 SE | 35 | 36 | 0.013659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1139-8_0_3_line_38 | NAYY 4x150 SE | 36 | 37 | 0.016288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1139-8_0_3_line_39 | NAYY 4x150 SE | 37 | 38 | 0.0073071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1139-8_0_3_line_40 | NAYY 4x150 SE | 38 | 39 | 0.01505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1139-8_0_3_line_41 | NAYY 4x150 SE | 39 | 40 | 0.012135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1139-8_0_3_line_42 | NAYY 4x150 SE | 40 | 41 | 0.028029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1139-8_0_3_line_43 | NAYY 4x150 SE | 41 | 42 | 0.0443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1139-8_0_3_line_44 | NAYY 4x150 SE | 42 | 43 | 0.012417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1139-8_0_3_line_45 | NAYY 4x150 SE | 43 | 44 | 0.0018151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1139-8_0_3_line_46 | NAYY 4x150 SE | 44 | 45 | 0.018017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1139-8_0_3_line_47 | NAYY 4x150 SE | 46 | 65 | 0.02329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1139-8_0_3_line_48 | NAYY 4x150 SE | 47 | 48 | 0.024229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1139-8_0_3_line_49 | NAYY 4x150 SE | 49 | 50 | 0.0039821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1139-8_0_3_line_50 | NAYY 4x150 SE | 49 | 51 | 0.0019381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1139-8_0_3_line_51 | NAYY 4x150 SE | 50 | 52 | 0.013656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1139-8_0_3_line_52 | NAYY 4x150 SE | 51 | 53 | 0.044187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1139-8_0_3_line_53 | NAYY 4x150 SE | 52 | 54 | 0.019225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1139-8_0_3_line_54 | NAYY 4x150 SE | 53 | 57 | 0.010795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1139-8_0_3_line_55 | NAYY 4x150 SE | 53 | 55 | 0.073476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1139-8_0_3_line_56 | NAYY 4x150 SE | 54 | 59 | 0.0039947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1139-8_0_3_line_57 | NAYY 4x150 SE | 55 | 56 | 0.028528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1139-8_0_3_line_58 | NAYY 4x150 SE | 57 | 58 | 0.020023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1139-8_0_3_line_59 | NAYY 4x150 SE | 58 | 68 | 0.011303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1139-8_0_3_line_60 | NAYY 4x150 SE | 59 | 66 | 0.017202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1139-8_0_3_line_61 | NAYY 4x150 SE | 60 | 61 | 0.027532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1139-8_0_3_line_62 | NAYY 4x150 SE | 61 | 62 | 0.007409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1139-8_0_3_line_63 | NAYY 4x150 SE | 61 | 63 | 0.039185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1139-8_0_3_line_64 | NAYY 4x150 SE | 62 | 64 | 0.026092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1139-8_0_3_line_65 | NAYY 4x150 SE | 62 | 65 | 0.0079392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1139-8_0_3_line_66 | NAYY 4x150 SE | 63 | 66 | 0.0043896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1139-8_0_3_line_67 | NAYY 4x150 SE | 64 | 67 | 0.012484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1139-8_0_3_line_68 | NAYY 4x150 SE | 67 | 69 | 0.019892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1139-8_0_3_trafo_16 | 0.25 MVA 20/0.4 kV | 70 | 8 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2634977.6231 | 1231106.5711 | 2634986.8223 | 1231106.9476 | 2634987.8418 | 1231107.3951
1 | 2634998.2208 | 1231111.951 | 2634987.8418 | 1231107.3951
2 | 2634977.6231 | 1231106.5711 | 2634974.4224 | 1231102.2497 | 2634967.7036 | 1231093.1588
3 | 2634977.6231 | 1231106.5711 | 2634990.0357 | 1231123.0086
4 | 2634998.2208 | 1231111.951 | 2635010.2597 | 1231096.0749
5 | 2634998.2208 | 1231111.951 | 2635005.0569 | 1231114.9486 | 2635016.5454 | 1231119.7157
6 | 2634938.6882 | 1231053.899 | 2634967.7036 | 1231093.1588
7 | 2635006.2802 | 1231144.5204 | 2634990.0357 | 1231123.0086
8 | 2635012.0428 | 1231093.7233 | 2635010.2597 | 1231096.0749
9 | 2635034.2256 | 1231127.0521 | 2635016.5454 | 1231119.7157
10 | 2634938.6882 | 1231053.899 | 2634956.9063 | 1231042.6382
11 | 2635033.0314 | 1231068.1959 | 2635024.5756 | 1231077.1958 | 2635012.0428 | 1231093.7233
12 | 2635060.0714 | 1231140.2427 | 2635039.7104 | 1231129.328 | 2635034.2256 | 1231127.0521
13 | 2634956.9063 | 1231042.6382 | 2634933.6442 | 1231002.3378
14 | 2634972.8477 | 1231032.4299 | 2634968.3544 | 1231035.5619 | 2634956.9063 | 1231042.6382
15 | 2635080.2048 | 1231151.0354 | 2635060.0714 | 1231140.2427
16 | 2634921.2365 | 1231165.3939 | 2634923.148 | 1231167.1665
17 | 2634923.148 | 1231167.1665 | 2634928.4445 | 1231172.0782
18 | 2634908.0462 | 1231194.6947 | 2634928.314 | 1231177.5475 | 2634929.0093 | 1231175.2056 | 2634928.4445 | 1231172.0782
19 | 2634908.0462 | 1231194.6947 | 2634911.6028 | 1231200.3301 | 2634911.3036 | 1231204.8533
20 | 2634911.3036 | 1231204.8533 | 2634916.693 | 1231202.7281 | 2634918.6548 | 1231202.6507 | 2634931.0084 | 1231203.6237
21 | 2634911.3036 | 1231204.8533 | 2634910.3489 | 1231219.1454 | 2634910.5484 | 1231221.2701 | 2634911.0948 | 1231222.374 | 2634912.0514 | 1231223.2468
22 | 2634918.7132 | 1231224.111 | 2634915.8564 | 1231223.9696 | 2634913.3057 | 1231223.7322 | 2634912.0514 | 1231223.2468
23 | 2634918.7132 | 1231224.111 | 2634939.5845 | 1231225.1442
24 | 2635042.919 | 1231188.8835 | 2635045.6255 | 1231190.9674 | 2635050.135 | 1231194.2181 | 2635056.4652 | 1231198.2245 | 2635066.2048 | 1231203.5602
25 | 2635042.919 | 1231188.8835 | 2635030.8182 | 1231201.5867 | 2635025.0005 | 1231207.0003
26 | 2635042.919 | 1231188.8835 | 2635057.9808 | 1231173.5946
27 | 2635076.3032 | 1231209.0925 | 2635066.2048 | 1231203.5602
28 | 2634980.6918 | 1231199.0571 | 2634994.0751 | 1231194.8999 | 2634997.2221 | 1231194.1957 | 2635000.6456 | 1231194.1158 | 2635004.0054 | 1231194.5691 | 2635007.1511 | 1231195.3548 | 2635009.9545 | 1231196.4164 | 2635014.1971 | 1231198.6983 | 2635017.3796 | 1231200.974 | 2635025.0005 | 1231207.0003
29 | 2635006.3921 | 1231223.9679 | 2635007.3265 | 1231222.1834 | 2635009.2641 | 1231219.7934 | 2635013.4952 | 1231216.3161 | 2635021.3244 | 1231210.1028 | 2635025.0005 | 1231207.0003
30 | 2635080.2048 | 1231151.0354 | 2635057.9808 | 1231173.5946
31 | 2635076.3032 | 1231209.0925 | 2635085.3395 | 1231213.687
32 | 2635006.3921 | 1231223.9679 | 2635005.3575 | 1231229.9099 | 2635004.5677 | 1231236.7095 | 2635003.3484 | 1231249.8722
33 | 2635006.3921 | 1231223.9679 | 2634987.5423 | 1231226.6254 | 2634980.8369 | 1231227.1863 | 2634963.7839 | 1231226.3422
34 | 2635080.2048 | 1231151.0354 | 2635084.1951 | 1231147.3121 | 2635087.7709 | 1231141.9633 | 2635091.0666 | 1231135.3008 | 2635091.4816 | 1231132.2168
35 | 2635080.2048 | 1231151.0354 | 2635093.5055 | 1231180.6377
36 | 2635113.4492 | 1231188.2874 | 2635093.5055 | 1231180.6377
37 | 2635091.4816 | 1231132.2168 | 2635092.1279 | 1231127.4133 | 2635091.7699 | 1231118.6079
38 | 2635091.1082 | 1231102.3338 | 2635091.7699 | 1231118.6079
39 | 2635090.8952 | 1231095.0312 | 2635090.8845 | 1231096.8317 | 2635091.1082 | 1231102.3338
40 | 2635090.8952 | 1231095.0312 | 2635090.9407 | 1231087.3039 | 2635092.1146 | 1231080.0761
41 | 2635096.9941 | 1231069.0724 | 2635095.5031 | 1231071.3432 | 2635092.4182 | 1231078.207 | 2635092.1146 | 1231080.0761
42 | 2635117.1597 | 1231050.0023 | 2635111.046 | 1231054.2132 | 2635105.9406 | 1231058.2412 | 2635100.0118 | 1231064.4767 | 2635096.9941 | 1231069.0724
43 | 2635117.1597 | 1231050.0023 | 2635123.1857 | 1231049.115 | 2635129.6849 | 1231050.1651 | 2635134.4071 | 1231053.3394 | 2635139.0509 | 1231058.2254 | 2635141.8548 | 1231064.3234 | 2635144.7856 | 1231076.4578
44 | 2635151.074 | 1231086.7364 | 2635148.4449 | 1231084.6081 | 2635145.625 | 1231079.9331 | 2635144.7856 | 1231076.4578
45 | 2635151.074 | 1231086.7364 | 2635152.4848 | 1231087.8785 | 2635152.4848 | 1231087.8785
46 | 2635168.1639 | 1231096.7544 | 2635152.4848 | 1231087.8785
47 | 2635003.3484 | 1231249.8722 | 2635001.2002 | 1231273.0628
48 | 2634963.7839 | 1231226.3422 | 2634939.5845 | 1231225.1442
49 | 2634899.0944 | 1231294.1583 | 2634902.2516 | 1231291.7314 | 2634902.2516 | 1231291.7314
50 | 2634897.5579 | 1231295.3395 | 2634899.0944 | 1231294.1583
51 | 2634902.2516 | 1231291.7314 | 2634908.3571 | 1231290.144 | 2634915.7026 | 1231289.9985
52 | 2634897.5579 | 1231295.3395 | 2634904.2884 | 1231339.0112
53 | 2634915.7026 | 1231289.9985 | 2634934.9242 | 1231289.6177
54 | 2634904.2884 | 1231339.0112 | 2634914.9142 | 1231340.9155
55 | 2634904.2884 | 1231339.0112 | 2634889.4269 | 1231410.9689
56 | 2634934.9242 | 1231289.6177 | 2634938.9181 | 1231289.5386
57 | 2634863.1062 | 1231421.0927 | 2634875.1251 | 1231414.4813 | 2634883.7904 | 1231411.5636 | 2634889.4269 | 1231410.9689
58 | 2634934.6227 | 1231344.4475 | 2634914.9142 | 1231340.9155
59 | 2634934.6227 | 1231344.4475 | 2634945.748 | 1231346.4412
60 | 2634956.1166 | 1231289.1978 | 2634938.9181 | 1231289.5386
61 | 2634999.6824 | 1231288.3347 | 2634997.3452 | 1231314.8817 | 2634997.3257 | 1231315.764
62 | 2634999.6824 | 1231288.3347 | 2635000.4678 | 1231280.9681
63 | 2634999.6824 | 1231288.3347 | 2634960.5053 | 1231289.1109
64 | 2635026.6287 | 1231280.3105 | 2635000.4678 | 1231280.9681
65 | 2635000.4678 | 1231280.9681 | 2635001.2002 | 1231273.0628
66 | 2634960.5053 | 1231289.1109 | 2634956.1166 | 1231289.1978
67 | 2635026.6287 | 1231280.3105 | 2635028.3876 | 1231279.9873 | 2635029.8538 | 1231279.1954 | 2635031.082 | 1231277.6795 | 2635032.933 | 1231274.5663 | 2635034.279 | 1231271.3831
68 | 2635042.026 | 1231253.0621 | 2635034.279 | 1231271.3831

## bus_geodata
| x | y | coords
0 | 2634987.8418 | 1231107.3951
1 | 2634977.6231 | 1231106.5711
2 | 2634998.2208 | 1231111.951
3 | 2634967.7036 | 1231093.1588
4 | 2634990.0357 | 1231123.0086
5 | 2635010.2597 | 1231096.0749
6 | 2635016.5454 | 1231119.7157
7 | 2634938.6882 | 1231053.899
8 | 2635006.2802 | 1231144.5204
9 | 2635012.0428 | 1231093.7233
10 | 2635034.2256 | 1231127.0521
11 | 2634956.9063 | 1231042.6382
12 | 2635033.0314 | 1231068.1959
13 | 2635060.0714 | 1231140.2427
14 | 2634972.8477 | 1231032.4299
15 | 2634933.6442 | 1231002.3378
16 | 2634921.2365 | 1231165.3939
17 | 2634923.148 | 1231167.1665
18 | 2634928.4445 | 1231172.0782
19 | 2634908.0462 | 1231194.6947
20 | 2634911.3036 | 1231204.8533
21 | 2634931.0084 | 1231203.6237
22 | 2634912.0514 | 1231223.2468
23 | 2634918.7132 | 1231224.111
24 | 2635042.919 | 1231188.8835
25 | 2635066.2048 | 1231203.5602
26 | 2635025.0005 | 1231207.0003
27 | 2635057.9808 | 1231173.5946
28 | 2635076.3032 | 1231209.0925
29 | 2634980.6918 | 1231199.0571
30 | 2635006.3921 | 1231223.9679
31 | 2635080.2048 | 1231151.0354
32 | 2635113.4492 | 1231188.2874
33 | 2635093.5055 | 1231180.6377
34 | 2635085.3395 | 1231213.687
35 | 2635091.4816 | 1231132.2168
36 | 2635091.7699 | 1231118.6079
37 | 2635091.1082 | 1231102.3338
38 | 2635090.8952 | 1231095.0312
39 | 2635092.1146 | 1231080.0761
40 | 2635096.9941 | 1231069.0724
41 | 2635117.1597 | 1231050.0023
42 | 2635144.7856 | 1231076.4578
43 | 2635151.074 | 1231086.7364
44 | 2635152.4848 | 1231087.8785
45 | 2635168.1639 | 1231096.7544
46 | 2635003.3484 | 1231249.8722
47 | 2634963.7839 | 1231226.3422
48 | 2634939.5845 | 1231225.1442
49 | 2634899.0944 | 1231294.1583
50 | 2634902.2516 | 1231291.7314
51 | 2634897.5579 | 1231295.3395
52 | 2634915.7026 | 1231289.9985
53 | 2634904.2884 | 1231339.0112
54 | 2634934.9242 | 1231289.6177
55 | 2634889.4269 | 1231410.9689
56 | 2634863.1062 | 1231421.0927
57 | 2634914.9142 | 1231340.9155
58 | 2634934.6227 | 1231344.4475
59 | 2634938.9181 | 1231289.5386
60 | 2634997.3257 | 1231315.764
61 | 2634999.6824 | 1231288.3347
62 | 2635000.4678 | 1231280.9681
63 | 2634960.5053 | 1231289.1109
64 | 2635026.6287 | 1231280.3105
65 | 2635001.2002 | 1231273.0628
66 | 2634956.1166 | 1231289.1978
67 | 2635034.279 | 1231271.3831
68 | 2634945.748 | 1231346.4412
69 | 2635042.026 | 1231253.0621
70 | 2634977.6231 | 1231106.5711

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99445 | -0.038381 | 0.006148 | 0.0015408
1 | 0.99521 | -0.033104 | 0 | 0
2 | 0.99365 | -0.043951 | 0 | 0
3 | 0.99416 | -0.040523 | 0.0057494 | 0.0014409
4 | 0.99717 | -0.019555 | 0.021215 | 0.0053171
5 | 0.99353 | -0.044775 | 0.0012682 | 0.00031785
6 | 0.99228 | -0.053479 | 0.0017667 | 0.00044278
7 | 0.99146 | -0.059475 | 0 | 0
8 | 1 | 0 | -0.22166 | -0.055811
9 | 0.99352 | -0.044859 | 0.00079447 | 0.00019911
10 | 0.99098 | -0.062552 | 0.0012983 | 0.00032537
11 | 0.99028 | -0.067821 | 0.0062675 | 0.0015708
12 | 0.99343 | -0.045535 | 0.0020202 | 0.00050632
13 | 0.98902 | -0.076234 | 0.0013198 | 0.00033077
14 | 0.98989 | -0.070569 | 0.014252 | 0.003572
15 | 0.98908 | -0.076267 | 0.017809 | 0.0044634
16 | 0.97224 | -0.19535 | 0.0065054 | 0.0016304
17 | 0.97227 | -0.19517 | 0.011124 | 0.002788
18 | 0.97245 | -0.19383 | 0.013159 | 0.0032981
19 | 0.9739 | -0.18339 | 0 | 0
20 | 0.97441 | -0.17976 | 0 | 0
21 | 0.97423 | -0.18107 | 0.0061886 | 0.001551
22 | 0.97544 | -0.17239 | 0.002248 | 0.0005634
23 | 0.97583 | -0.16961 | 0.0020691 | 0.00051856
24 | 0.98458 | -0.10744 | 0 | 0
25 | 0.98409 | -0.11094 | 0.0034432 | 0.00086294
26 | 0.98334 | -0.11622 | 0 | 0
27 | 0.98576 | -0.099165 | 0.00052817 | 0.00013237
28 | 0.98394 | -0.11199 | 0 | 0
29 | 0.98293 | -0.11914 | 0.0058299 | 0.0014611
30 | 0.98159 | -0.12857 | 0 | 0
31 | 0.9875 | -0.086931 | 0 | 0
32 | 0.98723 | -0.088809 | 0.0025149 | 0.0006303
33 | 0.98731 | -0.088259 | 0.0014764 | 0.00037002
34 | 0.98381 | -0.11292 | 0.0088678 | 0.0022225
35 | 0.98683 | -0.091626 | 0.0012004 | 0.00030085
36 | 0.98646 | -0.094319 | 0.0016604 | 0.00041614
37 | 0.98604 | -0.097255 | 0.0025146 | 0.00063023
38 | 0.98588 | -0.098384 | 0.0016973 | 0.00042537
39 | 0.98559 | -0.10045 | 0.0011557 | 0.00028965
40 | 0.98538 | -0.10197 | 0.0012158 | 0.0003047
41 | 0.98493 | -0.10513 | 0 | 0
42 | 0.98423 | -0.11014 | 0.0021715 | 0.00054423
43 | 0.98407 | -0.11127 | 0.0022499 | 0.00056387
44 | 0.98405 | -0.11139 | 0.0025953 | 0.00065044
45 | 0.98395 | -0.11212 | 0.0039535 | 0.00099085
46 | 0.97978 | -0.14147 | 0.0035909 | 0.00089995
47 | 0.97867 | -0.14935 | 0.0023128 | 0.00057965
48 | 0.97709 | -0.16057 | 0.0030645 | 0.00076805
49 | 0.97455 | -0.17887 | 0.0010382 | 0.00026019
50 | 0.97461 | -0.17847 | 0.0033667 | 0.00084377
51 | 0.97453 | -0.17905 | 0.0015635 | 0.00039184
52 | 0.97487 | -0.1766 | 0.0038888 | 0.00097464
53 | 0.97407 | -0.18233 | 0.0010946 | 0.00027433
54 | 0.97534 | -0.17319 | 0.00089809 | 0.00022508
55 | 0.97374 | -0.18476 | 0.0016536 | 0.00041442
56 | 0.97367 | -0.1852 | 0.0014838 | 0.00037188
57 | 0.97403 | -0.18265 | 0.00086734 | 0.00021737
58 | 0.97397 | -0.18306 | 0.0011112 | 0.00027849
59 | 0.97545 | -0.17244 | 0.0030717 | 0.00076985
60 | 0.97745 | -0.15813 | 0.0015156 | 0.00037984
61 | 0.97751 | -0.15769 | 0 | 0
62 | 0.97779 | -0.15569 | 0 | 0
63 | 0.97611 | -0.16767 | 0.0025406 | 0.00063674
64 | 0.97715 | -0.16027 | 0 | 0
65 | 0.97828 | -0.15216 | 0.0013967 | 0.00035005
66 | 0.97597 | -0.16867 | 0.00091076 | 0.00022826
67 | 0.97684 | -0.16246 | 0.0023222 | 0.00058199
68 | 0.97396 | -0.18316 | 0.00083101 | 0.00020827
69 | 0.97642 | -0.16547 | 0.01446 | 0.003624
70 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.15425 | -0.038945 | 0.15437 | 0.038989 | 0.00011446 | 4.362e-05 | 0.23091 | 0.23091 | 0.23091 | 0.99445 | -0.038381 | 0.99521 | -0.033104 | 28.5076
1 | 0.1481 | 0.037404 | -0.14799 | -0.03736 | 0.0001159 | 4.4134e-05 | 0.22171 | 0.22171 | 0.22171 | 0.99445 | -0.038381 | 0.99365 | -0.043951 | 27.3719
2 | 0.044296 | 0.011129 | -0.044251 | -0.011112 | 4.5674e-05 | 1.7351e-05 | 0.06624 | 0.06624 | 0.06624 | 0.99521 | -0.033104 | 0.99416 | -0.040523 | 24.5334
3 | -0.19866 | -0.050117 | 0.19904 | 0.050262 | 0.0003783 | 0.0001447 | 0.29715 | 0.29715 | 0.29715 | 0.99521 | -0.033104 | 0.99717 | -0.019555 | 36.6854
4 | 0.0040836 | 0.0010228 | -0.0040832 | -0.0010229 | 4.6493e-07 | -7.9237e-08 | 0.0061151 | 0.0061152 | 0.0061152 | 0.99365 | -0.043951 | 0.99353 | -0.044775 | 2.2649
5 | 0.14391 | 0.036337 | -0.14371 | -0.036264 | 0.00019243 | 7.3237e-05 | 0.2156 | 0.2156 | 0.2156 | 0.99365 | -0.043951 | 0.99228 | -0.053479 | 26.617
6 | 0.038501 | 0.0096706 | -0.0384 | -0.0096323 | 0.00010119 | 3.8288e-05 | 0.057635 | 0.057635 | 0.057635 | 0.99416 | -0.040523 | 0.99146 | -0.059475 | 21.3462
7 | -0.22026 | -0.055579 | 0.22086 | 0.055811 | 0.00060619 | 0.00023209 | 0.32881 | 0.32881 | 0.32881 | 0.99717 | -0.019555 | 1 | 0 | 40.5938
8 | 0.0028149 | 0.00070505 | -0.0028149 | -0.00070507 | 3.2729e-08 | -2.563e-08 | 0.0042158 | 0.0042158 | 0.0042158 | 0.99353 | -0.044775 | 0.99352 | -0.044859 | 1.5614
9 | 0.14195 | 0.035821 | -0.14177 | -0.035752 | 0.00018055 | 6.8702e-05 | 0.21295 | 0.21295 | 0.21295 | 0.99228 | -0.053479 | 0.99098 | -0.062552 | 26.29
10 | 0.0384 | 0.0096323 | -0.038356 | -0.0096155 | 4.4394e-05 | 1.6799e-05 | 0.057635 | 0.057635 | 0.057635 | 0.99146 | -0.059475 | 0.99028 | -0.067821 | 21.3463
11 | 0.0020204 | 0.00050596 | -0.0020202 | -0.00050632 | 1.8907e-07 | -3.5577e-07 | 0.0030259 | 0.003026 | 0.003026 | 0.99352 | -0.044859 | 0.99343 | -0.045535 | 1.1207
12 | 0.14047 | 0.035427 | -0.1402 | -0.035325 | 0.00026892 | 0.00010231 | 0.211 | 0.211 | 0.211 | 0.99098 | -0.062552 | 0.98902 | -0.076234 | 26.0493
13 | 0.01783 | 0.0044708 | -0.017809 | -0.0044634 | 2.0844e-05 | 7.4189e-06 | 0.026793 | 0.026793 | 0.026793 | 0.99028 | -0.067821 | 0.98908 | -0.076267 | 9.9233
14 | 0.014258 | 0.0035739 | -0.014252 | -0.003572 | 5.4236e-06 | 1.8425e-06 | 0.021424 | 0.021425 | 0.021425 | 0.99028 | -0.067821 | 0.98989 | -0.070569 | 7.935
15 | 0.13888 | 0.034994 | -0.13867 | -0.034915 | 0.00020758 | 7.896e-05 | 0.20901 | 0.20901 | 0.20901 | 0.98902 | -0.076234 | 0.9875 | -0.086931 | 25.8042
16 | -0.0065054 | -0.0016304 | 0.0065056 | 0.0016304 | 1.6126e-07 | 2.9694e-08 | 0.0099566 | 0.0099566 | 0.0099566 | 0.97224 | -0.19535 | 0.97227 | -0.19517 | 3.6876
17 | -0.01763 | -0.0044185 | 0.017633 | 0.0044196 | 3.2815e-06 | 1.1725e-06 | 0.026982 | 0.026982 | 0.026982 | 0.97227 | -0.19517 | 0.97245 | -0.19383 | 9.9933
18 | -0.030793 | -0.0077177 | 0.030837 | 0.0077345 | 4.4566e-05 | 1.6741e-05 | 0.047118 | 0.047118 | 0.047118 | 0.97245 | -0.19383 | 0.9739 | -0.18339 | 17.4512
19 | -0.030837 | -0.0077345 | 0.030853 | 0.0077403 | 1.5506e-05 | 5.8246e-06 | 0.047118 | 0.047118 | 0.047118 | 0.9739 | -0.18339 | 0.97441 | -0.17976 | 17.4511
20 | 0.0061897 | 0.0015512 | -0.0061886 | -0.001551 | 1.1202e-06 | 1.8062e-07 | 0.0094523 | 0.0094524 | 0.0094524 | 0.97441 | -0.17976 | 0.97423 | -0.18107 | 3.5009
21 | -0.037043 | -0.0092915 | 0.03708 | 0.0093058 | 3.7911e-05 | 1.4344e-05 | 0.05657 | 0.05657 | 0.05657 | 0.97441 | -0.17976 | 0.97544 | -0.17239 | 20.952
22 | -0.039328 | -0.0098692 | 0.039344 | 0.009875 | 1.5201e-05 | 5.762e-06 | 0.059999 | 0.059999 | 0.059999 | 0.97544 | -0.17239 | 0.97583 | -0.16961 | 22.222
23 | -0.041413 | -0.010394 | 0.041465 | 0.010413 | 5.2008e-05 | 1.9742e-05 | 0.063155 | 0.063154 | 0.063155 | 0.97583 | -0.16961 | 0.97709 | -0.16057 | 23.3906
24 | 0.012319 | 0.003088 | -0.012313 | -0.0030861 | 5.9641e-06 | 1.9434e-06 | 0.018619 | 0.018619 | 0.018619 | 0.98458 | -0.10744 | 0.98409 | -0.11094 | 6.8958
25 | 0.10104 | 0.025438 | -0.10092 | -0.025391 | 0.0001237 | 4.6607e-05 | 0.15274 | 0.15274 | 0.15274 | 0.98458 | -0.10744 | 0.98334 | -0.11622 | 18.8574
26 | -0.11336 | -0.028526 | 0.11349 | 0.028575 | 0.00013109 | 4.9599e-05 | 0.17136 | 0.17136 | 0.17136 | 0.98458 | -0.10744 | 0.98576 | -0.099165 | 21.1559
27 | 0.0088702 | 0.0022231 | -0.0088689 | -0.0022228 | 1.2925e-06 | 3.5086e-07 | 0.013412 | 0.013412 | 0.013412 | 0.98409 | -0.11094 | 0.98394 | -0.11199 | 4.9676
28 | 0.0058323 | 0.0014614 | -0.0058299 | -0.0014611 | 2.3631e-06 | 2.9237e-07 | 0.0088255 | 0.0088257 | 0.0088257 | 0.98334 | -0.11622 | 0.98293 | -0.11914 | 3.2688
29 | 0.095084 | 0.02393 | -0.09492 | -0.023867 | 0.00016372 | 6.2327e-05 | 0.14392 | 0.14392 | 0.14392 | 0.98334 | -0.11622 | 0.98159 | -0.12857 | 26.6518
30 | -0.11402 | -0.028708 | 0.11421 | 0.028782 | 0.00019523 | 7.3874e-05 | 0.17216 | 0.17216 | 0.17216 | 0.98576 | -0.099165 | 0.9875 | -0.086931 | 21.2543
31 | 0.0088689 | 0.0022228 | -0.0088678 | -0.0022225 | 1.138e-06 | 3.0894e-07 | 0.013412 | 0.013413 | 0.013413 | 0.98394 | -0.11199 | 0.98381 | -0.11292 | 4.9676
32 | 0.047873 | 0.012028 | -0.047787 | -0.011996 | 8.5785e-05 | 3.2665e-05 | 0.072582 | 0.072582 | 0.072582 | 0.98159 | -0.12857 | 0.97978 | -0.14147 | 26.8822
33 | 0.047048 | 0.011839 | -0.046912 | -0.011787 | 0.00013604 | 5.1783e-05 | 0.071338 | 0.071338 | 0.071338 | 0.98159 | -0.12857 | 0.97867 | -0.14935 | 26.4214
34 | 0.020465 | 0.0051334 | -0.020452 | -0.0051285 | 1.3315e-05 | 4.8344e-06 | 0.030839 | 0.03084 | 0.03084 | 0.9875 | -0.086931 | 0.98683 | -0.091626 | 11.422
35 | 0.0039922 | 0.00099998 | -0.0039915 | -0.0010001 | 7.3282e-07 | -1.3325e-07 | 0.0060155 | 0.0060157 | 0.0060157 | 0.9875 | -0.086931 | 0.98731 | -0.088259 | 2.228
36 | -0.0025149 | -0.0006303 | 0.0025151 | 0.0006301 | 1.9152e-07 | -1.9949e-07 | 0.0037906 | 0.0037905 | 0.0037906 | 0.98723 | -0.088809 | 0.98731 | -0.088259 | 1.4039
37 | 0.019251 | 0.0048277 | -0.019244 | -0.0048251 | 7.1828e-06 | 2.5882e-06 | 0.029029 | 0.02903 | 0.02903 | 0.98683 | -0.091626 | 0.98646 | -0.094319 | 10.7517
38 | 0.017584 | 0.004409 | -0.017577 | -0.0044064 | 7.1507e-06 | 2.5424e-06 | 0.026525 | 0.026525 | 0.026525 | 0.98646 | -0.094319 | 0.98604 | -0.097255 | 9.8241
39 | 0.015062 | 0.0037762 | -0.01506 | -0.0037754 | 2.3558e-06 | 8.1288e-07 | 0.02273 | 0.02273 | 0.02273 | 0.98604 | -0.097255 | 0.98588 | -0.098384 | 8.4186
40 | 0.013362 | 0.00335 | -0.013358 | -0.0033487 | 3.82e-06 | 1.2774e-06 | 0.020168 | 0.020169 | 0.020169 | 0.98588 | -0.098384 | 0.98559 | -0.10045 | 7.4698
41 | 0.012203 | 0.0030591 | -0.0122 | -0.0030582 | 2.5703e-06 | 8.3397e-07 | 0.018424 | 0.018424 | 0.018424 | 0.98559 | -0.10045 | 0.98538 | -0.10197 | 6.8236
42 | 0.010984 | 0.0027536 | -0.01098 | -0.0027521 | 4.8125e-06 | 1.4941e-06 | 0.016588 | 0.016588 | 0.016588 | 0.98538 | -0.10197 | 0.98493 | -0.10513 | 6.1437
43 | 0.01098 | 0.0027521 | -0.010972 | -0.0027497 | 7.6064e-06 | 2.3621e-06 | 0.016588 | 0.016588 | 0.016588 | 0.98493 | -0.10513 | 0.98423 | -0.11014 | 6.1438
44 | 0.0088005 | 0.0022055 | -0.0087992 | -0.0022051 | 1.3717e-06 | 3.6979e-07 | 0.013305 | 0.013305 | 0.013305 | 0.98423 | -0.11014 | 0.98407 | -0.11127 | 4.9279
45 | 0.0065493 | 0.0016412 | -0.0065492 | -0.0016412 | 1.1108e-07 | 1.9663e-08 | 0.0099032 | 0.0099032 | 0.0099032 | 0.98407 | -0.11127 | 0.98405 | -0.11139 | 3.6678
46 | 0.0039539 | 0.00099077 | -0.0039535 | -0.00099085 | 4.0188e-07 | -7.4297e-08 | 0.0059788 | 0.0059789 | 0.0059789 | 0.98405 | -0.11139 | 0.98395 | -0.11212 | 2.2144
47 | 0.044196 | 0.011096 | -0.04413 | -0.011071 | 6.5488e-05 | 2.4895e-05 | 0.067128 | 0.067128 | 0.067128 | 0.97978 | -0.14147 | 0.97828 | -0.15216 | 24.8624
48 | 0.044599 | 0.011208 | -0.044529 | -0.011181 | 6.9543e-05 | 2.6443e-05 | 0.067821 | 0.067821 | 0.067821 | 0.97867 | -0.14935 | 0.97709 | -0.16057 | 25.1191
49 | -0.0096479 | -0.0024163 | 0.0096485 | 0.0024164 | 5.3918e-07 | 1.5776e-07 | 0.014731 | 0.01473 | 0.014731 | 0.97455 | -0.17887 | 0.97461 | -0.17847 | 5.4557
50 | 0.0086098 | 0.0021561 | -0.0086095 | -0.002156 | 2.0898e-07 | 5.6228e-08 | 0.013145 | 0.013145 | 0.013145 | 0.97455 | -0.17887 | 0.97453 | -0.17905 | 4.8687
51 | -0.013015 | -0.0032602 | 0.013019 | 0.0032613 | 3.3645e-06 | 1.1238e-06 | 0.019871 | 0.019871 | 0.019871 | 0.97461 | -0.17847 | 0.97487 | -0.1766 | 7.3595
52 | 0.0070461 | 0.0017642 | -0.0070429 | -0.0017635 | 3.1913e-06 | 6.7711e-07 | 0.010758 | 0.010758 | 0.010758 | 0.97453 | -0.17905 | 0.97407 | -0.18233 | 3.9846
53 | -0.016907 | -0.004236 | 0.016915 | 0.0042388 | 7.9894e-06 | 2.833e-06 | 0.025806 | 0.025806 | 0.025806 | 0.97487 | -0.1766 | 0.97534 | -0.17319 | 9.558
54 | 0.0028098 | 0.00070371 | -0.0028097 | -0.00070379 | 1.241e-07 | -8.664e-08 | 0.0042921 | 0.0042922 | 0.0042922 | 0.97407 | -0.18233 | 0.97403 | -0.18265 | 1.5897
55 | 0.0031385 | 0.00078548 | -0.0031375 | -0.00078598 | 1.0538e-06 | -5.0898e-07 | 0.0047941 | 0.0047944 | 0.0047944 | 0.97407 | -0.18233 | 0.97374 | -0.18476 | 1.7757
56 | -0.017813 | -0.0044639 | 0.017815 | 0.0044645 | 1.841e-06 | 6.5822e-07 | 0.027177 | 0.027177 | 0.027177 | 0.97534 | -0.17319 | 0.97545 | -0.17244 | 10.0654
57 | 0.0014839 | 0.00037156 | -0.0014838 | -0.00037188 | 9.1535e-08 | -3.1964e-07 | 0.0022675 | 0.0022676 | 0.0022676 | 0.97374 | -0.18476 | 0.97367 | -0.1852 | 0.83987
58 | 0.0019423 | 0.00048642 | -0.0019422 | -0.00048663 | 1.1e-07 | -2.0689e-07 | 0.0029671 | 0.0029672 | 0.0029672 | 0.97403 | -0.18265 | 0.97397 | -0.18306 | 1.099
59 | 0.00083102 | 0.00020813 | -0.00083101 | -0.00020827 | 1.1368e-08 | -1.3629e-07 | 0.0012696 | 0.0012696 | 0.0012696 | 0.97397 | -0.18306 | 0.97396 | -0.18316 | 0.47023
60 | -0.020887 | -0.0052344 | 0.020898 | 0.0052384 | 1.0897e-05 | 3.9764e-06 | 0.031862 | 0.031862 | 0.031862 | 0.97545 | -0.17244 | 0.97597 | -0.16867 | 11.8009
61 | -0.0015156 | -0.00037984 | 0.0015157 | 0.00037953 | 9.1451e-08 | -3.0994e-07 | 0.0023072 | 0.0023071 | 0.0023072 | 0.97745 | -0.15813 | 0.97751 | -0.15769 | 0.85453
62 | -0.025902 | -0.0064965 | 0.025909 | 0.0064991 | 7.1881e-06 | 2.6718e-06 | 0.039431 | 0.039431 | 0.039431 | 0.97751 | -0.15769 | 0.97779 | -0.15569 | 14.604
63 | 0.024386 | 0.0061169 | -0.024352 | -0.0061045 | 3.3698e-05 | 1.247e-05 | 0.037124 | 0.037124 | 0.037124 | 0.97751 | -0.15769 | 0.97611 | -0.16767 | 13.7496
64 | 0.016804 | 0.0042136 | -0.016793 | -0.0042099 | 1.0648e-05 | 3.7683e-06 | 0.025573 | 0.025573 | 0.025573 | 0.97779 | -0.15569 | 0.97715 | -0.16027 | 9.4716
65 | -0.042713 | -0.010713 | 0.042734 | 0.010721 | 2.0934e-05 | 7.9517e-06 | 0.065004 | 0.065004 | 0.065004 | 0.97779 | -0.15569 | 0.97828 | -0.15216 | 24.0756
66 | 0.021812 | 0.0054677 | -0.021809 | -0.0054666 | 3.0284e-06 | 1.1099e-06 | 0.033251 | 0.033251 | 0.033251 | 0.97611 | -0.16767 | 0.97597 | -0.16867 | 12.3151
67 | 0.016793 | 0.0042099 | -0.016788 | -0.0042081 | 5.0945e-06 | 1.8031e-06 | 0.025573 | 0.025573 | 0.025573 | 0.97715 | -0.16027 | 0.97684 | -0.16246 | 9.4716
68 | 0.014466 | 0.0036261 | -0.01446 | -0.003624 | 6.0273e-06 | 2.0693e-06 | 0.022036 | 0.022036 | 0.022036 | 0.97684 | -0.16246 | 0.97642 | -0.16547 | 8.1616

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24157 | 0.0608

## res_load
| p_mw | q_mvar
0 | 0.006148 | 0.0015408
1 | 0.0057494 | 0.0014409
2 | 0.021215 | 0.0053171
3 | 0.0012682 | 0.00031785
4 | 0.0017667 | 0.00044278
5 | 0.019905 | 0.0049887
6 | 0.00079447 | 0.00019911
7 | 0.0012983 | 0.00032537
8 | 0.0062675 | 0.0015708
9 | 0.0020202 | 0.00050632
10 | 0.0013198 | 0.00033077
11 | 0.014252 | 0.003572
12 | 0.017809 | 0.0044634
13 | 0.0065054 | 0.0016304
14 | 0.011124 | 0.002788
15 | 0.013159 | 0.0032981
16 | 0.0061886 | 0.001551
17 | 0.002248 | 0.0005634
18 | 0.0020691 | 0.00051856
19 | 0.0034432 | 0.00086294
20 | 0.00052817 | 0.00013237
21 | 0.0058299 | 0.0014611
22 | 0.0025149 | 0.0006303
23 | 0.0014764 | 0.00037002
24 | 0.0088678 | 0.0022225
25 | 0.0012004 | 0.00030085
26 | 0.0016604 | 0.00041614
27 | 0.0025146 | 0.00063023
28 | 0.0016973 | 0.00042537
29 | 0.0011557 | 0.00028965
30 | 0.0012158 | 0.0003047
31 | 0.0021715 | 0.00054423
32 | 0.0022499 | 0.00056387
33 | 0.0025953 | 0.00065044
34 | 0.0039535 | 0.00099085
35 | 0.0035909 | 0.00089995
36 | 0.0023128 | 0.00057965
37 | 0.0030645 | 0.00076805
38 | 0.0010382 | 0.00026019
39 | 0.0033667 | 0.00084377
40 | 0.0015635 | 0.00039184
41 | 0.0038888 | 0.00097464
42 | 0.0010946 | 0.00027433
43 | 0.00089809 | 0.00022508
44 | 0.0016536 | 0.00041442
45 | 0.0014838 | 0.00037188
46 | 0.00086734 | 0.00021737
47 | 0.0011112 | 0.00027849
48 | 0.0030717 | 0.00076985
49 | 0.0015156 | 0.00037984
50 | 0.0025406 | 0.00063674
51 | 0.0013967 | 0.00035005
52 | 0.00091076 | 0.00022826
53 | 0.0023222 | 0.00058199
54 | 0.00083101 | 0.00020827
55 | 0.01446 | 0.003624

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1