## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1140-11_1_2_node_128 | 0.4 | n |  | TRUE
1 | bus_LV_1140-11_1_2_node_123 | 0.4 | n |  | TRUE
2 | bus_LV_1140-11_1_2_node_129 | 0.4 | n |  | TRUE
3 | bus_LV_1140-11_1_2_node_125 | 0.4 | n |  | TRUE
4 | bus_LV_1140-11_1_2_node_130 | 0.4 | n |  | TRUE
5 | bus_LV_1140-11_1_2_node_131 | 0.4 | n |  | TRUE
6 | bus_LV_1140-11_1_2_node_124 | 0.4 | n |  | TRUE
7 | bus_LV_1140-11_1_2_node_132 | 0.4 | n |  | TRUE
8 | bus_LV_1140-11_1_2_node_133 | 0.4 | n |  | TRUE
9 | bus_LV_1140-11_1_2_node_134 | 0.4 | n |  | TRUE
10 | bus_LV_1140-11_1_2_node_107 | 0.4 | n |  | TRUE
11 | bus_LV_1140-11_1_2_node_76 | 0.4 | n |  | TRUE
12 | bus_LV_1140-11_1_2_node_78 | 0.4 | n |  | TRUE
13 | bus_LV_1140-11_1_2_node_79 | 0.4 | n |  | TRUE
14 | bus_LV_1140-11_1_2_node_81 | 0.4 | n |  | TRUE
15 | bus_LV_1140-11_1_2_node_80 | 0.4 | n |  | TRUE
16 | bus_LV_1140-11_1_2_node_82 | 0.4 | n |  | TRUE
17 | bus_LV_1140-11_1_2_node_100 | 0.4 | n |  | TRUE
18 | bus_LV_1140-11_1_2_node_83 | 0.4 | n |  | TRUE
19 | bus_LV_1140-11_1_2_node_104 | 0.4 | n |  | TRUE
20 | bus_LV_1140-11_1_2_node_98 | 0.4 | n |  | TRUE
21 | bus_LV_1140-11_1_2_node_84 | 0.4 | n |  | TRUE
22 | bus_LV_1140-11_1_2_node_85 | 0.4 | n |  | TRUE
23 | bus_LV_1140-11_1_2_node_87 | 0.4 | n |  | TRUE
24 | bus_LV_1140-11_1_2_node_88 | 0.4 | n |  | TRUE
25 | bus_LV_1140-11_1_2_node_89 | 0.4 | n |  | TRUE
26 | bus_LV_1140-11_1_2_node_90 | 0.4 | n |  | TRUE
27 | bus_LV_1140-11_1_2_node_103 | 0.4 | n |  | TRUE
28 | bus_LV_1140-11_1_2_node_118 | 0.4 | n |  | TRUE
29 | bus_LV_1140-11_1_2_node_91 | 0.4 | n |  | TRUE
30 | bus_LV_1140-11_1_2_node_92 | 0.4 | n |  | TRUE
31 | bus_LV_1140-11_1_2_node_93 | 0.4 | n |  | TRUE
32 | bus_LV_1140-11_1_2_node_94 | 0.4 | n |  | TRUE
33 | bus_LV_1140-11_1_2_node_95 | 0.4 | n |  | TRUE
34 | bus_LV_1140-11_1_2_node_106 | 0.4 | n |  | TRUE
35 | bus_LV_1140-11_1_2_node_102 | 0.4 | n |  | TRUE
36 | bus_LV_1140-11_1_2_node_96 | 0.4 | n |  | TRUE
37 | bus_LV_1140-11_1_2_node_97 | 0.4 | n |  | TRUE
38 | bus_LV_1140-11_1_2_node_99 | 0.4 | n |  | TRUE
39 | bus_LV_1140-11_1_2_node_101 | 0.4 | n |  | TRUE
40 | bus_LV_1140-11_1_2_node_105 | 0.4 | n |  | TRUE
41 | bus_LV_1140-11_1_2_node_108 | 0.4 | n |  | TRUE
42 | bus_LV_1140-11_1_2_node_109 | 0.4 | n |  | TRUE
43 | bus_LV_1140-11_1_2_node_110 | 0.4 | n |  | TRUE
44 | bus_LV_1140-11_1_2_node_111 | 0.4 | n |  | TRUE
45 | bus_LV_1140-11_1_2_node_112 | 0.4 | n |  | TRUE
46 | bus_LV_1140-11_1_2_node_113 | 0.4 | n |  | TRUE
47 | bus_LV_1140-11_1_2_node_114 | 0.4 | n |  | TRUE
48 | bus_LV_1140-11_1_2_node_115 | 0.4 | n |  | TRUE
49 | bus_LV_1140-11_1_2_node_116 | 0.4 | n |  | TRUE
50 | bus_LV_1140-11_1_2_node_117 | 0.4 | n |  | TRUE
51 | bus_LV_1140-11_1_2_node_122 | 0.4 | n |  | TRUE
52 | bus_LV_1140-11_1_2_node_126 | 0.4 | n |  | TRUE
53 | bus_LV_1140-11_1_2_node_119 | 0.4 | n |  | TRUE
54 | bus_LV_1140-11_1_2_node_120 | 0.4 | n |  | TRUE
55 | bus_LV_1140-11_1_2_node_121 | 0.4 | n |  | TRUE
56 | bus_LV_1140-11_1_2_node_127 | 0.4 | n |  | TRUE
57 | bus_MV_475_0_node_49 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1140-11_1_2_load_128 | 0 | 0.001329 | 0.00033307 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1140-11_1_2_load_123 | 1 | 0.00081481 | 0.00020421 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1140-11_1_2_load_129 | 2 | 0.0074116 | 0.0018575 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1140-11_1_2_load_130 | 4 | 0.0057516 | 0.0014415 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1140-11_1_2_load_131 | 5 | 0.0042265 | 0.0010593 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1140-11_1_2_load_133 | 8 | 0.0043917 | 0.0011007 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1140-11_1_2_load_107 | 10 | 0.00063572 | 0.00015933 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1140-11_1_2_load_76 | 11 | 0.0089288 | 0.0022378 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1140-11_1_2_load_79 | 13 | 0.0053101 | 0.0013308 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1140-11_1_2_load_100 | 17 | 0.00044042 | 0.00011038 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1140-11_1_2_load_83 | 18 | 0.01341 | 0.0033609 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1140-11_1_2_load_104 | 19 | 0.0024315 | 0.00060938 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1140-11_1_2_load_84 | 21 | 0.0021186 | 0.00053097 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1140-11_1_2_load_87 | 23 | 0.012333 | 0.0030909 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1140-11_1_2_load_88 | 24 | 0.0022109 | 0.0005541 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1140-11_1_2_load_103 | 27 | 0.0011677 | 0.00029265 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1140-11_1_2_load_118 | 28 | 0.00041369 | 0.00010368 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1140-11_1_2_load_91 | 29 | 0.0036689 | 0.0009195 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1140-11_1_2_load_92 | 30 | 0.0054997 | 0.0013783 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1140-11_1_2_load_93 | 31 | 0.0021908 | 0.00054908 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1140-11_1_2_load_95 | 33 | 0.00087009 | 0.00021806 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1140-11_1_2_load_106 | 34 | 0.0086998 | 0.0021804 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1140-11_1_2_load_102 | 35 | 0.0089238 | 0.0022365 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1140-11_1_2_load_96 | 36 | 0.0015321 | 0.00038399 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1140-11_1_2_load_97 | 37 | 0.00058875 | 0.00014755 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1140-11_1_2_load_99 | 38 | 0.00046015 | 0.00011533 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1140-11_1_2_load_101 | 39 | 0.00044009 | 0.0001103 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1140-11_1_2_load_108 | 41 | 0.0045569 | 0.0011421 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1140-11_1_2_load_109 | 42 | 0.0033483 | 0.00083916 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1140-11_1_2_load_110 | 43 | 0.0039281 | 0.00098447 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1140-11_1_2_load_112 | 45 | 0.003229 | 0.00080927 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1140-11_1_2_load_113 | 46 | 0.0019674 | 0.00049307 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1140-11_1_2_load_115 | 48 | 0.0018537 | 0.00046457 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1140-11_1_2_load_116 | 49 | 0.0014766 | 0.00037006 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1140-11_1_2_load_117 | 50 | 0.0008 | 0.0002005 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1140-11_1_2_load_122 | 51 | 0.00087119 | 0.00021834 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1140-11_1_2_load_126 | 52 | 0.00049942 | 0.00012517 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1140-11_1_2_load_119 | 53 | 0.0047976 | 0.0012024 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1140-11_1_2_load_121 | 55 | 0.00055786 | 0.00013981 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1140-11_1_2_load_127 | 56 | 0.0014752 | 0.00036972 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1140-11_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.010518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1140-11_1_2_line_1 | NAYY 4x150 SE | 1 | 54 | 0.015798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1140-11_1_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.019975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1140-11_1_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.019733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1140-11_1_2_line_4 | NAYY 4x150 SE | 3 | 44 | 0.076882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1140-11_1_2_line_5 | NAYY 4x150 SE | 5 | 6 | 0.022905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1140-11_1_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.0047351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1140-11_1_2_line_7 | NAYY 4x150 SE | 6 | 44 | 0.014394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1140-11_1_2_line_8 | NAYY 4x150 SE | 7 | 8 | 0.01662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1140-11_1_2_line_9 | NAYY 4x150 SE | 8 | 9 | 0.02924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1140-11_1_2_line_10 | NAYY 4x150 SE | 9 | 10 | 0.016747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1140-11_1_2_line_11 | NAYY 4x150 SE | 10 | 40 | 0.029181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1140-11_1_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.014484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1140-11_1_2_line_13 | NAYY 4x150 SE | 12 | 13 | 0.014473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1140-11_1_2_line_14 | NAYY 4x150 SE | 13 | 14 | 0.0642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1140-11_1_2_line_15 | NAYY 4x150 SE | 14 | 16 | 0.007202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1140-11_1_2_line_16 | NAYY 4x150 SE | 14 | 18 | 0.044657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1140-11_1_2_line_17 | NAYY 4x150 SE | 15 | 16 | 0.009228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1140-11_1_2_line_18 | NAYY 4x150 SE | 15 | 17 | 0.014166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1140-11_1_2_line_19 | NAYY 4x150 SE | 16 | 19 | 0.015649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1140-11_1_2_line_20 | NAYY 4x150 SE | 17 | 38 | 0.022142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1140-11_1_2_line_21 | NAYY 4x150 SE | 18 | 20 | 0.029455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1140-11_1_2_line_22 | NAYY 4x150 SE | 19 | 40 | 0.021474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1140-11_1_2_line_23 | NAYY 4x150 SE | 20 | 23 | 0.044811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1140-11_1_2_line_24 | NAYY 4x150 SE | 20 | 37 | 0.056747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1140-11_1_2_line_25 | NAYY 4x150 SE | 21 | 22 | 0.024435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1140-11_1_2_line_26 | NAYY 4x150 SE | 22 | 23 | 0.034678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1140-11_1_2_line_27 | NAYY 4x150 SE | 22 | 24 | 0.0037458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1140-11_1_2_line_28 | NAYY 4x150 SE | 25 | 26 | 0.020037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1140-11_1_2_line_29 | NAYY 4x150 SE | 25 | 27 | 0.017076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1140-11_1_2_line_30 | NAYY 4x150 SE | 26 | 28 | 0.026627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1140-11_1_2_line_31 | NAYY 4x150 SE | 27 | 35 | 0.044053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1140-11_1_2_line_32 | NAYY 4x150 SE | 28 | 53 | 0.033612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1140-11_1_2_line_33 | NAYY 4x150 SE | 29 | 30 | 0.035588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1140-11_1_2_line_34 | NAYY 4x150 SE | 29 | 31 | 0.0064906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1140-11_1_2_line_35 | NAYY 4x150 SE | 30 | 32 | 0.018687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1140-11_1_2_line_36 | NAYY 4x150 SE | 31 | 33 | 0.033935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1140-11_1_2_line_37 | NAYY 4x150 SE | 32 | 34 | 0.023748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1140-11_1_2_line_38 | NAYY 4x150 SE | 33 | 35 | 0.0051135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1140-11_1_2_line_39 | NAYY 4x150 SE | 34 | 40 | 0.024029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1140-11_1_2_line_40 | NAYY 4x150 SE | 36 | 37 | 0.00020995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1140-11_1_2_line_41 | NAYY 4x150 SE | 38 | 39 | 0.0026638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1140-11_1_2_line_42 | NAYY 4x150 SE | 41 | 42 | 0.025588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1140-11_1_2_line_43 | NAYY 4x150 SE | 41 | 43 | 0.022101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1140-11_1_2_line_44 | NAYY 4x150 SE | 42 | 44 | 0.014358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1140-11_1_2_line_45 | NAYY 4x150 SE | 43 | 45 | 0.0042622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1140-11_1_2_line_46 | NAYY 4x150 SE | 46 | 47 | 0.0066483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1140-11_1_2_line_47 | NAYY 4x150 SE | 46 | 48 | 0.016693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1140-11_1_2_line_48 | NAYY 4x150 SE | 47 | 49 | 0.018005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1140-11_1_2_line_49 | NAYY 4x150 SE | 47 | 50 | 0.021502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1140-11_1_2_line_50 | NAYY 4x150 SE | 49 | 51 | 0.01939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1140-11_1_2_line_51 | NAYY 4x150 SE | 50 | 52 | 0.0018785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1140-11_1_2_line_52 | NAYY 4x150 SE | 51 | 55 | 0.00039066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1140-11_1_2_line_53 | NAYY 4x150 SE | 52 | 56 | 0.022018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1140-11_1_2_line_54 | NAYY 4x150 SE | 53 | 54 | 0.010734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1140-11_1_2_line_55 | NAYY 4x150 SE | 54 | 55 | 0.032238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1140-11_1_2_trafo_91 | 0.25 MVA 20/0.4 kV | 57 | 29 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2639684.0607 | 1230783.8555 | 2639676.9214 | 1230791.5788
1 | 2639666.1976 | 1230803.1799 | 2639676.9214 | 1230791.5788
2 | 2639803.5334 | 1230931.7874 | 2639792.9372 | 1230914.854
3 | 2639782.4695 | 1230898.1258 | 2639792.9372 | 1230914.854
4 | 2639739.9078 | 1230972.7098 | 2639754.0643 | 1230967.9125 | 2639772.3288 | 1230959.2403 | 2639788.7378 | 1230947.1869 | 2639803.5334 | 1230931.7874
5 | 2639746.1373 | 1230985.6928 | 2639741.917 | 1230987.1099 | 2639739.5717 | 1230993.5427 | 2639734.5103 | 1231003.9875
6 | 2639732.4454 | 1231008.2487 | 2639734.5103 | 1231003.9875
7 | 2639739.9078 | 1230972.7098 | 2639746.1373 | 1230985.6928
8 | 2639732.4454 | 1231008.2487 | 2639730.2979 | 1231008.8792 | 2639724.9419 | 1231019.3277 | 2639722.587 | 1231018.1334
9 | 2639708.5831 | 1231042.0659 | 2639717.1593 | 1231024.579 | 2639718.8365 | 1231025.1794 | 2639722.587 | 1231018.1334
10 | 2639708.5831 | 1231042.0659 | 2639693.9867 | 1231033.8551
11 | 2639668.6714 | 1231019.3746 | 2639671.2193 | 1231021.1705 | 2639675.0001 | 1231023.1747 | 2639693.9867 | 1231033.8551
12 | 2639634.1209 | 1231134.2934 | 2639632.409 | 1231148.6762
13 | 2639634.1209 | 1231134.2934 | 2639635.7554 | 1231119.9132
14 | 2639644.9916 | 1231056.551 | 2639641.844 | 1231066.3472 | 2639635.7554 | 1231119.9132
15 | 2639644.9916 | 1231056.551 | 2639647.6717 | 1231049.8647
16 | 2639644.9916 | 1231056.551 | 2639620.6467 | 1231039.0002 | 2639608.9496 | 1231030.188
17 | 2639647.6717 | 1231049.8647 | 2639656.1442 | 1231053.579
18 | 2639656.1442 | 1231053.579 | 2639669.1163 | 1231059.2709
19 | 2639647.6717 | 1231049.8647 | 2639650.0967 | 1231045.1001 | 2639655.6797 | 1231036.441
20 | 2639684.6159 | 1231055.7258 | 2639680.7159 | 1231064.3606 | 2639669.1163 | 1231059.2709
21 | 2639585.667 | 1231012.5956 | 2639591.7543 | 1231015.1154 | 2639608.9139 | 1231030.1611 | 2639608.9496 | 1231030.188
22 | 2639668.6714 | 1231019.3746 | 2639658.9047 | 1231031.4392 | 2639655.6797 | 1231036.441
23 | 2639585.667 | 1231012.5956 | 2639573.0256 | 1230992.3101 | 2639560.2076 | 1230975.7914
24 | 2639585.667 | 1231012.5956 | 2639578.985 | 1231011.7951 | 2639572.469 | 1231013.3639 | 2639560.844 | 1231020.1797 | 2639537.305 | 1231038.5187
25 | 2639542.4128 | 1230946.9119 | 2639544.8248 | 1230942.9477 | 2639556.6071 | 1230927.0409
26 | 2639542.4128 | 1230946.9119 | 2639543.515 | 1230954.2793 | 2639560.2076 | 1230975.7914
27 | 2639542.4128 | 1230946.9119 | 2639539.1812 | 1230948.806
28 | 2639607.1133 | 1230835.3731 | 2639607.4876 | 1230844.0031 | 2639608.0249 | 1230848.6095 | 2639610.2469 | 1230854.9949
29 | 2639610.2469 | 1230854.9949 | 2639617.0379 | 1230870.6622
30 | 2639607.1133 | 1230835.3731 | 2639619.569 | 1230834.6666 | 2639633.5382 | 1230832.4035
31 | 2639638.8024 | 1230908.8498 | 2639638.3609 | 1230908.2817 | 2639621.6964 | 1230881.4097 | 2639617.0379 | 1230870.6622
32 | 2639633.5382 | 1230832.4035 | 2639634.0048 | 1230832.328 | 2639642.7754 | 1230827.728 | 2639650.5397 | 1230820.6975 | 2639659.0441 | 1230811.1831
33 | 2639669.3029 | 1230942.4963 | 2639674.9796 | 1230947.9058 | 2639690.6786 | 1230963.9092 | 2639693.4924 | 1230968.4338
34 | 2639669.3029 | 1230942.4963 | 2639664.6041 | 1230938.0187
35 | 2639701.8063 | 1230985.1299 | 2639697.5751 | 1230975.6959 | 2639696.4483 | 1230973.1868 | 2639693.4924 | 1230968.4338
36 | 2639641.9406 | 1230912.8871 | 2639652.5381 | 1230926.5208 | 2639664.6041 | 1230938.0187
37 | 2639701.8063 | 1230985.1299 | 2639690.5211 | 1230995.4722 | 2639684.2985 | 1231001.1757
38 | 2639638.8024 | 1230908.8498 | 2639641.9406 | 1230912.8871
39 | 2639668.6714 | 1231019.3746 | 2639680.8513 | 1231004.3354 | 2639684.2985 | 1231001.1757
40 | 2639537.1393 | 1231038.6477 | 2639537.305 | 1231038.5187
41 | 2639685.7124 | 1231053.2981 | 2639684.6159 | 1231055.7258
42 | 2639726.2998 | 1230936.3479 | 2639726.1468 | 1230936.4289 | 2639724.9086 | 1230939.2557 | 2639726.1035 | 1230942.9104 | 2639733.8727 | 1230959.6818
43 | 2639726.2998 | 1230936.3479 | 2639741.644 | 1230928.2272 | 2639744.4492 | 1230924.4054
44 | 2639739.9078 | 1230972.7098 | 2639733.8727 | 1230959.6818
45 | 2639746.9712 | 1230920.9694 | 2639744.4492 | 1230924.4054
46 | 2639701.585 | 1230862.8305 | 2639704.574 | 1230868.769
47 | 2639712.0791 | 1230883.6801 | 2639704.574 | 1230868.769
48 | 2639701.585 | 1230862.8305 | 2639693.4908 | 1230846.7474
49 | 2639701.585 | 1230862.8305 | 2639682.9751 | 1230873.6014
50 | 2639693.4908 | 1230846.7474 | 2639684.7739 | 1230829.4271
51 | 2639681.3493 | 1230874.5424 | 2639682.9751 | 1230873.6014
52 | 2639684.7739 | 1230829.4271 | 2639684.5983 | 1230829.0781
53 | 2639662.2931 | 1230885.5715 | 2639681.3493 | 1230874.5424
54 | 2639666.1976 | 1230803.1799 | 2639659.0441 | 1230811.1831
55 | 2639666.1976 | 1230803.1799 | 2639676.5005 | 1230812.988 | 2639684.5983 | 1230829.0781

## bus_geodata
| x | y | coords
0 | 2639684.0607 | 1230783.8555
1 | 2639676.9214 | 1230791.5788
2 | 2639792.9372 | 1230914.854
3 | 2639803.5334 | 1230931.7874
4 | 2639782.4695 | 1230898.1258
5 | 2639734.5103 | 1231003.9875
6 | 2639746.1373 | 1230985.6928
7 | 2639732.4454 | 1231008.2487
8 | 2639722.587 | 1231018.1334
9 | 2639708.5831 | 1231042.0659
10 | 2639693.9867 | 1231033.8551
11 | 2639632.409 | 1231148.6762
12 | 2639634.1209 | 1231134.2934
13 | 2639635.7554 | 1231119.9132
14 | 2639644.9916 | 1231056.551
15 | 2639656.1442 | 1231053.579
16 | 2639647.6717 | 1231049.8647
17 | 2639669.1163 | 1231059.2709
18 | 2639608.9496 | 1231030.188
19 | 2639655.6797 | 1231036.441
20 | 2639585.667 | 1231012.5956
21 | 2639556.6071 | 1230927.0409
22 | 2639542.4128 | 1230946.9119
23 | 2639560.2076 | 1230975.7914
24 | 2639539.1812 | 1230948.806
25 | 2639610.2469 | 1230854.9949
26 | 2639607.1133 | 1230835.3731
27 | 2639617.0379 | 1230870.6622
28 | 2639633.5382 | 1230832.4035
29 | 2639669.3029 | 1230942.4963
30 | 2639693.4924 | 1230968.4338
31 | 2639664.6041 | 1230938.0187
32 | 2639701.8063 | 1230985.1299
33 | 2639641.9406 | 1230912.8871
34 | 2639684.2985 | 1231001.1757
35 | 2639638.8024 | 1230908.8498
36 | 2639537.1393 | 1231038.6477
37 | 2639537.305 | 1231038.5187
38 | 2639684.6159 | 1231055.7258
39 | 2639685.7124 | 1231053.2981
40 | 2639668.6714 | 1231019.3746
41 | 2639726.2998 | 1230936.3479
42 | 2639733.8727 | 1230959.6818
43 | 2639744.4492 | 1230924.4054
44 | 2639739.9078 | 1230972.7098
45 | 2639746.9712 | 1230920.9694
46 | 2639704.574 | 1230868.769
47 | 2639701.585 | 1230862.8305
48 | 2639712.0791 | 1230883.6801
49 | 2639693.4908 | 1230846.7474
50 | 2639682.9751 | 1230873.6014
51 | 2639684.7739 | 1230829.4271
52 | 2639681.3493 | 1230874.5424
53 | 2639659.0441 | 1230811.1831
54 | 2639666.1976 | 1230803.1799
55 | 2639684.5983 | 1230829.0781
56 | 2639662.2931 | 1230885.5715
57 | 2639701.8063 | 1230985.1299

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99445 | -0.038895 | 0.001329 | 0.00033307
1 | 0.99447 | -0.038754 | 0.00081481 | 0.00020421
2 | 0.97725 | -0.15975 | 0.0074116 | 0.0018575
3 | 0.97764 | -0.15701 | 0 | 0
4 | 0.97709 | -0.16094 | 0.0057516 | 0.0014415
5 | 0.98065 | -0.1355 | 0.0042265 | 0.0010593
6 | 0.97971 | -0.14222 | 0 | 0
7 | 0.98087 | -0.1339 | 0 | 0
8 | 0.98166 | -0.12831 | 0.0043917 | 0.0011007
9 | 0.98323 | -0.11716 | 0 | 0
10 | 0.98413 | -0.11079 | 0.00063572 | 0.00015933
11 | 0.98087 | -0.13396 | 0.0089288 | 0.0022378
12 | 0.98106 | -0.13261 | 0 | 0
13 | 0.98125 | -0.13127 | 0.0053101 | 0.0013308
14 | 0.98258 | -0.12181 | 0 | 0
15 | 0.98305 | -0.11848 | 0 | 0
16 | 0.98306 | -0.11835 | 0 | 0
17 | 0.98302 | -0.11867 | 0.00044042 | 0.00011038
18 | 0.98048 | -0.13671 | 0.01341 | 0.0033609
19 | 0.98415 | -0.11063 | 0.0024315 | 0.00060938
20 | 0.97968 | -0.14246 | 0 | 0
21 | 0.9783 | -0.15235 | 0.0021186 | 0.00053097
22 | 0.97837 | -0.15181 | 0 | 0
23 | 0.97859 | -0.15024 | 0.012333 | 0.0030909
24 | 0.97836 | -0.15189 | 0.0022109 | 0.0005541
25 | 0.99662 | -0.02365 | 0 | 0
26 | 0.99614 | -0.02705 | 0 | 0
27 | 0.99703 | -0.020754 | 0.0011677 | 0.00029265
28 | 0.99549 | -0.031573 | 0.00041369 | 0.00010368
29 | 1 | 0 | -0.13471 | -0.033816
30 | 0.99473 | -0.036406 | 0.0054997 | 0.0013783
31 | 0.99972 | -0.0019467 | 0.0021908 | 0.00054908
32 | 0.99211 | -0.054635 | 0 | 0
33 | 0.99837 | -0.011397 | 0.00087009 | 0.00021806
34 | 0.98878 | -0.07794 | 0.0086998 | 0.0021804
35 | 0.99817 | -0.012779 | 0.0089238 | 0.0022365
36 | 0.9795 | -0.14372 | 0.0015321 | 0.00038399
37 | 0.9795 | -0.14372 | 0.00058875 | 0.00014755
38 | 0.98299 | -0.11888 | 0.00046015 | 0.00011533
39 | 0.98299 | -0.11889 | 0.00044009 | 0.0001103
40 | 0.98572 | -0.099532 | 0 | 0
41 | 0.97836 | -0.15183 | 0.0045569 | 0.0011421
42 | 0.9788 | -0.1487 | 0.0033483 | 0.00083916
43 | 0.97813 | -0.15348 | 0.0039281 | 0.00098447
44 | 0.97911 | -0.14645 | 0 | 0
45 | 0.97811 | -0.15362 | 0.003229 | 0.00080927
46 | 0.99365 | -0.044585 | 0.0019674 | 0.00049307
47 | 0.99368 | -0.044328 | 0 | 0
48 | 0.9936 | -0.044898 | 0.0018537 | 0.00046457
49 | 0.99385 | -0.043127 | 0.0014766 | 0.00037006
50 | 0.9936 | -0.044932 | 0.0008 | 0.0002005
51 | 0.99408 | -0.041544 | 0.00087119 | 0.00021834
52 | 0.99359 | -0.044969 | 0.00049942 | 0.00012517
53 | 0.9947 | -0.037149 | 0.0047976 | 0.0012024
54 | 0.99452 | -0.038412 | 0 | 0
55 | 0.99408 | -0.041508 | 0.00055786 | 0.00013981
56 | 0.99355 | -0.045298 | 0.0014752 | 0.00036972
57 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.001329 | -0.00033307 | 0.001329 | 0.00033295 | 2.5952e-08 | -1.2648e-07 | 0.0019886 | 0.0019885 | 0.0019886 | 0.99445 | -0.038895 | 0.99447 | -0.038754 | 0.73651
1 | -0.0021438 | -0.00053716 | 0.0021439 | 0.00053699 | 1.0143e-07 | -1.6597e-07 | 0.0032077 | 0.0032076 | 0.0032077 | 0.99447 | -0.038754 | 0.99452 | -0.038412 | 1.188
2 | -0.013164 | -0.0032991 | 0.013169 | 0.0033008 | 5.008e-06 | 1.6758e-06 | 0.020044 | 0.020044 | 0.020044 | 0.97725 | -0.15975 | 0.97764 | -0.15701 | 7.4238
3 | 0.0057525 | 0.0014416 | -0.0057516 | -0.0014415 | 9.4473e-07 | 1.1615e-07 | 0.0087591 | 0.0087592 | 0.0087592 | 0.97725 | -0.15975 | 0.97709 | -0.16094 | 3.2441
4 | -0.013169 | -0.0033008 | 0.013188 | 0.0033073 | 1.9274e-05 | 6.4478e-06 | 0.020044 | 0.020044 | 0.020044 | 0.97764 | -0.15701 | 0.97911 | -0.14645 | 7.4238
5 | 0.028305 | 0.0071019 | -0.028279 | -0.007092 | 2.637e-05 | 9.8534e-06 | 0.042953 | 0.042953 | 0.042953 | 0.98065 | -0.1355 | 0.97971 | -0.14222 | 15.9084
6 | -0.032532 | -0.0081611 | 0.032539 | 0.0081638 | 7.2006e-06 | 2.7097e-06 | 0.049366 | 0.049366 | 0.049366 | 0.98065 | -0.1355 | 0.98087 | -0.1339 | 18.2836
7 | 0.028279 | 0.007092 | -0.028262 | -0.0070858 | 1.6571e-05 | 6.1923e-06 | 0.042953 | 0.042953 | 0.042953 | 0.97971 | -0.14222 | 0.97911 | -0.14645 | 15.9084
8 | -0.032539 | -0.0081638 | 0.032564 | 0.0081733 | 2.5273e-05 | 9.5106e-06 | 0.049366 | 0.049366 | 0.049366 | 0.98087 | -0.1339 | 0.98166 | -0.12831 | 18.2836
9 | -0.036956 | -0.009274 | 0.037013 | 0.0092957 | 5.7266e-05 | 2.1655e-05 | 0.056023 | 0.056023 | 0.056023 | 0.98166 | -0.12831 | 0.98323 | -0.11716 | 20.7492
10 | -0.037013 | -0.0092957 | 0.037046 | 0.0093081 | 3.2799e-05 | 1.2402e-05 | 0.056023 | 0.056023 | 0.056023 | 0.98323 | -0.11716 | 0.98413 | -0.11079 | 20.7491
11 | -0.037682 | -0.0094674 | 0.037741 | 0.0094898 | 5.9127e-05 | 2.237e-05 | 0.056984 | 0.056984 | 0.056984 | 0.98413 | -0.11079 | 0.98572 | -0.099532 | 21.1051
12 | -0.0089288 | -0.0022378 | 0.0089305 | 0.0022382 | 1.6583e-06 | 4.5494e-07 | 0.013545 | 0.013545 | 0.013545 | 0.98087 | -0.13396 | 0.98106 | -0.13261 | 5.0168
13 | -0.0089305 | -0.0022382 | 0.0089321 | 0.0022387 | 1.657e-06 | 4.5451e-07 | 0.013545 | 0.013545 | 0.013545 | 0.98106 | -0.13261 | 0.98125 | -0.13127 | 5.0168
14 | -0.014242 | -0.0035695 | 0.014261 | 0.0035759 | 1.8687e-05 | 6.3751e-06 | 0.021598 | 0.021597 | 0.021598 | 0.98125 | -0.13127 | 0.98258 | -0.12181 | 7.9992
15 | -0.046555 | -0.01168 | 0.046578 | 0.011689 | 2.2342e-05 | 8.5016e-06 | 0.070508 | 0.070508 | 0.070508 | 0.98258 | -0.12181 | 0.98306 | -0.11835 | 26.1141
16 | 0.032294 | 0.0081043 | -0.032228 | -0.0080792 | 6.6662e-05 | 2.5075e-05 | 0.04891 | 0.048911 | 0.048911 | 0.98258 | -0.12181 | 0.98048 | -0.13671 | 18.1151
17 | -0.0013407 | -0.00033553 | 0.0013408 | 0.00033542 | 2.3711e-08 | -1.0788e-07 | 0.0020293 | 0.0020292 | 0.0020293 | 0.98305 | -0.11848 | 0.98306 | -0.11835 | 0.75158
18 | 0.0013407 | 0.00033553 | -0.0013407 | -0.0003357 | 3.6401e-08 | -1.6559e-07 | 0.0020293 | 0.0020293 | 0.0020293 | 0.98305 | -0.11848 | 0.98302 | -0.11867 | 0.7516
19 | -0.047918 | -0.012024 | 0.04797 | 0.012044 | 5.138e-05 | 1.9563e-05 | 0.072537 | 0.072537 | 0.072537 | 0.98306 | -0.11835 | 0.98415 | -0.11063 | 26.8656
20 | 0.00090027 | 0.00022532 | -0.00090024 | -0.00022559 | 2.5656e-08 | -2.7083e-07 | 0.0013626 | 0.0013627 | 0.0013627 | 0.98302 | -0.11867 | 0.98299 | -0.11888 | 0.50472
21 | 0.018818 | 0.0047183 | -0.018803 | -0.0047129 | 1.4991e-05 | 5.3945e-06 | 0.028559 | 0.028559 | 0.028559 | 0.98048 | -0.13671 | 0.97968 | -0.14246 | 10.5775
22 | -0.050401 | -0.012653 | 0.050479 | 0.012683 | 7.7831e-05 | 2.9662e-05 | 0.076213 | 0.076213 | 0.076213 | 0.98415 | -0.11063 | 0.98572 | -0.099532 | 28.2272
23 | 0.016681 | 0.004182 | -0.016663 | -0.0041756 | 1.7951e-05 | 6.3407e-06 | 0.025337 | 0.025338 | 0.025338 | 0.97968 | -0.14246 | 0.97859 | -0.15024 | 9.3843
24 | 0.0021213 | 0.00053097 | -0.0021209 | -0.00053154 | 3.6757e-07 | -5.7304e-07 | 0.0032217 | 0.003222 | 0.003222 | 0.97968 | -0.14246 | 0.9795 | -0.14372 | 1.1933
25 | -0.0021186 | -0.00053097 | 0.0021187 | 0.00053072 | 1.5833e-07 | -2.4594e-07 | 0.0032224 | 0.0032223 | 0.0032224 | 0.9783 | -0.15235 | 0.97837 | -0.15181 | 1.1935
26 | -0.0043297 | -0.0010848 | 0.0043306 | 0.0010847 | 9.3828e-07 | -7.4711e-08 | 0.0065849 | 0.0065847 | 0.0065849 | 0.97837 | -0.15181 | 0.97859 | -0.15024 | 2.4389
27 | 0.0022109 | 0.00055406 | -0.0022109 | -0.0005541 | 2.6429e-08 | -3.6874e-08 | 0.0033626 | 0.0033626 | 0.0033626 | 0.97837 | -0.15181 | 0.97836 | -0.15189 | 1.2454
28 | 0.016897 | 0.004237 | -0.016889 | -0.0042342 | 7.9584e-06 | 2.8e-06 | 0.025229 | 0.02523 | 0.02523 | 0.99662 | -0.02365 | 0.99614 | -0.02705 | 9.3443
29 | -0.016897 | -0.004237 | 0.016904 | 0.0042394 | 6.7823e-06 | 2.386e-06 | 0.025229 | 0.025229 | 0.025229 | 0.99662 | -0.02365 | 0.99703 | -0.020754 | 9.3442
30 | 0.016889 | 0.0042342 | -0.016879 | -0.0042305 | 1.0576e-05 | 3.7213e-06 | 0.02523 | 0.02523 | 0.02523 | 0.99614 | -0.02705 | 0.99549 | -0.031573 | 9.3443
31 | -0.018072 | -0.0045321 | 0.018092 | 0.0045392 | 1.9998e-05 | 7.1163e-06 | 0.026972 | 0.026972 | 0.026972 | 0.99703 | -0.020754 | 0.99817 | -0.012779 | 9.9896
32 | 0.016465 | 0.0041268 | -0.016452 | -0.0041224 | 1.2704e-05 | 4.4496e-06 | 0.024611 | 0.024611 | 0.024611 | 0.99549 | -0.031573 | 0.9947 | -0.037149 | 9.1153
33 | 0.10378 | 0.026254 | -0.10325 | -0.026051 | 0.00053019 | 0.00020345 | 0.15452 | 0.15452 | 0.15452 | 1 | 0 | 0.99473 | -0.036406 | 57.2281
34 | 0.030126 | 0.0075614 | -0.030118 | -0.0075584 | 8.1405e-06 | 3.0458e-06 | 0.044833 | 0.044833 | 0.044833 | 1 | 0 | 0.99972 | -0.0019467 | 16.6046
35 | 0.097752 | 0.024672 | -0.097503 | -0.024577 | 0.00024955 | 9.5737e-05 | 0.14629 | 0.14629 | 0.14629 | 0.99473 | -0.036406 | 0.99211 | -0.054635 | 54.1811
36 | 0.027927 | 0.0070093 | -0.027891 | -0.0069957 | 3.6596e-05 | 1.3631e-05 | 0.041572 | 0.041572 | 0.041572 | 0.99972 | -0.0019467 | 0.99837 | -0.011397 | 15.397
37 | 0.097503 | 0.024577 | -0.097186 | -0.024455 | 0.00031713 | 0.00012167 | 0.14629 | 0.14629 | 0.14629 | 0.99211 | -0.054635 | 0.98878 | -0.07794 | 54.1812
38 | 0.027021 | 0.0067776 | -0.027016 | -0.0067757 | 5.1757e-06 | 1.9238e-06 | 0.040275 | 0.040275 | 0.040275 | 0.99837 | -0.011397 | 0.99817 | -0.012779 | 14.9167
39 | 0.088486 | 0.022275 | -0.08822 | -0.022172 | 0.00026602 | 0.00010201 | 0.1332 | 0.1332 | 0.1332 | 0.98878 | -0.07794 | 0.98572 | -0.099532 | 49.3322
40 | -0.0015321 | -0.00038399 | 0.0015321 | 0.00038399 | 7.098e-10 | -2.3695e-09 | 0.0023276 | 0.0023276 | 0.0023276 | 0.9795 | -0.14372 | 0.9795 | -0.14372 | 0.86206
41 | 0.00044009 | 0.00011026 | -0.00044009 | -0.0001103 | 7.377e-10 | -3.3485e-08 | 0.00066618 | 0.00066619 | 0.00066619 | 0.98299 | -0.11888 | 0.98299 | -0.11889 | 0.24674
42 | -0.011716 | -0.0029361 | 0.011721 | 0.0029378 | 5.0695e-06 | 1.6284e-06 | 0.017819 | 0.017819 | 0.017819 | 0.97836 | -0.15183 | 0.9788 | -0.1487 | 6.5995
43 | 0.0071588 | 0.0017941 | -0.0071572 | -0.0017937 | 1.6349e-06 | 3.5135e-07 | 0.010888 | 0.010888 | 0.010888 | 0.97836 | -0.15183 | 0.97813 | -0.15348 | 4.0326
44 | -0.015069 | -0.0037769 | 0.015074 | 0.0037786 | 4.702e-06 | 1.628e-06 | 0.022909 | 0.022909 | 0.022909 | 0.9788 | -0.1487 | 0.97911 | -0.14645 | 8.4848
45 | 0.0032291 | 0.00080924 | -0.003229 | -0.00080927 | 6.4181e-08 | -2.8812e-08 | 0.0049124 | 0.0049124 | 0.0049124 | 0.97813 | -0.15348 | 0.97811 | -0.15362 | 1.8194
46 | -0.0038211 | -0.00095746 | 0.0038213 | 0.00095742 | 1.3584e-07 | -3.3875e-08 | 0.0057222 | 0.0057221 | 0.0057222 | 0.99365 | -0.044585 | 0.99368 | -0.044328 | 2.1193
47 | 0.0018538 | 0.00046439 | -0.0018537 | -0.00046457 | 8.0273e-08 | -1.8535e-07 | 0.002776 | 0.0027761 | 0.0027761 | 0.99365 | -0.044585 | 0.9936 | -0.044898 | 1.0282
48 | -0.0065962 | -0.0016523 | 0.0065973 | 0.0016525 | 1.0961e-06 | 1.883e-07 | 0.0098773 | 0.0098773 | 0.0098773 | 0.99368 | -0.044328 | 0.99385 | -0.043127 | 3.6583
49 | 0.0027749 | 0.00069492 | -0.0027747 | -0.00069511 | 2.3166e-07 | -1.8941e-07 | 0.0041552 | 0.0041553 | 0.0041553 | 0.99368 | -0.044328 | 0.9936 | -0.044932 | 1.539
50 | -0.0080738 | -0.0020226 | 0.0080756 | 0.002023 | 1.768e-06 | 4.2866e-07 | 0.012088 | 0.012088 | 0.012088 | 0.99385 | -0.043127 | 0.99408 | -0.041544 | 4.477
51 | 0.0019747 | 0.00049461 | -0.0019747 | -0.00049463 | 1.0251e-08 | -2.0388e-08 | 0.0029572 | 0.0029572 | 0.0029572 | 0.9936 | -0.044932 | 0.99359 | -0.044969 | 1.0953
52 | -0.0089468 | -0.0022414 | 0.0089469 | 0.0022414 | 4.372e-08 | 1.175e-08 | 0.013392 | 0.013392 | 0.013392 | 0.99408 | -0.041544 | 0.99408 | -0.041508 | 4.96
53 | 0.0014753 | 0.00036946 | -0.0014752 | -0.00036972 | 6.7063e-08 | -2.5936e-07 | 0.0022093 | 0.0022094 | 0.0022094 | 0.99359 | -0.044969 | 0.99355 | -0.045298 | 0.81829
54 | 0.011655 | 0.00292 | -0.011653 | -0.0029193 | 2.036e-06 | 6.4376e-07 | 0.017434 | 0.017435 | 0.017435 | 0.9947 | -0.037149 | 0.99452 | -0.038412 | 6.4572
55 | 0.0095088 | 0.0023823 | -0.0095047 | -0.0023812 | 4.0717e-06 | 1.1479e-06 | 0.014227 | 0.014227 | 0.014227 | 0.99452 | -0.038412 | 0.99408 | -0.041508 | 5.2693

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.13838 | 0.034735

## res_load
| p_mw | q_mvar
0 | 0.001329 | 0.00033307
1 | 0.00081481 | 0.00020421
2 | 0.0074116 | 0.0018575
3 | 0.0057516 | 0.0014415
4 | 0.0042265 | 0.0010593
5 | 0.0043917 | 0.0011007
6 | 0.00063572 | 0.00015933
7 | 0.0089288 | 0.0022378
8 | 0.0053101 | 0.0013308
9 | 0.00044042 | 0.00011038
10 | 0.01341 | 0.0033609
11 | 0.0024315 | 0.00060938
12 | 0.0021186 | 0.00053097
13 | 0.012333 | 0.0030909
14 | 0.0022109 | 0.0005541
15 | 0.0011677 | 0.00029265
16 | 0.00041369 | 0.00010368
17 | 0.0036689 | 0.0009195
18 | 0.0054997 | 0.0013783
19 | 0.0021908 | 0.00054908
20 | 0.00087009 | 0.00021806
21 | 0.0086998 | 0.0021804
22 | 0.0089238 | 0.0022365
23 | 0.0015321 | 0.00038399
24 | 0.00058875 | 0.00014755
25 | 0.00046015 | 0.00011533
26 | 0.00044009 | 0.0001103
27 | 0.0045569 | 0.0011421
28 | 0.0033483 | 0.00083916
29 | 0.0039281 | 0.00098447
30 | 0.003229 | 0.00080927
31 | 0.0019674 | 0.00049307
32 | 0.0018537 | 0.00046457
33 | 0.0014766 | 0.00037006
34 | 0.0008 | 0.0002005
35 | 0.00087119 | 0.00021834
36 | 0.00049942 | 0.00012517
37 | 0.0047976 | 0.0012024
38 | 0.00055786 | 0.00013981
39 | 0.0014752 | 0.00036972

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1