## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1140-17_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1140-17_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1140-17_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1140-17_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1140-17_0_3_node_37 | 0.4 | n |  | TRUE
5 | bus_LV_1140-17_0_3_node_38 | 0.4 | n |  | TRUE
6 | bus_LV_1140-17_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1140-17_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1140-17_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1140-17_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1140-17_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1140-17_0_3_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1140-17_0_3_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_1140-17_0_3_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_1140-17_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1140-17_0_3_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_1140-17_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1140-17_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1140-17_0_3_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1140-17_0_3_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_1140-17_0_3_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_1140-17_0_3_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1140-17_0_3_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1140-17_0_3_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1140-17_0_3_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1140-17_0_3_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1140-17_0_3_node_39 | 0.4 | n |  | TRUE
27 | bus_LV_1140-17_0_3_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_1140-17_0_3_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_1140-17_0_3_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_1140-17_0_3_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_1140-17_0_3_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_1140-17_0_3_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_1140-17_0_3_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_1140-17_0_3_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_1140-17_0_3_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_1140-17_0_3_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_1140-17_0_3_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_1140-17_0_3_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_1140-17_0_3_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_1140-17_0_3_node_42 | 0.4 | n |  | TRUE
41 | bus_LV_1140-17_0_3_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_1140-17_0_3_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_1140-17_0_3_node_44 | 0.4 | n |  | TRUE
44 | bus_LV_1140-17_0_3_node_45 | 0.4 | n |  | TRUE
45 | bus_MV_475_0_node_60 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1140-17_0_3_load_0 | 0 | 0.0092695 | 0.0023232 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1140-17_0_3_load_3 | 3 | 0.0044328 | 0.001111 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1140-17_0_3_load_37 | 4 | 0.00052079 | 0.00013052 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1140-17_0_3_load_4 | 6 | 0.0050309 | 0.0012609 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1140-17_0_3_load_5 | 7 | 0.0026619 | 0.00066715 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1140-17_0_3_load_7 | 9 | 0.0020682 | 0.00051834 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1140-17_0_3_load_8 | 10 | 0.00088045 | 0.00022066 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1140-17_0_3_load_9 | 11 | 0.0012736 | 0.0003192 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1140-17_0_3_load_13 | 12 | 0.0026997 | 0.00067661 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1140-17_0_3_load_15 | 13 | 0.00055655 | 0.00013948 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1140-17_0_3_load_11 | 14 | 0.0033086 | 0.00082922 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1140-17_0_3_load_16 | 15 | 0.0068086 | 0.0017064 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1140-17_0_3_load_10 | 16 | 0.014611 | 0.0036619 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1140-17_0_3_load_14 | 18 | 0.0089866 | 0.0022523 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1140-17_0_3_load_29 | 19 | 0.0035878 | 0.00089918 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1140-17_0_3_load_27 | 20 | 0.02015 | 0.0050501 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1140-17_0_3_load_17 | 21 | 0.0092085 | 0.0023079 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1140-17_0_3_load_18 | 22 | 0.01638 | 0.0041052 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1140-17_0_3_load_19 | 23 | 0.0052144 | 0.0013069 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1140-17_0_3_load_20 | 24 | 0.013842 | 0.0034691 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1140-17_0_3_load_21 | 25 | 0.012457 | 0.0031219 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1140-17_0_3_load_39 | 26 | 0.0052099 | 0.0013057 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1140-17_0_3_load_28 | 29 | 0.0022562 | 0.00056547 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1140-17_0_3_load_22 | 30 | 0.001196 | 0.00029975 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1140-17_0_3_load_23 | 31 | 0.014701 | 0.0036844 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1140-17_0_3_load_24 | 32 | 0.0031316 | 0.00078485 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1140-17_0_3_load_25 | 33 | 0.0053256 | 0.0013347 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1140-17_0_3_load_26 | 34 | 0.0036091 | 0.00090451 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1140-17_0_3_load_35 | 35 | 0.0029691 | 0.00074412 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1140-17_0_3_load_32 | 36 | 0.0038204 | 0.00095748 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1140-17_0_3_load_34 | 37 | 0.015267 | 0.0038264 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1140-17_0_3_load_33 | 38 | 0.0037899 | 0.00094985 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1140-17_0_3_load_36 | 39 | 0.0071339 | 0.0017879 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1140-17_0_3_load_42 | 40 | 0.0035991 | 0.00090202 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1140-17_0_3_load_41 | 41 | 0.0035946 | 0.00090088 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1140-17_0_3_load_43 | 42 | 0.003973 | 0.00099572 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1140-17_0_3_load_45 | 44 | 0.0091703 | 0.0022983 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1140-17_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.030907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1140-17_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.006679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1140-17_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.02113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1140-17_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.037239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1140-17_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.027062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1140-17_0_3_line_5 | NAYY 4x150 SE | 5 | 11 | 0.013463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1140-17_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.026504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1140-17_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.0053455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1140-17_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.0090951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1140-17_0_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.013336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1140-17_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.018204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1140-17_0_3_line_11 | NAYY 4x150 SE | 9 | 12 | 0.025095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1140-17_0_3_line_12 | NAYY 4x150 SE | 10 | 13 | 0.0074506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1140-17_0_3_line_13 | NAYY 4x150 SE | 12 | 14 | 0.010299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1140-17_0_3_line_14 | NAYY 4x150 SE | 13 | 15 | 0.020189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1140-17_0_3_line_15 | NAYY 4x150 SE | 14 | 16 | 0.027003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1140-17_0_3_line_16 | NAYY 4x150 SE | 16 | 17 | 0.037336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1140-17_0_3_line_17 | NAYY 4x150 SE | 17 | 18 | 0.027055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1140-17_0_3_line_18 | NAYY 4x150 SE | 18 | 19 | 0.0079325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1140-17_0_3_line_19 | NAYY 4x150 SE | 19 | 20 | 0.00075099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1140-17_0_3_line_20 | NAYY 4x150 SE | 20 | 29 | 0.0068915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1140-17_0_3_line_21 | NAYY 4x150 SE | 21 | 22 | 0.015979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1140-17_0_3_line_22 | NAYY 4x150 SE | 21 | 23 | 0.020896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1140-17_0_3_line_23 | NAYY 4x150 SE | 22 | 24 | 0.016839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1140-17_0_3_line_24 | NAYY 4x150 SE | 23 | 25 | 0.0073949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1140-17_0_3_line_25 | NAYY 4x150 SE | 24 | 26 | 0.014512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1140-17_0_3_line_26 | NAYY 4x150 SE | 25 | 27 | 0.018069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1140-17_0_3_line_27 | NAYY 4x150 SE | 27 | 28 | 0.019263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1140-17_0_3_line_28 | NAYY 4x150 SE | 27 | 29 | 0.030638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_1140-17_0_3_line_29 | NAYY 4x150 SE | 28 | 39 | 0.0025515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1140-17_0_3_line_30 | NAYY 4x150 SE | 28 | 37 | 0.021564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1140-17_0_3_line_31 | NAYY 4x150 SE | 30 | 31 | 0.00015068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1140-17_0_3_line_32 | NAYY 4x150 SE | 30 | 32 | 0.021175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1140-17_0_3_line_33 | NAYY 4x150 SE | 31 | 33 | 0.013118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1140-17_0_3_line_34 | NAYY 4x150 SE | 32 | 34 | 0.00071004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1140-17_0_3_line_35 | NAYY 4x150 SE | 33 | 35 | 0.008702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1140-17_0_3_line_36 | NAYY 4x150 SE | 34 | 36 | 0.030527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1140-17_0_3_line_37 | NAYY 4x150 SE | 35 | 37 | 0.010645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1140-17_0_3_line_38 | NAYY 4x150 SE | 36 | 38 | 0.0011309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1140-17_0_3_line_39 | NAYY 4x150 SE | 38 | 40 | 0.019888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1140-17_0_3_line_40 | NAYY 4x150 SE | 40 | 41 | 0.020744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1140-17_0_3_line_41 | NAYY 4x150 SE | 41 | 42 | 0.019778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1140-17_0_3_line_42 | NAYY 4x150 SE | 42 | 43 | 0.03703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1140-17_0_3_line_43 | NAYY 4x150 SE | 43 | 44 | 0.016225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1140-17_0_3_trafo_28 | 0.25 MVA 20/0.4 kV | 45 | 29 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2
0 | 2640310.8968 | 1233143.6671 | 2640281.0175 | 1233135.7618
1 | 2640309.1119 | 1233150.1034 | 2640310.8968 | 1233143.6671
2 | 2640310.8968 | 1233143.6671 | 2640316.46 | 1233123.2825
3 | 2640309.1119 | 1233150.1034 | 2640344.9654 | 1233160.166
4 | 2640371.0204 | 1233167.4785 | 2640344.9654 | 1233160.166
5 | 2640371.0204 | 1233167.4785 | 2640383.9828 | 1233171.1163
6 | 2640401.8967 | 1233170.7038 | 2640403.815 | 1233144.2696
7 | 2640401.5098 | 1233176.0352 | 2640401.8967 | 1233170.7038
8 | 2640403.815 | 1233144.2696 | 2640404.4733 | 1233135.1983
9 | 2640401.5098 | 1233176.0352 | 2640401.406 | 1233189.3704
10 | 2640401.5098 | 1233176.0352 | 2640383.9828 | 1233171.1163
11 | 2640406.2897 | 1233110.1694 | 2640404.4733 | 1233135.1983
12 | 2640401.406 | 1233189.3704 | 2640401.348 | 1233196.8208
13 | 2640406.2897 | 1233110.1694 | 2640407.0351 | 1233099.8977
14 | 2640415.498 | 1233210.1176 | 2640401.331 | 1233199.0039 | 2640401.348 | 1233196.8208
15 | 2640408.9895 | 1233072.9661 | 2640407.0351 | 1233099.8977
16 | 2640411.6919 | 1233035.7278 | 2640408.9895 | 1233072.9661
17 | 2640411.6919 | 1233035.7278 | 2640437.8211 | 1233028.7121
18 | 2640445.7008 | 1233027.7985 | 2640437.8211 | 1233028.7121
19 | 2640445.7008 | 1233027.7985 | 2640446.4468 | 1233027.712
20 | 2640446.4468 | 1233027.712 | 2640453.2925 | 1233026.9182
21 | 2640483.7469 | 1232964.1963 | 2640483.7588 | 1232970.0767 | 2640483.7781 | 1232980.1749
22 | 2640483.8179 | 1233001.0708 | 2640483.7781 | 1232980.1749
23 | 2640483.7469 | 1232964.1963 | 2640483.7128 | 1232947.3571
24 | 2640483.832 | 1233008.4657 | 2640483.8179 | 1233001.0708
25 | 2640483.6835 | 1232932.8449 | 2640483.7128 | 1232947.3571
26 | 2640483.8665 | 1233026.535 | 2640483.832 | 1233008.4657
27 | 2640483.8665 | 1233026.535 | 2640498.0178 | 1233029.6666 | 2640502.7273 | 1233030.7104
28 | 2640483.8665 | 1233026.535 | 2640461.6426 | 1233025.9501 | 2640453.2925 | 1233026.9182
29 | 2640502.7273 | 1233030.7104 | 2640505.173 | 1233031.4373
30 | 2640502.7273 | 1233030.7104 | 2640500.89 | 1233052.1958
31 | 2640498.111 | 1233084.6927 | 2640498.1239 | 1233084.5426
32 | 2640496.3068 | 1233105.7911 | 2640498.111 | 1233084.6927
33 | 2640498.1239 | 1233084.5426 | 2640499.2415 | 1233071.4725
34 | 2640496.2463 | 1233106.4985 | 2640496.3068 | 1233105.7911
35 | 2640499.2415 | 1233071.4725 | 2640499.983 | 1233062.8021
36 | 2640493.6454 | 1233136.9142 | 2640496.2463 | 1233106.4985
37 | 2640500.89 | 1233052.1958 | 2640499.983 | 1233062.8021
38 | 2640493.549 | 1233138.041 | 2640493.6454 | 1233136.9142
39 | 2640493.549 | 1233138.041 | 2640493.3004 | 1233140.9484 | 2640490.9421 | 1233157.7535
40 | 2640488.0593 | 1233178.2963 | 2640490.9421 | 1233157.7535
41 | 2640488.0593 | 1233178.2963 | 2640485.3108 | 1233197.8819
42 | 2640479.7027 | 1233234.4699 | 2640481.055 | 1233228.2085 | 2640485.3108 | 1233197.8819
43 | 2640479.7027 | 1233234.4699 | 2640463.5198 | 1233233.2964

## bus_geodata
| x | y | coords
0 | 2640281.0175 | 1233135.7618
1 | 2640310.8968 | 1233143.6671
2 | 2640309.1119 | 1233150.1034
3 | 2640316.46 | 1233123.2825
4 | 2640344.9654 | 1233160.166
5 | 2640371.0204 | 1233167.4785
6 | 2640401.8967 | 1233170.7038
7 | 2640403.815 | 1233144.2696
8 | 2640401.5098 | 1233176.0352
9 | 2640404.4733 | 1233135.1983
10 | 2640401.406 | 1233189.3704
11 | 2640383.9828 | 1233171.1163
12 | 2640406.2897 | 1233110.1694
13 | 2640401.348 | 1233196.8208
14 | 2640407.0351 | 1233099.8977
15 | 2640415.498 | 1233210.1176
16 | 2640408.9895 | 1233072.9661
17 | 2640411.6919 | 1233035.7278
18 | 2640437.8211 | 1233028.7121
19 | 2640445.7008 | 1233027.7985
20 | 2640446.4468 | 1233027.712
21 | 2640483.7781 | 1232980.1749
22 | 2640483.7469 | 1232964.1963
23 | 2640483.8179 | 1233001.0708
24 | 2640483.7128 | 1232947.3571
25 | 2640483.832 | 1233008.4657
26 | 2640483.6835 | 1232932.8449
27 | 2640483.8665 | 1233026.535
28 | 2640502.7273 | 1233030.7104
29 | 2640453.2925 | 1233026.9182
30 | 2640498.111 | 1233084.6927
31 | 2640498.1239 | 1233084.5426
32 | 2640496.3068 | 1233105.7911
33 | 2640499.2416 | 1233071.4725
34 | 2640496.2463 | 1233106.4985
35 | 2640499.983 | 1233062.8021
36 | 2640493.6454 | 1233136.9142
37 | 2640500.89 | 1233052.1958
38 | 2640493.549 | 1233138.041
39 | 2640505.173 | 1233031.4373
40 | 2640490.9421 | 1233157.7535
41 | 2640488.0593 | 1233178.2963
42 | 2640485.3108 | 1233197.8819
43 | 2640479.7027 | 1233234.4699
44 | 2640463.5198 | 1233233.2964
45 | 2640483.8665 | 1233026.535

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98582 | -0.099649 | 0.0092695 | 0.0023232
1 | 0.98623 | -0.096707 | 0 | 0
2 | 0.98636 | -0.095768 | 0 | 0
3 | 0.98609 | -0.097669 | 0.0044328 | 0.001111
4 | 0.9871 | -0.090535 | 0.00052079 | 0.00013052
5 | 0.98766 | -0.086591 | 0 | 0
6 | 0.98852 | -0.080448 | 0.0050309 | 0.0012609
7 | 0.98962 | -0.072662 | 0.0026619 | 0.00066715
8 | 0.98834 | -0.081745 | 0 | 0
9 | 0.99004 | -0.069748 | 0.0020682 | 0.00051834
10 | 0.98818 | -0.082869 | 0.00088045 | 0.00022066
11 | 0.98793 | -0.084631 | 0.0012736 | 0.0003192
12 | 0.99125 | -0.061191 | 0.0026997 | 0.00067661
13 | 0.9881 | -0.08343 | 0.00055655 | 0.00013948
14 | 0.99179 | -0.057404 | 0.0033086 | 0.00082922
15 | 0.9879 | -0.084836 | 0.0068086 | 0.0017064
16 | 0.99333 | -0.046588 | 0.014611 | 0.0036619
17 | 0.99624 | -0.026197 | 0 | 0
18 | 0.99835 | -0.011494 | 0.0089866 | 0.0022523
19 | 0.99907 | -0.006482 | 0.0035878 | 0.00089918
20 | 0.99914 | -0.005981 | 0.02015 | 0.0050501
21 | 0.99335 | -0.046497 | 0.0092085 | 0.0023079
22 | 0.99254 | -0.052229 | 0.01638 | 0.0041052
23 | 0.99469 | -0.037074 | 0.0052144 | 0.0013069
24 | 0.99208 | -0.055481 | 0.013842 | 0.0034691
25 | 0.99522 | -0.033357 | 0.012457 | 0.0031219
26 | 0.99197 | -0.056248 | 0.0052099 | 0.0013057
27 | 0.99684 | -0.022028 | 0 | 0
28 | 0.99458 | -0.037794 | 0 | 0
29 | 1 | 0 | -0.23308 | -0.058453
30 | 0.9897 | -0.072086 | 0.001196 | 0.00029975
31 | 0.98971 | -0.072031 | 0.014701 | 0.0036844
32 | 0.98864 | -0.079581 | 0.0031316 | 0.00078485
33 | 0.99067 | -0.065274 | 0.0053256 | 0.0013347
34 | 0.98861 | -0.07981 | 0.0036091 | 0.00090451
35 | 0.99137 | -0.060329 | 0.0029691 | 0.00074412
36 | 0.98738 | -0.088537 | 0.0038204 | 0.00095748
37 | 0.99228 | -0.053968 | 0.015267 | 0.0038264
38 | 0.98734 | -0.088816 | 0.0037899 | 0.00094985
39 | 0.99455 | -0.037978 | 0.0071339 | 0.0017879
40 | 0.98675 | -0.092962 | 0.0035991 | 0.00090202
41 | 0.98625 | -0.096524 | 0.0035946 | 0.00090088
42 | 0.98588 | -0.099193 | 0.003973 | 0.00099572
43 | 0.98538 | -0.10268 | 0 | 0
44 | 0.98517 | -0.10421 | 0.0091703 | 0.0022983
45 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0092695 | -0.0023232 | 0.0092733 | 0.0023242 | 3.7755e-06 | 1.0579e-06 | 0.013992 | 0.013991 | 0.013992 | 0.98582 | -0.099649 | 0.98623 | -0.096707 | 5.1821
1 | -0.013707 | -0.0034351 | 0.013708 | 0.0034357 | 1.7824e-06 | 6.0032e-07 | 0.02068 | 0.02068 | 0.02068 | 0.98623 | -0.096707 | 0.98636 | -0.095768 | 7.6594
2 | 0.0044334 | 0.0011109 | -0.0044328 | -0.001111 | 5.8994e-07 | -4.2691e-08 | 0.006689 | 0.0066891 | 0.0066891 | 0.98623 | -0.096707 | 0.98609 | -0.097669 | 2.4774
3 | -0.013708 | -0.0034357 | 0.013718 | 0.0034391 | 9.9379e-06 | 3.3466e-06 | 0.02068 | 0.02068 | 0.02068 | 0.98636 | -0.095768 | 0.9871 | -0.090535 | 7.6594
4 | -0.014239 | -0.0035696 | 0.014247 | 0.0035722 | 7.7806e-06 | 2.6464e-06 | 0.021465 | 0.021465 | 0.021465 | 0.9871 | -0.090535 | 0.98766 | -0.086591 | 7.9501
5 | -0.014247 | -0.0035722 | 0.014251 | 0.0035736 | 3.8708e-06 | 1.3164e-06 | 0.021465 | 0.021465 | 0.021465 | 0.98766 | -0.086591 | 0.98793 | -0.084631 | 7.9501
6 | -0.028815 | -0.0072246 | 0.028846 | 0.0072362 | 3.1115e-05 | 1.1627e-05 | 0.043375 | 0.043375 | 0.043375 | 0.98852 | -0.080448 | 0.98962 | -0.072662 | 16.0649
7 | 0.023784 | 0.0059637 | -0.023779 | -0.0059622 | 4.2756e-06 | 1.5759e-06 | 0.035802 | 0.035802 | 0.035802 | 0.98852 | -0.080448 | 0.98834 | -0.081745 | 13.2602
8 | -0.031508 | -0.0079034 | 0.03152 | 0.0079081 | 1.2739e-05 | 4.7828e-06 | 0.047378 | 0.047378 | 0.047378 | 0.98962 | -0.072662 | 0.99004 | -0.069748 | 17.5473
9 | 0.0082488 | 0.0020672 | -0.0082475 | -0.0020669 | 1.2834e-06 | 3.2276e-07 | 0.012419 | 0.012419 | 0.012419 | 0.98834 | -0.081745 | 0.98818 | -0.082869 | 4.5997
10 | 0.015531 | 0.0038949 | -0.015524 | -0.0038928 | 6.2111e-06 | 2.1557e-06 | 0.023383 | 0.023383 | 0.023383 | 0.98834 | -0.081745 | 0.98793 | -0.084631 | 8.6605
11 | -0.033589 | -0.0084265 | 0.033628 | 0.0084415 | 3.9913e-05 | 1.5028e-05 | 0.050486 | 0.050486 | 0.050486 | 0.99004 | -0.069748 | 0.99125 | -0.061191 | 18.6986
12 | 0.007367 | 0.0018463 | -0.0073665 | -0.0018461 | 5.7214e-07 | 1.2461e-07 | 0.011093 | 0.011093 | 0.011093 | 0.98818 | -0.082869 | 0.9881 | -0.08343 | 4.1087
13 | -0.036328 | -0.0091181 | 0.036347 | 0.0091253 | 1.9115e-05 | 7.2191e-06 | 0.054539 | 0.054539 | 0.054539 | 0.99125 | -0.061191 | 0.99179 | -0.057404 | 20.1995
14 | 0.0068099 | 0.0017066 | -0.0068086 | -0.0017064 | 1.325e-06 | 2.5105e-07 | 0.010255 | 0.010255 | 0.010255 | 0.9881 | -0.08343 | 0.9879 | -0.084836 | 3.7983
15 | -0.039656 | -0.0099546 | 0.039716 | 0.0099772 | 5.9657e-05 | 2.2596e-05 | 0.059503 | 0.059503 | 0.059503 | 0.99179 | -0.057404 | 0.99333 | -0.046588 | 22.0381
16 | -0.054327 | -0.013639 | 0.054481 | 0.013698 | 0.00015433 | 5.8874e-05 | 0.081391 | 0.08139 | 0.081391 | 0.99333 | -0.046588 | 0.99624 | -0.026197 | 30.1447
17 | -0.054481 | -0.013698 | 0.054593 | 0.013741 | 0.00011183 | 4.266e-05 | 0.08139 | 0.08139 | 0.08139 | 0.99624 | -0.026197 | 0.99835 | -0.011494 | 30.1446
18 | -0.06358 | -0.015993 | 0.063624 | 0.01601 | 4.447e-05 | 1.7e-05 | 0.094785 | 0.094785 | 0.094785 | 0.99835 | -0.011494 | 0.99907 | -0.006482 | 35.1054
19 | -0.067212 | -0.016909 | 0.067217 | 0.016911 | 4.6982e-06 | 1.7972e-06 | 0.10013 | 0.10013 | 0.10013 | 0.99907 | -0.006482 | 0.99914 | -0.005981 | 37.0845
20 | -0.087367 | -0.021961 | 0.08744 | 0.021989 | 7.283e-05 | 2.7921e-05 | 0.13014 | 0.13014 | 0.13014 | 0.99914 | -0.005981 | 1 | 0 | 48.1992
21 | 0.035469 | 0.0088937 | -0.035441 | -0.0088831 | 2.8148e-05 | 1.062e-05 | 0.053133 | 0.053133 | 0.053133 | 0.99335 | -0.046497 | 0.99254 | -0.052229 | 19.6789
22 | -0.044677 | -0.011202 | 0.044736 | 0.011224 | 5.8405e-05 | 2.2193e-05 | 0.066927 | 0.066927 | 0.066927 | 0.99335 | -0.046497 | 0.99469 | -0.037074 | 24.7878
23 | 0.019061 | 0.0047779 | -0.019052 | -0.0047748 | 8.5806e-06 | 3.0827e-06 | 0.028576 | 0.028576 | 0.028576 | 0.99254 | -0.052229 | 0.99208 | -0.055481 | 10.5838
24 | -0.04995 | -0.012531 | 0.049976 | 0.01254 | 2.5768e-05 | 9.8147e-06 | 0.074728 | 0.074727 | 0.074728 | 0.99469 | -0.037074 | 0.99522 | -0.033357 | 27.6769
25 | 0.0052104 | 0.0013057 | -0.0052099 | -0.0013057 | 5.5308e-07 | 2.5358e-08 | 0.0078151 | 0.0078151 | 0.0078151 | 0.99208 | -0.055481 | 0.99197 | -0.056248 | 2.8945
26 | -0.062433 | -0.015662 | 0.062531 | 0.0157 | 9.8259e-05 | 3.7557e-05 | 0.093352 | 0.093352 | 0.093352 | 0.99522 | -0.033357 | 0.99684 | -0.022028 | 34.5749
27 | 0.08187 | 0.020594 | -0.08169 | -0.020525 | 0.0001796 | 6.8827e-05 | 0.12224 | 0.12224 | 0.12224 | 0.99684 | -0.022028 | 0.99458 | -0.037794 | 45.2729
28 | -0.1444 | -0.036294 | 0.14484 | 0.036464 | 0.00044429 | 0.00017008 | 0.21559 | 0.21559 | 0.21559 | 0.99684 | -0.022028 | 1 | 0 | 39.9238
29 | 0.0071341 | 0.001788 | -0.0071339 | -0.0017879 | 1.8138e-07 | 3.6651e-08 | 0.010674 | 0.010674 | 0.010674 | 0.99458 | -0.037794 | 0.99455 | -0.037978 | 3.9532
30 | 0.074556 | 0.018737 | -0.074388 | -0.018673 | 0.00016748 | 6.4135e-05 | 0.11156 | 0.11156 | 0.11156 | 0.99458 | -0.037794 | 0.99228 | -0.053968 | 41.3198
31 | -0.035987 | -0.0090309 | 0.035987 | 0.009031 | 2.753e-07 | 1.0395e-07 | 0.054111 | 0.054111 | 0.054111 | 0.9897 | -0.072086 | 0.98971 | -0.072031 | 20.0409
32 | 0.034791 | 0.0087311 | -0.034755 | -0.0087175 | 3.616e-05 | 1.3636e-05 | 0.052312 | 0.052312 | 0.052312 | 0.9897 | -0.072086 | 0.98864 | -0.079581 | 19.375
33 | -0.050688 | -0.012715 | 0.050736 | 0.012733 | 4.7545e-05 | 1.8118e-05 | 0.076213 | 0.076213 | 0.076213 | 0.98971 | -0.072031 | 0.99067 | -0.065274 | 28.227
34 | 0.031623 | 0.0079327 | -0.031622 | -0.0079323 | 1.0038e-06 | 3.7699e-07 | 0.047599 | 0.047599 | 0.047599 | 0.98864 | -0.079581 | 0.98861 | -0.07981 | 17.6293
35 | -0.056061 | -0.014068 | 0.0561 | 0.014083 | 3.8508e-05 | 1.4699e-05 | 0.084212 | 0.084212 | 0.084212 | 0.99067 | -0.065274 | 0.99137 | -0.060329 | 31.1896
36 | 0.028013 | 0.0070278 | -0.027979 | -0.0070151 | 3.3869e-05 | 1.2636e-05 | 0.042167 | 0.042167 | 0.042167 | 0.98861 | -0.07981 | 0.98738 | -0.088537 | 15.6174
37 | -0.059069 | -0.014827 | 0.059121 | 0.014847 | 5.2224e-05 | 1.9949e-05 | 0.088668 | 0.088668 | 0.088668 | 0.99137 | -0.060329 | 0.99228 | -0.053968 | 32.8402
38 | 0.024159 | 0.0060576 | -0.024158 | -0.0060573 | 9.3546e-07 | 3.4533e-07 | 0.036409 | 0.036409 | 0.036409 | 0.98738 | -0.088537 | 0.98734 | -0.088816 | 13.485
39 | 0.020368 | 0.0051075 | -0.020356 | -0.0051032 | 1.1695e-05 | 4.2437e-06 | 0.030698 | 0.030698 | 0.030698 | 0.98734 | -0.088816 | 0.98675 | -0.092962 | 11.3695
40 | 0.016757 | 0.0042012 | -0.016749 | -0.0041983 | 8.2661e-06 | 2.9144e-06 | 0.02527 | 0.02527 | 0.02527 | 0.98675 | -0.092962 | 0.98625 | -0.096524 | 9.3594
41 | 0.013154 | 0.0032974 | -0.01315 | -0.0032958 | 4.8613e-06 | 1.6175e-06 | 0.019847 | 0.019847 | 0.019847 | 0.98625 | -0.096524 | 0.98588 | -0.099193 | 7.3508
42 | 0.0091767 | 0.0023001 | -0.0091722 | -0.0022988 | 4.4328e-06 | 1.233e-06 | 0.013851 | 0.013851 | 0.013851 | 0.98588 | -0.099193 | 0.98538 | -0.10268 | 5.13
43 | 0.0091722 | 0.0022988 | -0.0091703 | -0.0022983 | 1.9424e-06 | 5.4043e-07 | 0.013851 | 0.013851 | 0.013851 | 0.98538 | -0.10268 | 0.98517 | -0.10421 | 5.13

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23534 | 0.059019

## res_load
| p_mw | q_mvar
0 | 0.0092695 | 0.0023232
1 | 0.0044328 | 0.001111
2 | 0.00052079 | 0.00013052
3 | 0.0050309 | 0.0012609
4 | 0.0026619 | 0.00066715
5 | 0.0020682 | 0.00051834
6 | 0.00088045 | 0.00022066
7 | 0.0012736 | 0.0003192
8 | 0.0026997 | 0.00067661
9 | 0.00055655 | 0.00013948
10 | 0.0033086 | 0.00082922
11 | 0.0068086 | 0.0017064
12 | 0.014611 | 0.0036619
13 | 0.0089866 | 0.0022523
14 | 0.0035878 | 0.00089918
15 | 0.02015 | 0.0050501
16 | 0.0092085 | 0.0023079
17 | 0.01638 | 0.0041052
18 | 0.0052144 | 0.0013069
19 | 0.013842 | 0.0034691
20 | 0.012457 | 0.0031219
21 | 0.0052099 | 0.0013057
22 | 0.0022562 | 0.00056547
23 | 0.001196 | 0.00029975
24 | 0.014701 | 0.0036844
25 | 0.0031316 | 0.00078485
26 | 0.0053256 | 0.0013347
27 | 0.0036091 | 0.00090451
28 | 0.0029691 | 0.00074412
29 | 0.0038204 | 0.00095748
30 | 0.015267 | 0.0038264
31 | 0.0037899 | 0.00094985
32 | 0.0071339 | 0.0017879
33 | 0.0035991 | 0.00090202
34 | 0.0035946 | 0.00090088
35 | 0.003973 | 0.00099572
36 | 0.0091703 | 0.0022983

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1