## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1140-19_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1140-19_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1140-19_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1140-19_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1140-19_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1140-19_0_4_node_42 | 0.4 | n |  | TRUE
6 | bus_LV_1140-19_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1140-19_0_4_node_28 | 0.4 | n |  | TRUE
8 | bus_LV_1140-19_0_4_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_1140-19_0_4_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_1140-19_0_4_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_1140-19_0_4_node_32 | 0.4 | n |  | TRUE
12 | bus_LV_1140-19_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1140-19_0_4_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1140-19_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1140-19_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1140-19_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1140-19_0_4_node_46 | 0.4 | n |  | TRUE
18 | bus_LV_1140-19_0_4_node_47 | 0.4 | n |  | TRUE
19 | bus_LV_1140-19_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1140-19_0_4_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1140-19_0_4_node_44 | 0.4 | n |  | TRUE
22 | bus_LV_1140-19_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1140-19_0_4_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1140-19_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1140-19_0_4_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1140-19_0_4_node_48 | 0.4 | n |  | TRUE
27 | bus_LV_1140-19_0_4_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_1140-19_0_4_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_1140-19_0_4_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_1140-19_0_4_node_39 | 0.4 | n |  | TRUE
31 | bus_LV_1140-19_0_4_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_1140-19_0_4_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_1140-19_0_4_node_45 | 0.4 | n |  | TRUE
34 | bus_LV_1140-19_0_4_node_40 | 0.4 | n |  | TRUE
35 | bus_LV_1140-19_0_4_node_50 | 0.4 | n |  | TRUE
36 | bus_LV_1140-19_0_4_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_1140-19_0_4_node_51 | 0.4 | n |  | TRUE
38 | bus_LV_1140-19_0_4_node_49 | 0.4 | n |  | TRUE
39 | bus_LV_1140-19_0_4_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_1140-19_0_4_node_41 | 0.4 | n |  | TRUE
41 | bus_LV_1140-19_0_4_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_1140-19_0_4_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_1140-19_0_4_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_1140-19_0_4_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_1140-19_0_4_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_1140-19_0_4_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_1140-19_0_4_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_1140-19_0_4_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_1140-19_0_4_node_43 | 0.4 | n |  | TRUE
50 | bus_MV_475_0_node_61 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1140-19_0_4_load_0 | 0 | 0.0010531 | 0.00026393 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1140-19_0_4_load_1 | 1 | 0.00074273 | 0.00018615 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1140-19_0_4_load_3 | 3 | 0.0013941 | 0.0003494 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1140-19_0_4_load_4 | 4 | 0.0022102 | 0.00055393 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1140-19_0_4_load_42 | 5 | 0.0027553 | 0.00069055 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1140-19_0_4_load_5 | 6 | 0.0010664 | 0.00026725 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1140-19_0_4_load_19 | 8 | 0.0018088 | 0.00045333 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1140-19_0_4_load_11 | 9 | 0.0013395 | 0.0003357 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1140-19_0_4_load_12 | 10 | 0.00134 | 0.00033584 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1140-19_0_4_load_10 | 12 | 0.0005154 | 0.00012917 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1140-19_0_4_load_6 | 13 | 0.00068778 | 0.00017237 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1140-19_0_4_load_7 | 14 | 0.00062228 | 0.00015596 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1140-19_0_4_load_8 | 15 | 0.00082587 | 0.00020698 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1140-19_0_4_load_9 | 16 | 0.0028321 | 0.00070978 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1140-19_0_4_load_46 | 17 | 0.0023919 | 0.00059946 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1140-19_0_4_load_44 | 21 | 0.0014747 | 0.00036959 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1140-19_0_4_load_14 | 23 | 0.0027459 | 0.0006882 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1140-19_0_4_load_15 | 24 | 0.0056648 | 0.0014197 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1140-19_0_4_load_17 | 25 | 0.001861 | 0.0004664 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1140-19_0_4_load_48 | 26 | 0.0026879 | 0.00067364 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1140-19_0_4_load_20 | 27 | 0.0030366 | 0.00076105 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1140-19_0_4_load_22 | 29 | 0.0041064 | 0.0010292 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1140-19_0_4_load_39 | 30 | 0.0026009 | 0.00065184 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1140-19_0_4_load_45 | 33 | 0.0034179 | 0.00085661 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1140-19_0_4_load_40 | 34 | 0.0034687 | 0.00086933 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1140-19_0_4_load_50 | 35 | 0.012427 | 0.0031144 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1140-19_0_4_load_51 | 37 | 0.007162 | 0.001795 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1140-19_0_4_load_49 | 38 | 0.0035775 | 0.00089661 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1140-19_0_4_load_27 | 39 | 0.070254 | 0.017607 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1140-19_0_4_load_24 | 41 | 0.078626 | 0.019706 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1140-19_0_4_load_33 | 43 | 0.0017262 | 0.00043262 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1140-19_0_4_load_34 | 44 | 0.0018297 | 0.00045857 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1140-19_0_4_load_36 | 46 | 0.0015371 | 0.00038522 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1140-19_0_4_load_37 | 47 | 0.0025139 | 0.00063005 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1140-19_0_4_load_38 | 48 | 0.0047785 | 0.0011976 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1140-19_0_4_load_43 | 49 | 0.0029041 | 0.00072784 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1140-19_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.022789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1140-19_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0093777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1140-19_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0081485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1140-19_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.022935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1140-19_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.01476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1140-19_0_4_line_5 | NAYY 4x150 SE | 5 | 8 | 0.0061926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1140-19_0_4_line_6 | NAYY 4x150 SE | 6 | 7 | 0.023655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1140-19_0_4_line_7 | NAYY 4x150 SE | 7 | 11 | 0.087811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1140-19_0_4_line_8 | NAYY 4x150 SE | 7 | 12 | 0.024706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1140-19_0_4_line_9 | NAYY 4x150 SE | 8 | 22 | 0.011401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1140-19_0_4_line_10 | NAYY 4x150 SE | 9 | 10 | 0.0082815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1140-19_0_4_line_11 | NAYY 4x150 SE | 10 | 19 | 0.037025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1140-19_0_4_line_12 | NAYY 4x150 SE | 11 | 39 | 0.065806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1140-19_0_4_line_13 | NAYY 4x150 SE | 12 | 15 | 0.014997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1140-19_0_4_line_14 | NAYY 4x150 SE | 13 | 14 | 0.011534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1140-19_0_4_line_15 | NAYY 4x150 SE | 13 | 15 | 0.0041581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1140-19_0_4_line_16 | NAYY 4x150 SE | 14 | 16 | 0.012804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1140-19_0_4_line_17 | NAYY 4x150 SE | 16 | 17 | 0.00052737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1140-19_0_4_line_18 | NAYY 4x150 SE | 17 | 18 | 0.014525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1140-19_0_4_line_19 | NAYY 4x150 SE | 18 | 26 | 0.0068292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1140-19_0_4_line_20 | NAYY 4x150 SE | 18 | 25 | 0.018353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1140-19_0_4_line_21 | NAYY 4x150 SE | 19 | 20 | 0.025537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1140-19_0_4_line_22 | NAYY 4x150 SE | 20 | 21 | 0.0098311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1140-19_0_4_line_23 | NAYY 4x150 SE | 20 | 22 | 0.021153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1140-19_0_4_line_24 | NAYY 4x150 SE | 22 | 23 | 0.0062415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1140-19_0_4_line_25 | NAYY 4x150 SE | 23 | 24 | 0.021401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1140-19_0_4_line_26 | NAYY 4x150 SE | 24 | 25 | 0.0022945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1140-19_0_4_line_27 | NAYY 4x150 SE | 26 | 47 | 0.022396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1140-19_0_4_line_28 | NAYY 4x150 SE | 27 | 28 | 0.0010917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1140-19_0_4_line_29 | NAYY 4x150 SE | 28 | 29 | 0.018156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1140-19_0_4_line_30 | NAYY 4x150 SE | 29 | 30 | 0.001875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1140-19_0_4_line_31 | NAYY 4x150 SE | 30 | 34 | 0.024169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1140-19_0_4_line_32 | NAYY 4x150 SE | 31 | 32 | 0.12856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1140-19_0_4_line_33 | NAYY 4x150 SE | 31 | 33 | 0.043469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1140-19_0_4_line_34 | NAYY 4x150 SE | 32 | 35 | 0.020252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1140-19_0_4_line_35 | NAYY 4x150 SE | 33 | 40 | 0.0091794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1140-19_0_4_line_36 | NAYY 4x150 SE | 34 | 40 | 0.011978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1140-19_0_4_line_37 | NAYY 4x150 SE | 35 | 38 | 0.0022358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1140-19_0_4_line_38 | NAYY 4x150 SE | 36 | 37 | 0.015089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1140-19_0_4_line_39 | NAYY 4x150 SE | 36 | 38 | 0.01743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1140-19_0_4_line_40 | NAYY 4x150 SE | 39 | 42 | 0.0060559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1140-19_0_4_line_41 | NAYY 4x150 SE | 40 | 48 | 0.019321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1140-19_0_4_line_42 | NAYY 4x150 SE | 41 | 42 | 0.041328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1140-19_0_4_line_43 | NAYY 4x150 SE | 43 | 44 | 0.015614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1140-19_0_4_line_44 | NAYY 4x150 SE | 43 | 45 | 0.013679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1140-19_0_4_line_45 | NAYY 4x150 SE | 44 | 46 | 0.014835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1140-19_0_4_line_46 | NAYY 4x150 SE | 45 | 47 | 0.013798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1140-19_0_4_line_47 | NAYY 4x150 SE | 45 | 48 | 0.010928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1140-19_0_4_line_48 | NAYY 4x150 SE | 46 | 49 | 0.0030556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1140-19_0_4_trafo_32 | 0.25 MVA 20/0.4 kV | 50 | 11 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2640227.5764 | 1233102.4579 | 2640205.092 | 1233098.7461
1 | 2640236.8289 | 1233103.9854 | 2640227.5764 | 1233102.4579
2 | 2640197.0523 | 1233097.4188 | 2640205.092 | 1233098.7461
3 | 2640236.8289 | 1233103.9854 | 2640221.6069 | 1233121.1404
4 | 2640197.0523 | 1233097.4188 | 2640182.4897 | 1233095.0148
5 | 2640176.3798 | 1233094.0061 | 2640182.4897 | 1233095.0148
6 | 2640260.6028 | 1233051.1576 | 2640251.2313 | 1233072.8768
7 | 2640260.6028 | 1233051.1576 | 2640315.8166 | 1233055.6121 | 2640323.8542 | 1233056.0001 | 2640325.4217 | 1233052.5975 | 2640328.1721 | 1233050.0368 | 2640331.694 | 1233048.7042 | 2640335.4561 | 1233048.7965 | 2640339.6437 | 1233050.8817 | 2640342.3739 | 1233054.6581
8 | 2640260.6028 | 1233051.1576 | 2640235.9538 | 1233049.4732
9 | 2640165.1308 | 1233092.1491 | 2640176.3798 | 1233094.0061
10 | 2640194.6143 | 1233142.5186 | 2640186.4127 | 1233141.3708
11 | 2640149.7446 | 1233136.2394 | 2640186.4127 | 1233141.3708
12 | 2640342.3739 | 1233054.6581 | 2640352.6956 | 1233052.0154 | 2640393.8358 | 1233040.7986 | 2640401.147 | 1233038.8915 | 2640405.8915 | 1233037.4681
13 | 2640235.9538 | 1233049.4732 | 2640220.9919 | 1233048.4507
14 | 2640216.8435 | 1233048.1672 | 2640205.3362 | 1233047.3808
15 | 2640216.8435 | 1233048.1672 | 2640220.9919 | 1233048.4507
16 | 2640192.5617 | 1233046.5078 | 2640205.3362 | 1233047.3808
17 | 2640192.5617 | 1233046.5078 | 2640192.0356 | 1233046.4718
18 | 2640177.5442 | 1233045.4815 | 2640192.0356 | 1233046.4718
19 | 2640177.5442 | 1233045.4815 | 2640170.731 | 1233045.0137
20 | 2640177.5442 | 1233045.4815 | 2640172.8263 | 1233063.2183
21 | 2640149.7446 | 1233136.2394 | 2640158.0991 | 1233112.103
22 | 2640158.0991 | 1233112.103 | 2640148.3219 | 1233111.075
23 | 2640165.1308 | 1233092.1491 | 2640158.0991 | 1233112.103
24 | 2640165.1308 | 1233092.1491 | 2640166.7352 | 1233086.1173
25 | 2640172.2365 | 1233065.4357 | 2640166.7352 | 1233086.1173
26 | 2640172.8263 | 1233063.2183 | 2640172.2365 | 1233065.4357
27 | 2640170.731 | 1233045.0137 | 2640148.3881 | 1233043.4796
28 | 2640090.8958 | 1233094.9835 | 2640090.6322 | 1233096.0429
29 | 2640090.8958 | 1233094.9835 | 2640095.2744 | 1233077.3632
30 | 2640095.2744 | 1233077.3632 | 2640095.7266 | 1233075.5435
31 | 2640101.5554 | 1233052.0875 | 2640095.7266 | 1233075.5435
32 | 2640051.9195 | 1233036.8514 | 2640052.1868 | 1233025.2793 | 2640052.6275 | 1232996.9424 | 2640053.4116 | 1232982.8055 | 2640054.1825 | 1232974.0163 | 2640055.4077 | 1232965.219 | 2640058.7467 | 1232946.074 | 2640094.6854 | 1232956.2447
33 | 2640051.9195 | 1233036.8514 | 2640095.2864 | 1233039.8333
34 | 2640094.6854 | 1232956.2447 | 2640114.4051 | 1232960.8564
35 | 2640104.4441 | 1233040.463 | 2640095.2864 | 1233039.8333
36 | 2640104.4441 | 1233040.463 | 2640101.5554 | 1233052.0875
37 | 2640116.5821 | 1232961.3655 | 2640114.4051 | 1232960.8564
38 | 2640133.5537 | 1232965.3346 | 2640140.8006 | 1232978.5695
39 | 2640133.5537 | 1232965.3346 | 2640116.5821 | 1232961.3655
40 | 2640411.6919 | 1233035.7278 | 2640405.8915 | 1233037.4681
41 | 2640104.4441 | 1233040.463 | 2640110.0364 | 1233040.8454 | 2640123.7203 | 1233041.7855
42 | 2640411.6919 | 1233035.7278 | 2640408.7006 | 1233076.9474
43 | 2640126.4423 | 1233070.6621 | 2640130.8027 | 1233055.669
44 | 2640134.6225 | 1233042.5344 | 2640130.8027 | 1233055.669
45 | 2640126.4423 | 1233070.6621 | 2640122.2997 | 1233084.9065
46 | 2640134.6225 | 1233042.5344 | 2640148.3881 | 1233043.4796
47 | 2640134.6225 | 1233042.5344 | 2640123.7203 | 1233041.7855
48 | 2640121.4465 | 1233087.8405 | 2640122.2997 | 1233084.9065

## bus_geodata
| x | y | coords
0 | 2640227.5764 | 1233102.4579
1 | 2640205.092 | 1233098.7461
2 | 2640236.8289 | 1233103.9854
3 | 2640197.0523 | 1233097.4188
4 | 2640221.6069 | 1233121.1404
5 | 2640182.4897 | 1233095.0148
6 | 2640251.2313 | 1233072.8768
7 | 2640260.6028 | 1233051.1576
8 | 2640176.3798 | 1233094.0061
9 | 2640194.6143 | 1233142.5186
10 | 2640186.4127 | 1233141.3708
11 | 2640342.3739 | 1233054.6581
12 | 2640235.9538 | 1233049.4732
13 | 2640216.8435 | 1233048.1672
14 | 2640205.3362 | 1233047.3808
15 | 2640220.9919 | 1233048.4507
16 | 2640192.5617 | 1233046.5078
17 | 2640192.0356 | 1233046.4718
18 | 2640177.5442 | 1233045.4815
19 | 2640149.7446 | 1233136.2394
20 | 2640158.0991 | 1233112.103
21 | 2640148.3219 | 1233111.075
22 | 2640165.1308 | 1233092.1491
23 | 2640166.7352 | 1233086.1173
24 | 2640172.2364 | 1233065.4357
25 | 2640172.8263 | 1233063.2183
26 | 2640170.731 | 1233045.0137
27 | 2640090.6322 | 1233096.0429
28 | 2640090.8958 | 1233094.9835
29 | 2640095.2744 | 1233077.3632
30 | 2640095.7266 | 1233075.5435
31 | 2640051.9195 | 1233036.8514
32 | 2640094.6854 | 1232956.2447
33 | 2640095.2864 | 1233039.8333
34 | 2640101.5554 | 1233052.0875
35 | 2640114.4051 | 1232960.8564
36 | 2640133.5537 | 1232965.3346
37 | 2640140.8006 | 1232978.5695
38 | 2640116.5821 | 1232961.3655
39 | 2640405.8915 | 1233037.4681
40 | 2640104.4441 | 1233040.463
41 | 2640408.7006 | 1233076.9474
42 | 2640411.6919 | 1233035.7278
43 | 2640130.8027 | 1233055.669
44 | 2640126.4423 | 1233070.6621
45 | 2640134.6225 | 1233042.5344
46 | 2640122.2997 | 1233084.9065
47 | 2640148.3881 | 1233043.4796
48 | 2640123.7203 | 1233041.7855
49 | 2640121.4465 | 1233087.8405
50 | 2640411.6919 | 1233035.7278

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98164 | -0.12828 | 0.0010531 | 0.00026393
1 | 0.98175 | -0.12751 | 0.00074273 | 0.00018615
2 | 0.98161 | -0.1285 | 0 | 0
3 | 0.98179 | -0.12718 | 0.0013941 | 0.0003494
4 | 0.98154 | -0.12903 | 0.0022102 | 0.00055393
5 | 0.98191 | -0.12635 | 0.0027553 | 0.00069055
6 | 0.99414 | -0.040446 | 0.0010664 | 0.00026725
7 | 0.99417 | -0.040191 | 0 | 0
8 | 0.98198 | -0.12583 | 0.0018088 | 0.00045333
9 | 0.98176 | -0.12741 | 0.0013395 | 0.0003357
10 | 0.98178 | -0.1273 | 0.00134 | 0.00033584
11 | 1 | 0 | -0.24415 | -0.061426
12 | 0.99093 | -0.062745 | 0.0005154 | 0.00012917
13 | 0.98844 | -0.080196 | 0.00068778 | 0.00017237
14 | 0.98696 | -0.090589 | 0.00062228 | 0.00015596
15 | 0.98898 | -0.076428 | 0.00082587 | 0.00020698
16 | 0.98533 | -0.10208 | 0.0028321 | 0.00070978
17 | 0.98526 | -0.10254 | 0.0023919 | 0.00059946
18 | 0.98352 | -0.11484 | 0 | 0
19 | 0.98192 | -0.12627 | 0 | 0
20 | 0.98202 | -0.12556 | 0 | 0
21 | 0.982 | -0.12571 | 0.0014747 | 0.00036959
22 | 0.98215 | -0.12465 | 0 | 0
23 | 0.98228 | -0.12374 | 0.0027459 | 0.0006882
24 | 0.9828 | -0.12 | 0.0056648 | 0.0014197
25 | 0.98287 | -0.11947 | 0.001861 | 0.0004664
26 | 0.98295 | -0.11892 | 0.0026879 | 0.00067364
27 | 0.97757 | -0.15717 | 0.0030366 | 0.00076105
28 | 0.97757 | -0.15714 | 0 | 0
29 | 0.97765 | -0.15656 | 0.0041064 | 0.0010292
30 | 0.97767 | -0.15642 | 0.0026009 | 0.00065184
31 | 0.97641 | -0.16539 | 0 | 0
32 | 0.97204 | -0.19673 | 0 | 0
33 | 0.97789 | -0.15486 | 0.0034179 | 0.00085661
34 | 0.97802 | -0.15396 | 0.0034687 | 0.00086933
35 | 0.97135 | -0.20168 | 0.012427 | 0.0031144
36 | 0.97113 | -0.20326 | 0 | 0
37 | 0.97098 | -0.2044 | 0.007162 | 0.001795
38 | 0.97132 | -0.20194 | 0.0035775 | 0.00089661
39 | 0.99295 | -0.04924 | 0.070254 | 0.017607
40 | 0.97825 | -0.15231 | 0 | 0
41 | 0.98757 | -0.08716 | 0.078626 | 0.019706
42 | 0.99226 | -0.054064 | 0 | 0
43 | 0.97993 | -0.14036 | 0.0017262 | 0.00043262
44 | 0.97978 | -0.14138 | 0.0018297 | 0.00045857
45 | 0.98009 | -0.13923 | 0 | 0
46 | 0.97969 | -0.14207 | 0.0015371 | 0.00038522
47 | 0.98115 | -0.13169 | 0.0025139 | 0.00063005
48 | 0.97937 | -0.14429 | 0.0047785 | 0.0011976
49 | 0.97968 | -0.14216 | 0.0029041 | 0.00072784
50 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0032635 | -0.00081754 | 0.0032639 | 0.00081738 | 3.4798e-07 | -1.5429e-07 | 0.0049469 | 0.0049468 | 0.0049469 | 0.98164 | -0.12828 | 0.98175 | -0.12751 | 1.8322
1 | 0.0022104 | 0.00055361 | -0.0022104 | -0.0005537 | 6.5692e-08 | -9.3283e-08 | 0.0033505 | 0.0033506 | 0.0033506 | 0.98164 | -0.12828 | 0.98161 | -0.1285 | 1.241
2 | -0.0040066 | -0.0010035 | 0.0040068 | 0.0010035 | 1.875e-07 | -3.0926e-08 | 0.0060725 | 0.0060725 | 0.0060725 | 0.98175 | -0.12751 | 0.98179 | -0.12718 | 2.2491
3 | 0.0022104 | 0.0005537 | -0.0022102 | -0.00055393 | 1.6067e-07 | -2.281e-07 | 0.0033506 | 0.0033507 | 0.0033507 | 0.98161 | -0.1285 | 0.98154 | -0.12903 | 1.241
4 | -0.0054009 | -0.0013529 | 0.0054015 | 0.0013529 | 6.1708e-07 | 5.0665e-08 | 0.0081854 | 0.0081853 | 0.0081854 | 0.98179 | -0.12718 | 0.98191 | -0.12635 | 3.0316
5 | -0.0081568 | -0.0020435 | 0.0081574 | 0.0020436 | 5.9041e-07 | 1.4874e-07 | 0.012361 | 0.012361 | 0.012361 | 0.98191 | -0.12635 | 0.98198 | -0.12583 | 4.5781
6 | -0.0010664 | -0.00026725 | 0.0010664 | 0.00026696 | 3.7601e-08 | -2.9225e-07 | 0.0015961 | 0.001596 | 0.0015961 | 0.99414 | -0.040446 | 0.99417 | -0.040191 | 0.59115
7 | -0.092502 | -0.02336 | 0.093027 | 0.02356 | 0.00052564 | 0.00019988 | 0.13851 | 0.13851 | 0.13851 | 0.99417 | -0.040191 | 1 | 0 | 25.6506
8 | 0.091435 | 0.023093 | -0.091146 | -0.022983 | 0.00028901 | 0.00011084 | 0.13692 | 0.13692 | 0.13692 | 0.99417 | -0.040191 | 0.99093 | -0.062745 | 50.7102
9 | -0.0099662 | -0.002497 | 0.0099679 | 0.0024975 | 1.6225e-06 | 4.7979e-07 | 0.015102 | 0.015102 | 0.015102 | 0.98198 | -0.12583 | 0.98215 | -0.12465 | 5.5932
10 | -0.0013395 | -0.0003357 | 0.0013395 | 0.00033561 | 2.1299e-08 | -9.653e-08 | 0.0020302 | 0.0020301 | 0.0020302 | 0.98176 | -0.12741 | 0.98178 | -0.1273 | 0.75192
11 | -0.0026795 | -0.00067144 | 0.0026799 | 0.00067112 | 3.8103e-07 | -3.2172e-07 | 0.0040611 | 0.0040609 | 0.0040611 | 0.98178 | -0.1273 | 0.98192 | -0.12627 | 1.5041
12 | 0.15032 | 0.037866 | -0.1493 | -0.037472 | 0.0010279 | 0.00039363 | 0.22375 | 0.22375 | 0.22375 | 1 | 0 | 0.99295 | -0.04924 | 41.4355
13 | 0.090631 | 0.022853 | -0.090457 | -0.022787 | 0.00017345 | 6.652e-05 | 0.13614 | 0.13614 | 0.13614 | 0.99093 | -0.062745 | 0.98898 | -0.076428 | 50.4236
14 | 0.088896 | 0.022389 | -0.088768 | -0.02234 | 0.00012898 | 4.9458e-05 | 0.13387 | 0.13387 | 0.13387 | 0.98844 | -0.080196 | 0.98696 | -0.090589 | 49.5799
15 | -0.089584 | -0.022562 | 0.089631 | 0.02258 | 4.7218e-05 | 1.8107e-05 | 0.1349 | 0.1349 | 0.1349 | 0.98844 | -0.080196 | 0.98898 | -0.076428 | 49.9634
16 | 0.088145 | 0.022184 | -0.088004 | -0.02213 | 0.00014118 | 5.4136e-05 | 0.13293 | 0.13293 | 0.13293 | 0.98696 | -0.090589 | 0.98533 | -0.10208 | 49.2324
17 | 0.085172 | 0.02142 | -0.085167 | -0.021418 | 5.4466e-06 | 2.0881e-06 | 0.12865 | 0.12865 | 0.12865 | 0.98533 | -0.10208 | 0.98526 | -0.10254 | 47.6484
18 | 0.082775 | 0.020819 | -0.082633 | -0.020764 | 0.00014171 | 5.4318e-05 | 0.12504 | 0.12504 | 0.12504 | 0.98526 | -0.10254 | 0.98352 | -0.11484 | 46.3105
19 | 0.05821 | 0.014642 | -0.058177 | -0.014629 | 3.3066e-05 | 1.2631e-05 | 0.088088 | 0.088088 | 0.088088 | 0.98352 | -0.11484 | 0.98295 | -0.11892 | 32.6251
20 | 0.024423 | 0.0061222 | -0.024407 | -0.0061164 | 1.5637e-05 | 5.7814e-06 | 0.036951 | 0.036951 | 0.036951 | 0.98352 | -0.11484 | 0.98287 | -0.11947 | 13.6855
21 | -0.0026799 | -0.00067112 | 0.0026801 | 0.0006709 | 2.6278e-07 | -2.2199e-07 | 0.0040609 | 0.0040608 | 0.0040609 | 0.98192 | -0.12627 | 0.98202 | -0.12556 | 1.5041
22 | 0.0014747 | 0.00036948 | -0.0014747 | -0.00036959 | 3.0632e-08 | -1.126e-07 | 0.0022345 | 0.0022346 | 0.0022346 | 0.98202 | -0.12556 | 0.982 | -0.12571 | 0.82762
23 | -0.0041549 | -0.0010404 | 0.0041554 | 0.0010403 | 5.2311e-07 | -6.6462e-08 | 0.0062954 | 0.0062953 | 0.0062954 | 0.98202 | -0.12556 | 0.98215 | -0.12465 | 2.3316
24 | -0.014123 | -0.0035378 | 0.014125 | 0.0035384 | 1.7831e-06 | 6.0681e-07 | 0.021397 | 0.021397 | 0.021397 | 0.98215 | -0.12465 | 0.98228 | -0.12374 | 7.9248
25 | -0.016871 | -0.0042266 | 0.01688 | 0.0042297 | 8.7221e-06 | 3.0836e-06 | 0.025557 | 0.025557 | 0.025557 | 0.98228 | -0.12374 | 0.9828 | -0.12 | 9.4654
26 | -0.022545 | -0.0056494 | 0.022546 | 0.00565 | 1.6682e-06 | 6.1252e-07 | 0.034133 | 0.034133 | 0.034133 | 0.9828 | -0.12 | 0.98287 | -0.11947 | 12.642
27 | 0.055489 | 0.013956 | -0.055391 | -0.013918 | 9.865e-05 | 3.7659e-05 | 0.084019 | 0.084019 | 0.084019 | 0.98295 | -0.11892 | 0.98115 | -0.13169 | 31.1181
28 | -0.0030366 | -0.00076105 | 0.0030366 | 0.00076104 | 1.4554e-08 | -8.0892e-09 | 0.0046222 | 0.0046222 | 0.0046222 | 0.97757 | -0.15717 | 0.97757 | -0.15714 | 1.7119
29 | -0.0030366 | -0.00076104 | 0.0030369 | 0.00076091 | 2.4205e-07 | -1.3456e-07 | 0.0046222 | 0.0046221 | 0.0046222 | 0.97757 | -0.15714 | 0.97765 | -0.15656 | 1.7119
30 | -0.0071433 | -0.0017901 | 0.0071434 | 0.0017901 | 1.383e-07 | 2.968e-08 | 0.010872 | 0.010872 | 0.010872 | 0.97765 | -0.15656 | 0.97767 | -0.15642 | 4.0267
31 | -0.0097443 | -0.0024419 | 0.0097476 | 0.0024429 | 3.3172e-06 | 9.7265e-07 | 0.014831 | 0.014831 | 0.014831 | 0.97767 | -0.15642 | 0.97802 | -0.15396 | 5.4929
32 | 0.023286 | 0.0058498 | -0.023185 | -0.0058125 | 0.00010106 | 3.7268e-05 | 0.035492 | 0.035493 | 0.035493 | 0.97641 | -0.16539 | 0.97204 | -0.19673 | 13.1454
33 | -0.023286 | -0.0058498 | 0.02332 | 0.0058624 | 3.4168e-05 | 1.2597e-05 | 0.035492 | 0.035492 | 0.035492 | 0.97641 | -0.16539 | 0.97789 | -0.15486 | 13.1452
34 | 0.023185 | 0.0058125 | -0.023169 | -0.0058067 | 1.5919e-05 | 5.8719e-06 | 0.035493 | 0.035493 | 0.035493 | 0.97204 | -0.19673 | 0.97135 | -0.20168 | 13.1454
35 | -0.026738 | -0.006719 | 0.026748 | 0.0067225 | 9.4848e-06 | 3.5328e-06 | 0.040693 | 0.040693 | 0.040693 | 0.97789 | -0.15486 | 0.97825 | -0.15231 | 15.0714
36 | -0.013216 | -0.0033122 | 0.013219 | 0.0033133 | 3.0221e-06 | 1.012e-06 | 0.020108 | 0.020108 | 0.020108 | 0.97802 | -0.15396 | 0.97825 | -0.15231 | 7.4474
37 | 0.010742 | 0.0026922 | -0.010742 | -0.0026921 | 3.7781e-07 | 1.1764e-07 | 0.016456 | 0.016456 | 0.016456 | 0.97135 | -0.20168 | 0.97132 | -0.20194 | 6.0949
38 | 0.0071632 | 0.0017952 | -0.007162 | -0.001795 | 1.1343e-06 | 2.4959e-07 | 0.010976 | 0.010976 | 0.010976 | 0.97113 | -0.20326 | 0.97098 | -0.2044 | 4.0651
39 | -0.0071632 | -0.0017952 | 0.0071645 | 0.0017955 | 1.3102e-06 | 2.8822e-07 | 0.010976 | 0.010976 | 0.010976 | 0.97113 | -0.20326 | 0.97132 | -0.20194 | 4.0651
40 | 0.079041 | 0.019865 | -0.078988 | -0.019844 | 5.3037e-05 | 2.032e-05 | 0.11847 | 0.11847 | 0.11847 | 0.99295 | -0.04924 | 0.99226 | -0.054064 | 43.8776
41 | -0.039967 | -0.010036 | 0.040011 | 0.010053 | 4.457e-05 | 1.6899e-05 | 0.060801 | 0.060801 | 0.060801 | 0.97825 | -0.15231 | 0.97937 | -0.14429 | 22.5188
42 | -0.078626 | -0.019706 | 0.078988 | 0.019844 | 0.00036194 | 0.00013868 | 0.11847 | 0.11847 | 0.11847 | 0.98757 | -0.08716 | 0.99226 | -0.054064 | 43.8777
43 | 0.0062722 | 0.0015717 | -0.0062713 | -0.0015716 | 8.8384e-07 | 1.4326e-07 | 0.0095243 | 0.0095243 | 0.0095243 | 0.97993 | -0.14036 | 0.97978 | -0.14138 | 3.5275
44 | -0.0079984 | -0.0020043 | 0.0079996 | 0.0020047 | 1.2591e-06 | 3.1191e-07 | 0.012145 | 0.012145 | 0.012145 | 0.97993 | -0.14036 | 0.98009 | -0.13923 | 4.4983
45 | 0.0044416 | 0.001113 | -0.0044412 | -0.001113 | 4.212e-07 | -2.4809e-08 | 0.0067455 | 0.0067456 | 0.0067456 | 0.97978 | -0.14138 | 0.97969 | -0.14207 | 2.4984
46 | -0.052821 | -0.013267 | 0.052877 | 0.013288 | 5.5388e-05 | 2.1129e-05 | 0.080206 | 0.080206 | 0.080206 | 0.98009 | -0.13923 | 0.98115 | -0.13169 | 29.706
47 | 0.044822 | 0.011262 | -0.04479 | -0.01125 | 3.1588e-05 | 1.2011e-05 | 0.068061 | 0.068061 | 0.068061 | 0.98009 | -0.13923 | 0.97937 | -0.14429 | 25.2077
48 | 0.0029041 | 0.00072781 | -0.0029041 | -0.00072784 | 3.7099e-08 | -2.4206e-08 | 0.004411 | 0.004411 | 0.004411 | 0.97969 | -0.14207 | 0.97968 | -0.14216 | 1.6337

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24415 | 0.061426

## res_load
| p_mw | q_mvar
0 | 0.0010531 | 0.00026393
1 | 0.00074273 | 0.00018615
2 | 0.0013941 | 0.0003494
3 | 0.0022102 | 0.00055393
4 | 0.0027553 | 0.00069055
5 | 0.0010664 | 0.00026725
6 | 0.0018088 | 0.00045333
7 | 0.0013395 | 0.0003357
8 | 0.00134 | 0.00033584
9 | 0.0005154 | 0.00012917
10 | 0.00068778 | 0.00017237
11 | 0.00062228 | 0.00015596
12 | 0.00082587 | 0.00020698
13 | 0.0028321 | 0.00070978
14 | 0.0023919 | 0.00059946
15 | 0.0014747 | 0.00036959
16 | 0.0027459 | 0.0006882
17 | 0.0056648 | 0.0014197
18 | 0.001861 | 0.0004664
19 | 0.0026879 | 0.00067364
20 | 0.0030366 | 0.00076105
21 | 0.0041064 | 0.0010292
22 | 0.0026009 | 0.00065184
23 | 0.0034179 | 0.00085661
24 | 0.0034687 | 0.00086933
25 | 0.012427 | 0.0031144
26 | 0.007162 | 0.001795
27 | 0.0035775 | 0.00089661
28 | 0.070254 | 0.017607
29 | 0.078626 | 0.019706
30 | 0.0017262 | 0.00043262
31 | 0.0018297 | 0.00045857
32 | 0.0015371 | 0.00038522
33 | 0.0025139 | 0.00063005
34 | 0.0047785 | 0.0011976
35 | 0.0029041 | 0.00072784

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1