## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1140-25_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1140-25_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1140-25_0_4_node_129 | 0.4 | n |  | TRUE
3 | bus_LV_1140-25_0_4_node_121 | 0.4 | n |  | TRUE
4 | bus_LV_1140-25_0_4_node_130 | 0.4 | n |  | TRUE
5 | bus_LV_1140-25_0_4_node_80 | 0.4 | n |  | TRUE
6 | bus_LV_1140-25_0_4_node_128 | 0.4 | n |  | TRUE
7 | bus_LV_1140-25_0_4_node_79 | 0.4 | n |  | TRUE
8 | bus_LV_1140-25_0_4_node_122 | 0.4 | n |  | TRUE
9 | bus_LV_1140-25_0_4_node_3 | 0.4 | n |  | TRUE
10 | bus_LV_1140-25_0_4_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_1140-25_0_4_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1140-25_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1140-25_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1140-25_0_4_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_1140-25_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1140-25_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1140-25_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1140-25_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1140-25_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1140-25_0_4_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_1140-25_0_4_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_1140-25_0_4_node_97 | 0.4 | n |  | TRUE
23 | bus_LV_1140-25_0_4_node_112 | 0.4 | n |  | TRUE
24 | bus_LV_1140-25_0_4_node_108 | 0.4 | n |  | TRUE
25 | bus_LV_1140-25_0_4_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_1140-25_0_4_node_103 | 0.4 | n |  | TRUE
27 | bus_LV_1140-25_0_4_node_113 | 0.4 | n |  | TRUE
28 | bus_LV_1140-25_0_4_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_1140-25_0_4_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_1140-25_0_4_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_1140-25_0_4_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_1140-25_0_4_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_1140-25_0_4_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_1140-25_0_4_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_1140-25_0_4_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_1140-25_0_4_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_1140-25_0_4_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_1140-25_0_4_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_1140-25_0_4_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_1140-25_0_4_node_24 | 0.4 | n |  | TRUE
41 | bus_LV_1140-25_0_4_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_1140-25_0_4_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_1140-25_0_4_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_1140-25_0_4_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_1140-25_0_4_node_49 | 0.4 | n |  | TRUE
46 | bus_LV_1140-25_0_4_node_59 | 0.4 | n |  | TRUE
47 | bus_LV_1140-25_0_4_node_27 | 0.4 | n |  | TRUE
48 | bus_LV_1140-25_0_4_node_106 | 0.4 | n |  | TRUE
49 | bus_LV_1140-25_0_4_node_31 | 0.4 | n |  | TRUE
50 | bus_LV_1140-25_0_4_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_1140-25_0_4_node_42 | 0.4 | n |  | TRUE
52 | bus_LV_1140-25_0_4_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_1140-25_0_4_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_1140-25_0_4_node_47 | 0.4 | n |  | TRUE
55 | bus_LV_1140-25_0_4_node_60 | 0.4 | n |  | TRUE
56 | bus_LV_1140-25_0_4_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_1140-25_0_4_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_1140-25_0_4_node_38 | 0.4 | n |  | TRUE
59 | bus_LV_1140-25_0_4_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_1140-25_0_4_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_1140-25_0_4_node_39 | 0.4 | n |  | TRUE
62 | bus_LV_1140-25_0_4_node_40 | 0.4 | n |  | TRUE
63 | bus_LV_1140-25_0_4_node_48 | 0.4 | n |  | TRUE
64 | bus_LV_1140-25_0_4_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_1140-25_0_4_node_51 | 0.4 | n |  | TRUE
66 | bus_LV_1140-25_0_4_node_52 | 0.4 | n |  | TRUE
67 | bus_LV_1140-25_0_4_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_1140-25_0_4_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_1140-25_0_4_node_115 | 0.4 | n |  | TRUE
70 | bus_LV_1140-25_0_4_node_114 | 0.4 | n |  | TRUE
71 | bus_LV_1140-25_0_4_node_55 | 0.4 | n |  | TRUE
72 | bus_LV_1140-25_0_4_node_111 | 0.4 | n |  | TRUE
73 | bus_LV_1140-25_0_4_node_56 | 0.4 | n |  | TRUE
74 | bus_LV_1140-25_0_4_node_57 | 0.4 | n |  | TRUE
75 | bus_LV_1140-25_0_4_node_58 | 0.4 | n |  | TRUE
76 | bus_LV_1140-25_0_4_node_64 | 0.4 | n |  | TRUE
77 | bus_LV_1140-25_0_4_node_98 | 0.4 | n |  | TRUE
78 | bus_LV_1140-25_0_4_node_62 | 0.4 | n |  | TRUE
79 | bus_LV_1140-25_0_4_node_61 | 0.4 | n |  | TRUE
80 | bus_LV_1140-25_0_4_node_63 | 0.4 | n |  | TRUE
81 | bus_LV_1140-25_0_4_node_65 | 0.4 | n |  | TRUE
82 | bus_LV_1140-25_0_4_node_66 | 0.4 | n |  | TRUE
83 | bus_LV_1140-25_0_4_node_84 | 0.4 | n |  | TRUE
84 | bus_LV_1140-25_0_4_node_74 | 0.4 | n |  | TRUE
85 | bus_LV_1140-25_0_4_node_99 | 0.4 | n |  | TRUE
86 | bus_LV_1140-25_0_4_node_83 | 0.4 | n |  | TRUE
87 | bus_LV_1140-25_0_4_node_95 | 0.4 | n |  | TRUE
88 | bus_LV_1140-25_0_4_node_72 | 0.4 | n |  | TRUE
89 | bus_LV_1140-25_0_4_node_67 | 0.4 | n |  | TRUE
90 | bus_LV_1140-25_0_4_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_1140-25_0_4_node_69 | 0.4 | n |  | TRUE
92 | bus_LV_1140-25_0_4_node_70 | 0.4 | n |  | TRUE
93 | bus_LV_1140-25_0_4_node_77 | 0.4 | n |  | TRUE
94 | bus_LV_1140-25_0_4_node_78 | 0.4 | n |  | TRUE
95 | bus_LV_1140-25_0_4_node_71 | 0.4 | n |  | TRUE
96 | bus_LV_1140-25_0_4_node_73 | 0.4 | n |  | TRUE
97 | bus_LV_1140-25_0_4_node_75 | 0.4 | n |  | TRUE
98 | bus_LV_1140-25_0_4_node_76 | 0.4 | n |  | TRUE
99 | bus_LV_1140-25_0_4_node_85 | 0.4 | n |  | TRUE
100 | bus_LV_1140-25_0_4_node_96 | 0.4 | n |  | TRUE
101 | bus_LV_1140-25_0_4_node_86 | 0.4 | n |  | TRUE
102 | bus_LV_1140-25_0_4_node_82 | 0.4 | n |  | TRUE
103 | bus_LV_1140-25_0_4_node_81 | 0.4 | n |  | TRUE
104 | bus_LV_1140-25_0_4_node_116 | 0.4 | n |  | TRUE
105 | bus_LV_1140-25_0_4_node_117 | 0.4 | n |  | TRUE
106 | bus_LV_1140-25_0_4_node_118 | 0.4 | n |  | TRUE
107 | bus_LV_1140-25_0_4_node_119 | 0.4 | n |  | TRUE
108 | bus_LV_1140-25_0_4_node_120 | 0.4 | n |  | TRUE
109 | bus_LV_1140-25_0_4_node_127 | 0.4 | n |  | TRUE
110 | bus_LV_1140-25_0_4_node_126 | 0.4 | n |  | TRUE
111 | bus_LV_1140-25_0_4_node_124 | 0.4 | n |  | TRUE
112 | bus_LV_1140-25_0_4_node_125 | 0.4 | n |  | TRUE
113 | bus_LV_1140-25_0_4_node_87 | 0.4 | n |  | TRUE
114 | bus_LV_1140-25_0_4_node_88 | 0.4 | n |  | TRUE
115 | bus_LV_1140-25_0_4_node_90 | 0.4 | n |  | TRUE
116 | bus_LV_1140-25_0_4_node_91 | 0.4 | n |  | TRUE
117 | bus_LV_1140-25_0_4_node_92 | 0.4 | n |  | TRUE
118 | bus_LV_1140-25_0_4_node_93 | 0.4 | n |  | TRUE
119 | bus_LV_1140-25_0_4_node_94 | 0.4 | n |  | TRUE
120 | bus_LV_1140-25_0_4_node_101 | 0.4 | n |  | TRUE
121 | bus_LV_1140-25_0_4_node_100 | 0.4 | n |  | TRUE
122 | bus_LV_1140-25_0_4_node_104 | 0.4 | n |  | TRUE
123 | bus_LV_1140-25_0_4_node_102 | 0.4 | n |  | TRUE
124 | bus_LV_1140-25_0_4_node_105 | 0.4 | n |  | TRUE
125 | bus_LV_1140-25_0_4_node_107 | 0.4 | n |  | TRUE
126 | bus_LV_1140-25_0_4_node_109 | 0.4 | n |  | TRUE
127 | bus_LV_1140-25_0_4_node_110 | 0.4 | n |  | TRUE
128 | bus_MV_475_0_node_81 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1140-25_0_4_load_0 | 0 | 0.0008584 | 0.00021514 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1140-25_0_4_load_129 | 2 | 0.0023797 | 0.00059642 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1140-25_0_4_load_121 | 3 | 0.0090622 | 0.0022712 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1140-25_0_4_load_79 | 7 | 0.0014291 | 0.00035815 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1140-25_0_4_load_122 | 8 | 0.0010299 | 0.00025812 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1140-25_0_4_load_3 | 9 | 0.0015752 | 0.00039478 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1140-25_0_4_load_4 | 10 | 0.0014799 | 0.00037089 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1140-25_0_4_load_5 | 11 | 0.0024457 | 0.00061295 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1140-25_0_4_load_8 | 15 | 0.0026146 | 0.00065529 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1140-25_0_4_load_7 | 16 | 0.0025955 | 0.0006505 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1140-25_0_4_load_9 | 17 | 0.001841 | 0.00046141 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1140-25_0_4_load_11 | 18 | 0.0022845 | 0.00057256 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1140-25_0_4_load_28 | 20 | 0.0031955 | 0.00080087 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1140-25_0_4_load_25 | 21 | 0.0025694 | 0.00064394 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1140-25_0_4_load_112 | 23 | 0.0067012 | 0.0016795 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1140-25_0_4_load_108 | 24 | 0.0026712 | 0.00066945 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1140-25_0_4_load_26 | 25 | 0.0055539 | 0.0013919 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1140-25_0_4_load_103 | 26 | 0.002172 | 0.00054435 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1140-25_0_4_load_113 | 27 | 0.0024573 | 0.00061586 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1140-25_0_4_load_14 | 28 | 0.002482 | 0.00062206 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1140-25_0_4_load_15 | 29 | 0.0036808 | 0.00092249 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1140-25_0_4_load_17 | 31 | 0.011493 | 0.0028804 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1140-25_0_4_load_18 | 32 | 0.0061438 | 0.0015398 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1140-25_0_4_load_19 | 33 | 0.0046239 | 0.0011589 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1140-25_0_4_load_30 | 34 | 0.0025408 | 0.00063678 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1140-25_0_4_load_29 | 35 | 0.0015117 | 0.00037887 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1140-25_0_4_load_20 | 36 | 0.0030347 | 0.00076056 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1140-25_0_4_load_21 | 37 | 0.0018537 | 0.00046457 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1140-25_0_4_load_22 | 38 | 0.003119 | 0.0007817 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1140-25_0_4_load_23 | 39 | 0.0025375 | 0.00063597 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1140-25_0_4_load_34 | 42 | 0.0017048 | 0.00042728 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1140-25_0_4_load_49 | 45 | 0.003173 | 0.00079523 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1140-25_0_4_load_27 | 47 | 0.0024923 | 0.00062462 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1140-25_0_4_load_106 | 48 | 0.0043122 | 0.0010807 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1140-25_0_4_load_42 | 51 | 0.0026481 | 0.00066368 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1140-25_0_4_load_46 | 52 | 0.0019869 | 0.00049797 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1140-25_0_4_load_41 | 53 | 0.0021265 | 0.00053295 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1140-25_0_4_load_47 | 54 | 0.0026102 | 0.00065419 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1140-25_0_4_load_60 | 55 | 0.0038268 | 0.00095908 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1140-25_0_4_load_36 | 56 | 0.0020532 | 0.00051457 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1140-25_0_4_load_37 | 57 | 0.0024596 | 0.00061642 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1140-25_0_4_load_38 | 58 | 0.0016126 | 0.00040416 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1140-25_0_4_load_44 | 59 | 0.0016124 | 0.00040411 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1140-25_0_4_load_45 | 60 | 0.0023835 | 0.00059736 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1140-25_0_4_load_39 | 61 | 0.003001 | 0.00075213 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1140-25_0_4_load_40 | 62 | 0.0031929 | 0.00080021 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1140-25_0_4_load_48 | 63 | 0.0020626 | 0.00051694 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1140-25_0_4_load_50 | 64 | 0.0022693 | 0.00056873 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1140-25_0_4_load_51 | 65 | 0.0025302 | 0.00063412 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1140-25_0_4_load_54 | 68 | 0.0016359 | 0.00040999 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1140-25_0_4_load_115 | 69 | 0.0037464 | 0.00093893 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1140-25_0_4_load_114 | 70 | 0.00096238 | 0.0002412 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1140-25_0_4_load_55 | 71 | 0.00065343 | 0.00016376 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1140-25_0_4_load_56 | 73 | 0.0015425 | 0.00038658 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1140-25_0_4_load_57 | 74 | 0.0016345 | 0.00040966 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1140-25_0_4_load_58 | 75 | 0.0056625 | 0.0014192 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1140-25_0_4_load_98 | 77 | 0.0015907 | 0.00039867 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1140-25_0_4_load_62 | 78 | 0.0016334 | 0.00040936 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1140-25_0_4_load_61 | 79 | 0.0025755 | 0.00064547 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1140-25_0_4_load_65 | 81 | 0.0023315 | 0.00058432 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1140-25_0_4_load_66 | 82 | 0.0018024 | 0.00045172 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1140-25_0_4_load_84 | 83 | 0.0023562 | 0.00059051 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1140-25_0_4_load_99 | 85 | 0.0021297 | 0.00053374 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1140-25_0_4_load_83 | 86 | 0.0024987 | 0.00062623 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1140-25_0_4_load_95 | 87 | 0.0023626 | 0.00059212 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1140-25_0_4_load_72 | 88 | 0.0013 | 0.0003258 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1140-25_0_4_load_67 | 89 | 0.0021129 | 0.00052955 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1140-25_0_4_load_68 | 90 | 0.0013835 | 0.00034674 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1140-25_0_4_load_69 | 91 | 0.001676 | 0.00042005 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1140-25_0_4_load_70 | 92 | 0.00090932 | 0.0002279 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1140-25_0_4_load_77 | 93 | 0.00051269 | 0.00012849 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1140-25_0_4_load_78 | 94 | 0.0011161 | 0.00027971 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1140-25_0_4_load_71 | 95 | 0.0019364 | 0.0004853 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1140-25_0_4_load_76 | 98 | 0.0014875 | 0.00037281 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1140-25_0_4_load_85 | 99 | 0.0037306 | 0.00093498 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1140-25_0_4_load_96 | 100 | 0.0017576 | 0.0004405 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1140-25_0_4_load_86 | 101 | 0.0022857 | 0.00057286 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1140-25_0_4_load_82 | 102 | 0.00079232 | 0.00019857 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1140-25_0_4_load_81 | 103 | 0.0017433 | 0.00043691 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1140-25_0_4_load_116 | 104 | 0.00010785 | 2.703e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1140-25_0_4_load_117 | 105 | 0.00032282 | 8.0907e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1140-25_0_4_load_119 | 107 | 0.00081744 | 0.00020487 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1140-25_0_4_load_120 | 108 | 0.00023724 | 5.9459e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1140-25_0_4_load_127 | 109 | 0.00038334 | 9.6074e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1140-25_0_4_load_124 | 111 | 0.00018852 | 4.7248e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1140-25_0_4_load_125 | 112 | 0.0014878 | 0.00037288 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1140-25_0_4_load_87 | 113 | 0.0012677 | 0.00031772 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1140-25_0_4_load_88 | 114 | 0.0021663 | 0.00054293 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1140-25_0_4_load_90 | 115 | 0.0022446 | 0.00056254 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1140-25_0_4_load_91 | 116 | 0.001827 | 0.00045789 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1140-25_0_4_load_92 | 117 | 0.0015504 | 0.00038857 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1140-25_0_4_load_93 | 118 | 0.00093562 | 0.00023449 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1140-25_0_4_load_94 | 119 | 0.001556 | 0.00038997 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1140-25_0_4_load_101 | 120 | 0.0027201 | 0.00068172 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1140-25_0_4_load_100 | 121 | 0.0024519 | 0.00061451 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1140-25_0_4_load_104 | 122 | 0.0019844 | 0.00049734 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1140-25_0_4_load_102 | 123 | 0.0018811 | 0.00047146 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1140-25_0_4_load_105 | 124 | 0.0030659 | 0.00076839 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1140-25_0_4_load_107 | 125 | 0.0024 | 0.0006015 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1140-25_0_4_load_109 | 126 | 0.0057588 | 0.0014433 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1140-25_0_4_load_110 | 127 | 0.0010907 | 0.00027337 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 87 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1140-25_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.030701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1140-25_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.12349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1140-25_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.1383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1140-25_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.045488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1140-25_0_4_line_4 | NAYY 4x150 SE | 3 | 8 | 0.075927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1140-25_0_4_line_5 | NAYY 4x150 SE | 4 | 110 | 0.030845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1140-25_0_4_line_6 | NAYY 4x150 SE | 5 | 6 | 0.98901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1140-25_0_4_line_7 | NAYY 4x150 SE | 5 | 7 | 0.052672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_1140-25_0_4_line_8 | NAYY 4x150 SE | 6 | 109 | 0.064026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1140-25_0_4_line_9 | NAYY 4x150 SE | 7 | 97 | 0.013196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_1140-25_0_4_line_10 | NAYY 4x150 SE | 9 | 10 | 0.023293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1140-25_0_4_line_11 | NAYY 4x150 SE | 9 | 11 | 0.022239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1140-25_0_4_line_12 | NAYY 4x150 SE | 10 | 12 | 0.074804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1140-25_0_4_line_13 | NAYY 4x150 SE | 12 | 13 | 0.093686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1140-25_0_4_line_14 | NAYY 4x150 SE | 13 | 14 | 0.11654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1140-25_0_4_line_15 | NAYY 4x150 SE | 13 | 15 | 0.10602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1140-25_0_4_line_16 | NAYY 4x150 SE | 14 | 22 | 0.077312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1140-25_0_4_line_17 | NAYY 4x150 SE | 14 | 23 | 0.037536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1140-25_0_4_line_18 | NAYY 4x150 SE | 15 | 16 | 0.027297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1140-25_0_4_line_19 | NAYY 4x150 SE | 16 | 17 | 0.02793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1140-25_0_4_line_20 | NAYY 4x150 SE | 17 | 18 | 0.020269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1140-25_0_4_line_21 | NAYY 4x150 SE | 19 | 20 | 0.014599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1140-25_0_4_line_22 | NAYY 4x150 SE | 19 | 21 | 0.049345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1140-25_0_4_line_23 | NAYY 4x150 SE | 20 | 24 | 0.0097483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1140-25_0_4_line_24 | NAYY 4x150 SE | 21 | 25 | 0.009056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1140-25_0_4_line_25 | NAYY 4x150 SE | 22 | 26 | 0.069341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1140-25_0_4_line_26 | NAYY 4x150 SE | 23 | 27 | 0.030949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1140-25_0_4_line_27 | NAYY 4x150 SE | 24 | 48 | 0.023076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1140-25_0_4_line_28 | NAYY 4x150 SE | 25 | 47 | 0.015261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1140-25_0_4_line_29 | NAYY 4x150 SE | 26 | 120 | 0.0093163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1140-25_0_4_line_30 | NAYY 4x150 SE | 28 | 29 | 0.002325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1140-25_0_4_line_31 | NAYY 4x150 SE | 28 | 30 | 0.019605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1140-25_0_4_line_32 | NAYY 4x150 SE | 29 | 31 | 0.0096775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1140-25_0_4_line_33 | NAYY 4x150 SE | 30 | 32 | 0.011269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1140-25_0_4_line_34 | NAYY 4x150 SE | 30 | 33 | 0.014332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1140-25_0_4_line_35 | NAYY 4x150 SE | 33 | 34 | 0.028213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1140-25_0_4_line_36 | NAYY 4x150 SE | 34 | 35 | 0.0040156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1140-25_0_4_line_37 | NAYY 4x150 SE | 35 | 49 | 0.00618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1140-25_0_4_line_38 | NAYY 4x150 SE | 36 | 37 | 0.027547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1140-25_0_4_line_39 | NAYY 4x150 SE | 36 | 38 | 0.017667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1140-25_0_4_line_40 | NAYY 4x150 SE | 37 | 39 | 0.010516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1140-25_0_4_line_41 | NAYY 4x150 SE | 38 | 40 | 0.013661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1140-25_0_4_line_42 | NAYY 4x150 SE | 39 | 41 | 0.0043614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1140-25_0_4_line_43 | NAYY 4x150 SE | 40 | 42 | 0.0090078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1140-25_0_4_line_44 | NAYY 4x150 SE | 40 | 43 | 0.030252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1140-25_0_4_line_45 | NAYY 4x150 SE | 41 | 44 | 0.013335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1140-25_0_4_line_46 | NAYY 4x150 SE | 42 | 45 | 0.038496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1140-25_0_4_line_47 | NAYY 4x150 SE | 43 | 46 | 0.041338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_1140-25_0_4_line_48 | NAYY 4x150 SE | 43 | 47 | 0.0015417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1140-25_0_4_line_49 | NAYY 4x150 SE | 44 | 52 | 0.031372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1140-25_0_4_line_50 | NAYY 4x150 SE | 44 | 50 | 0.006743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1140-25_0_4_line_51 | NAYY 4x150 SE | 45 | 54 | 0.010039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1140-25_0_4_line_52 | NAYY 4x150 SE | 46 | 55 | 0.036742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
53 | LV_1140-25_0_4_line_53 | NAYY 4x150 SE | 48 | 124 | 0.017756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1140-25_0_4_line_54 | NAYY 4x150 SE | 49 | 50 | 0.019097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1140-25_0_4_line_55 | NAYY 4x150 SE | 50 | 51 | 0.019496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1140-25_0_4_line_56 | NAYY 4x150 SE | 51 | 53 | 0.024873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1140-25_0_4_line_57 | NAYY 4x150 SE | 52 | 60 | 0.020259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1140-25_0_4_line_58 | NAYY 4x150 SE | 53 | 62 | 0.017498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1140-25_0_4_line_59 | NAYY 4x150 SE | 54 | 63 | 0.021384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1140-25_0_4_line_60 | NAYY 4x150 SE | 55 | 76 | 0.018364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_1140-25_0_4_line_61 | NAYY 4x150 SE | 56 | 57 | 0.048989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1140-25_0_4_line_62 | NAYY 4x150 SE | 57 | 58 | 0.025314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1140-25_0_4_line_63 | NAYY 4x150 SE | 58 | 59 | 0.016509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1140-25_0_4_line_64 | NAYY 4x150 SE | 59 | 60 | 0.021205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1140-25_0_4_line_65 | NAYY 4x150 SE | 61 | 62 | 0.02539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1140-25_0_4_line_66 | NAYY 4x150 SE | 63 | 64 | 0.022187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1140-25_0_4_line_67 | NAYY 4x150 SE | 64 | 65 | 0.027153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1140-25_0_4_line_68 | NAYY 4x150 SE | 65 | 66 | 0.013754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1140-25_0_4_line_69 | NAYY 4x150 SE | 66 | 67 | 0.039113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1140-25_0_4_line_70 | NAYY 4x150 SE | 66 | 68 | 0.034644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1140-25_0_4_line_71 | NAYY 4x150 SE | 67 | 69 | 0.046409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1140-25_0_4_line_72 | NAYY 4x150 SE | 67 | 70 | 0.08617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1140-25_0_4_line_73 | NAYY 4x150 SE | 68 | 71 | 0.014478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1140-25_0_4_line_74 | NAYY 4x150 SE | 70 | 72 | 0.089075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1140-25_0_4_line_75 | NAYY 4x150 SE | 71 | 73 | 0.0411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1140-25_0_4_line_76 | NAYY 4x150 SE | 72 | 127 | 0.023024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1140-25_0_4_line_77 | NAYY 4x150 SE | 73 | 74 | 0.021628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1140-25_0_4_line_78 | NAYY 4x150 SE | 74 | 75 | 0.021029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1140-25_0_4_line_79 | NAYY 4x150 SE | 76 | 77 | 0.037673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1140-25_0_4_line_80 | NAYY 4x150 SE | 76 | 78 | 0.014392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
81 | LV_1140-25_0_4_line_81 | NAYY 4x150 SE | 77 | 85 | 0.027169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1140-25_0_4_line_82 | NAYY 4x150 SE | 78 | 79 | 0.0077202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
83 | LV_1140-25_0_4_line_83 | NAYY 4x150 SE | 79 | 80 | 0.012045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
84 | LV_1140-25_0_4_line_84 | NAYY 4x150 SE | 80 | 81 | 0.027606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1140-25_0_4_line_85 | NAYY 4x150 SE | 80 | 82 | 0.0038272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
86 | LV_1140-25_0_4_line_86 | NAYY 4x150 SE | 81 | 83 | 0.0056881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1140-25_0_4_line_87 | NAYY 4x150 SE | 82 | 84 | 0.02002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_1140-25_0_4_line_88 | NAYY 4x150 SE | 83 | 86 | 0.016246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1140-25_0_4_line_89 | NAYY 4x150 SE | 84 | 87 | 0.0126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
90 | LV_1140-25_0_4_line_90 | NAYY 4x150 SE | 84 | 88 | 0.033066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
91 | LV_1140-25_0_4_line_91 | NAYY 4x150 SE | 85 | 121 | 0.01715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1140-25_0_4_line_92 | NAYY 4x150 SE | 86 | 103 | 0.0091818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1140-25_0_4_line_93 | NAYY 4x150 SE | 87 | 100 | 0.023242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1140-25_0_4_line_94 | NAYY 4x150 SE | 88 | 95 | 0.0054721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
95 | LV_1140-25_0_4_line_95 | NAYY 4x150 SE | 89 | 90 | 0.018408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1140-25_0_4_line_96 | NAYY 4x150 SE | 89 | 91 | 0.0018715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1140-25_0_4_line_97 | NAYY 4x150 SE | 90 | 92 | 0.022903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1140-25_0_4_line_98 | NAYY 4x150 SE | 92 | 93 | 0.0008275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1140-25_0_4_line_99 | NAYY 4x150 SE | 93 | 94 | 0.0095265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1140-25_0_4_line_100 | NAYY 4x150 SE | 94 | 102 | 0.012372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1140-25_0_4_line_101 | NAYY 4x150 SE | 95 | 96 | 0.020715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
102 | LV_1140-25_0_4_line_102 | NAYY 4x150 SE | 96 | 97 | 0.010489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
103 | LV_1140-25_0_4_line_103 | NAYY 4x150 SE | 96 | 98 | 0.025797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1140-25_0_4_line_104 | NAYY 4x150 SE | 98 | 99 | 0.0052895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1140-25_0_4_line_105 | NAYY 4x150 SE | 99 | 101 | 0.027688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1140-25_0_4_line_106 | NAYY 4x150 SE | 100 | 119 | 0.0046396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1140-25_0_4_line_107 | NAYY 4x150 SE | 101 | 113 | 0.0012665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1140-25_0_4_line_108 | NAYY 4x150 SE | 102 | 103 | 0.0061332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1140-25_0_4_line_109 | NAYY 4x150 SE | 104 | 105 | 0.10496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1140-25_0_4_line_110 | NAYY 4x150 SE | 104 | 106 | 0.038237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1140-25_0_4_line_111 | NAYY 4x150 SE | 106 | 107 | 0.01664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1140-25_0_4_line_112 | NAYY 4x150 SE | 106 | 108 | 0.029789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1140-25_0_4_line_113 | NAYY 4x150 SE | 107 | 109 | 0.014027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1140-25_0_4_line_114 | NAYY 4x150 SE | 108 | 110 | 0.056668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1140-25_0_4_line_115 | NAYY 4x150 SE | 110 | 112 | 0.087483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1140-25_0_4_line_116 | NAYY 4x150 SE | 111 | 112 | 0.069991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1140-25_0_4_line_117 | NAYY 4x150 SE | 113 | 114 | 0.021796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1140-25_0_4_line_118 | NAYY 4x150 SE | 115 | 116 | 0.024321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1140-25_0_4_line_119 | NAYY 4x150 SE | 115 | 117 | 0.0033558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1140-25_0_4_line_120 | NAYY 4x150 SE | 116 | 118 | 0.019472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1140-25_0_4_line_121 | NAYY 4x150 SE | 117 | 119 | 0.018339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_1140-25_0_4_line_122 | NAYY 4x150 SE | 120 | 123 | 0.018993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_1140-25_0_4_line_123 | NAYY 4x150 SE | 121 | 122 | 0.006878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_1140-25_0_4_line_124 | NAYY 4x150 SE | 122 | 123 | 0.011266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_1140-25_0_4_line_125 | NAYY 4x150 SE | 124 | 125 | 0.0063394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_1140-25_0_4_line_126 | NAYY 4x150 SE | 126 | 127 | 0.01992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1140-25_0_4_trafo_95 | 0.25 MVA 20/0.4 kV | 128 | 87 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2640239.5176 | 1231119.6799 | 2640242.2024 | 1231130.3046 | 2640237.0257 | 1231143.2443 | 2640233.9271 | 1231148.1535
1 | 2640354.2201 | 1231176.076 | 2640233.9271 | 1231148.1535
2 | 2640239.5176 | 1231119.6799 | 2640103.9793 | 1231092.1799
3 | 2640395.1912 | 1231195.8372 | 2640354.2201 | 1231176.076
4 | 2640103.9793 | 1231092.1799 | 2640061.0903 | 1231067.0658 | 2640075.128 | 1231044.9136
5 | 2640395.1912 | 1231195.8372 | 2640399.6885 | 1231199.3588 | 2640413.5211 | 1231211.0155 | 2640417.1223 | 1231217.1215
6 | 2640838.9673 | 1232253.9239 | 2640497.1722 | 1231325.8554
7 | 2640838.9673 | 1232253.9239 | 2640839.8072 | 1232265.0255 | 2640839.7636 | 1232271.3847 | 2640841.6751 | 1232285.2176 | 2640843.6128 | 1232295.2371 | 2640844.2997 | 1232301.0566 | 2640842.9357 | 1232306.0229
8 | 2640497.1722 | 1231325.8554 | 2640452.006 | 1231315.9532 | 2640436.1995 | 1231307.7961
9 | 2640838.1847 | 1232318.2698 | 2640841.3098 | 1232311.9428 | 2640842.9357 | 1232306.0229
10 | 2640866.9932 | 1232631.0838 | 2640843.7006 | 1232630.9691
11 | 2640866.9932 | 1232631.0838 | 2640889.2319 | 1232631.1933
12 | 2640768.8972 | 1232630.6006 | 2640843.7006 | 1232630.9691
13 | 2640707.2791 | 1232597.8027 | 2640706.8205 | 1232629.3971 | 2640729.6152 | 1232629.7755 | 2640768.8972 | 1232630.6006
14 | 2640657.2779 | 1232506.9597 | 2640662.2553 | 1232513.1865 | 2640665.0549 | 1232517.8752 | 2640671.3186 | 1232530.8595 | 2640684.4974 | 1232551.2401 | 2640693.1629 | 1232565.0635 | 2640687.1445 | 1232569.3695 | 2640696.49 | 1232597.7844 | 2640707.2791 | 1232597.8027
15 | 2640707.2791 | 1232597.8027 | 2640813.3011 | 1232597.9121
16 | 2640645.9469 | 1232433.3364 | 2640643.2571 | 1232448.0161 | 2640644.3507 | 1232470.7933 | 2640644.8726 | 1232476.4115 | 2640645.5444 | 1232482.253 | 2640646.7676 | 1232488.2874 | 2640648.3827 | 1232494.5912 | 2640650.3732 | 1232499.141 | 2640657.2779 | 1232506.9597
17 | 2640657.2779 | 1232506.9597 | 2640663.6997 | 1232504.5799 | 2640666.1041 | 1232503.9626 | 2640668.514 | 1232503.6455 | 2640694.2446 | 1232502.141
18 | 2640840.5982 | 1232597.9403 | 2640813.3011 | 1232597.9121
19 | 2640840.5982 | 1232597.9403 | 2640868.5286 | 1232597.9691
20 | 2640888.7972 | 1232597.99 | 2640868.5286 | 1232597.9691
21 | 2640763.2438 | 1232554.0474 | 2640765.7485 | 1232539.6646
22 | 2640763.2438 | 1232554.0474 | 2640774.0041 | 1232552.7537 | 2640780.3282 | 1232551.3628 | 2640811.2483 | 1232542.9972
23 | 2640767.421 | 1232530.0608 | 2640765.7485 | 1232539.6646
24 | 2640811.2483 | 1232542.9972 | 2640819.99 | 1232540.6321
25 | 2640645.9469 | 1232433.3364 | 2640715.2476 | 1232435.7056
26 | 2640694.2446 | 1232502.141 | 2640725.1408 | 1232500.3345
27 | 2640771.3802 | 1232507.3266 | 2640767.421 | 1232530.0608
28 | 2640819.99 | 1232540.6321 | 2640823.8918 | 1232539.5764 | 2640834.7224 | 1232536.6499
29 | 2640724.5584 | 1232436.0239 | 2640715.2476 | 1232435.7056
30 | 2640994.1008 | 1232584.8835 | 2640991.8355 | 1232585.4068
31 | 2640972.7336 | 1232589.8197 | 2640991.8355 | 1232585.4068
32 | 2641003.53 | 1232582.7052 | 2640994.1008 | 1232584.8835
33 | 2640972.7336 | 1232589.8197 | 2640975.126 | 1232600.8319
34 | 2640972.7336 | 1232589.8197 | 2640968.9927 | 1232575.9848
35 | 2640968.9927 | 1232575.9848 | 2640964.7522 | 1232560.3019 | 2640960.8551 | 1232548.9875
36 | 2640959.5073 | 1232545.2058 | 2640959.8234 | 1232545.9924 | 2640960.8551 | 1232548.9875
37 | 2640956.8233 | 1232539.6566 | 2640958.3048 | 1232542.2129 | 2640959.5073 | 1232545.2058
38 | 2640893.2918 | 1232537.0057 | 2640910.1972 | 1232537.6124 | 2640918.0828 | 1232537.0663 | 2640920.7307 | 1232536.4175
39 | 2640893.2918 | 1232537.0057 | 2640889.1159 | 1232536.8559 | 2640882.8513 | 1232536.1902 | 2640879.253 | 1232535.3539 | 2640875.9445 | 1232534.2304
40 | 2640920.7307 | 1232536.4175 | 2640923.953 | 1232535.628 | 2640930.564 | 1232532.7795
41 | 2640864.8305 | 1232526.3825 | 2640871.5542 | 1232531.8543 | 2640875.9445 | 1232534.2304
42 | 2640934.5694 | 1232531.0537 | 2640930.564 | 1232532.7795
43 | 2640864.8305 | 1232526.3825 | 2640868.2652 | 1232523.4821 | 2640871.5101 | 1232520.3465
44 | 2640836.2107 | 1232536.2477 | 2640854.0702 | 1232530.967 | 2640860.4091 | 1232528.5313 | 2640864.8305 | 1232526.3825
45 | 2640944.8564 | 1232522.6414 | 2640941.7906 | 1232525.8446 | 2640939.026 | 1232528.1937 | 2640934.5694 | 1232531.0537
46 | 2640897.0655 | 1232491.5669 | 2640873.3491 | 1232518.5695 | 2640871.5101 | 1232520.3465
47 | 2640839.3104 | 1232495.0322 | 2640836.2107 | 1232536.2477
48 | 2640836.2107 | 1232536.2477 | 2640834.7224 | 1232536.6499
49 | 2640944.8564 | 1232522.6414 | 2640944.9259 | 1232520.2404 | 2640944.9072 | 1232517.4608 | 2640944.6768 | 1232515.7359 | 2640944.0737 | 1232513.1524 | 2640942.2689 | 1232508.0701 | 2640941.5966 | 1232504.541 | 2640941.4997 | 1232501.016 | 2640942.0586 | 1232497.9179 | 2640943.2159 | 1232494.7905 | 2640944.7313 | 1232492.4328
50 | 2640944.8564 | 1232522.6414 | 2640951.5197 | 1232521.4866
51 | 2640903.6901 | 1232484.0244 | 2640897.0655 | 1232491.5669
52 | 2640839.3104 | 1232495.0322 | 2640842.182 | 1232458.4021
53 | 2640771.0691 | 1232490.2898 | 2640773.4664 | 1232495.3475 | 2640771.3802 | 1232507.3266
54 | 2640956.8233 | 1232539.6566 | 2640956.9033 | 1232536.8332 | 2640956.4396 | 1232534.9066 | 2640951.5197 | 1232521.4866
55 | 2640951.5197 | 1232521.4866 | 2640957.843 | 1232519.1175 | 2640968.8367 | 1232512.6724
56 | 2640991.8934 | 1232503.8042 | 2640987.4554 | 1232504.7902 | 2640981.3103 | 1232506.5601 | 2640975.0316 | 1232509.0407 | 2640968.8367 | 1232512.6724
57 | 2640961.6034 | 1232481.3464 | 2640956.0574 | 1232484.8616 | 2640947.1246 | 1232490.1256 | 2640944.7313 | 1232492.4328 | 2640944.7313 | 1232492.4328
58 | 2641009.299 | 1232503.6915 | 2641008.12 | 1232503.4095 | 2641003.8747 | 1232503.0801 | 2640997.0446 | 1232503.1553 | 2640992.7939 | 1232503.6041 | 2640991.8934 | 1232503.8042
59 | 2640903.6901 | 1232484.0244 | 2640917.8014 | 1232467.9578
60 | 2640843.6173 | 1232440.0942 | 2640842.182 | 1232458.4021
61 | 2641066.9907 | 1232480.3075 | 2641028.5797 | 1232472.4646 | 2641018.9995 | 1232470.473
62 | 2641018.9995 | 1232470.473 | 2640994.2153 | 1232465.3207
63 | 2640994.2153 | 1232465.3207 | 2640988.697 | 1232464.1735 | 2640979.5137 | 1232469.9941
64 | 2640979.5137 | 1232469.9941 | 2640961.6034 | 1232481.3464
65 | 2641033.993 | 1232509.5972 | 2641009.299 | 1232503.6915
66 | 2640934.5831 | 1232453.6073 | 2640922.5021 | 1232462.6057 | 2640917.8014 | 1232467.9578
67 | 2640956.3592 | 1232437.3874 | 2640934.5831 | 1232453.6073
68 | 2640967.3895 | 1232429.1715 | 2640956.3592 | 1232437.3874
69 | 2640967.3895 | 1232429.1715 | 2640985.5012 | 1232419.2234 | 2641000.5073 | 1232408.3533
70 | 2640967.3895 | 1232429.1715 | 2640952.1083 | 1232403.0278 | 2640948.5849 | 1232405.5998
71 | 2641000.5073 | 1232408.3533 | 2641037.3711 | 1232409.8084 | 2641043.7959 | 1232402.626
72 | 2641000.5073 | 1232408.3533 | 2641029.3424 | 1232379.4785 | 2641048.2861 | 1232358.7296 | 2641056.966 | 1232343.8027
73 | 2640948.5849 | 1232405.5998 | 2640936.8912 | 1232414.1355
74 | 2641093.8257 | 1232265.0855 | 2641079.8778 | 1232281.6217 | 2641066.4812 | 1232301.664 | 2641062.2898 | 1232325.3053 | 2641058.0866 | 1232341.8756 | 2641056.966 | 1232343.8027
75 | 2640936.8912 | 1232414.1355 | 2640903.6947 | 1232438.3671
76 | 2641093.8257 | 1232265.0855 | 2641116.0185 | 1232260.7361 | 2641116.4224 | 1232260.6705
77 | 2640903.6947 | 1232438.3671 | 2640886.2253 | 1232451.1188
78 | 2640886.2253 | 1232451.1188 | 2640885.2485 | 1232451.8318 | 2640870.8105 | 1232465.4093
79 | 2640843.6173 | 1232440.0942 | 2640805.9667 | 1232438.807
80 | 2640843.6173 | 1232440.0942 | 2640845.1002 | 1232425.7793
81 | 2640805.9667 | 1232438.807 | 2640778.814 | 1232437.8787
82 | 2640845.8957 | 1232418.1002 | 2640845.1002 | 1232425.7793
83 | 2640847.1368 | 1232406.1193 | 2640845.8957 | 1232418.1002
84 | 2640847.1368 | 1232406.1193 | 2640870.4456 | 1232391.3279
85 | 2640847.1368 | 1232406.1193 | 2640847.6428 | 1232402.3257
86 | 2640870.4456 | 1232391.3279 | 2640875.2484 | 1232388.2801
87 | 2640850.2899 | 1232382.4818 | 2640847.6428 | 1232402.3257
88 | 2640888.9655 | 1232379.5755 | 2640875.2484 | 1232388.2801
89 | 2640850.2899 | 1232382.4818 | 2640837.696 | 1232382.8658
90 | 2640850.2899 | 1232382.4818 | 2640853.3426 | 1232349.5573
91 | 2640778.814 | 1232437.8787 | 2640761.674 | 1232437.2928
92 | 2640896.7181 | 1232374.6558 | 2640888.9655 | 1232379.5755
93 | 2640837.696 | 1232382.8658 | 2640814.4647 | 1232383.5741
94 | 2640853.8477 | 1232344.1086 | 2640853.3426 | 1232349.5573
95 | 2640914.677 | 1232320.5438 | 2640918.5435 | 1232327.0718 | 2640921.4304 | 1232337.5002
96 | 2640913.7233 | 1232318.9335 | 2640914.677 | 1232320.5438
97 | 2640920.0967 | 1232358.1071 | 2640925.2814 | 1232351.4111 | 2640921.4304 | 1232337.5002
98 | 2640919.5901 | 1232358.7614 | 2640920.0967 | 1232358.1071
99 | 2640919.5901 | 1232358.7614 | 2640917.489 | 1232361.4749 | 2640912.343 | 1232364.7404
100 | 2640912.343 | 1232364.7404 | 2640901.8966 | 1232371.3696
101 | 2640844.4188 | 1232326.7178 | 2640854.2561 | 1232339.7046 | 2640853.8477 | 1232344.1086
102 | 2640838.1847 | 1232318.2698 | 2640844.4188 | 1232326.7178
103 | 2640844.4188 | 1232326.7178 | 2640819.0152 | 1232331.2071
104 | 2640813.8063 | 1232332.1276 | 2640819.0152 | 1232331.2071
105 | 2640813.8063 | 1232332.1276 | 2640790.5185 | 1232336.2429 | 2640786.48 | 1232336.1491
106 | 2640814.4647 | 1232383.5741 | 2640809.8272 | 1232383.7154
107 | 2640785.2138 | 1232336.1197 | 2640786.48 | 1232336.1491
108 | 2640896.7181 | 1232374.6558 | 2640901.8966 | 1232371.3696
109 | 2640376.2852 | 1231283.496 | 2640372.9575 | 1231284.9305 | 2640367.6614 | 1231290.8872 | 2640356.5222 | 1231313.1032 | 2640348.0863 | 1231326.432 | 2640338.5061 | 1231337.6518 | 2640311.1887 | 1231364.0473
110 | 2640413.7628 | 1231286.9087 | 2640405.6833 | 1231286.7648 | 2640386.0618 | 1231282.2733 | 2640379.1021 | 1231282.2816 | 2640376.2852 | 1231283.496
111 | 2640413.7628 | 1231286.9087 | 2640425.9071 | 1231298.2839
112 | 2640413.7628 | 1231286.9087 | 2640401.9022 | 1231273.7088 | 2640394.4311 | 1231264.2634
113 | 2640436.1995 | 1231307.7961 | 2640435.8942 | 1231307.6385 | 2640425.9071 | 1231298.2839
114 | 2640417.1223 | 1231217.1215 | 2640417.0916 | 1231221.6463 | 2640414.709 | 1231225.666 | 2640394.4354 | 1231246.9082 | 2640391.8703 | 1231256.619 | 2640394.4311 | 1231264.2634
115 | 2640417.1223 | 1231217.1215 | 2640454.6977 | 1231184.0785 | 2640486.5801 | 1231164.4392
116 | 2640542.6389 | 1231122.6573 | 2640499.3091 | 1231156.5982 | 2640486.5801 | 1231164.4392
117 | 2640785.2138 | 1232336.1197 | 2640763.4239 | 1232335.6135
118 | 2640788.1421 | 1232384.3766 | 2640763.8322 | 1232385.1178
119 | 2640788.1421 | 1232384.3766 | 2640791.4964 | 1232384.2743
120 | 2640744.3665 | 1232384.7617 | 2640761.5846 | 1232385.1863 | 2640763.8322 | 1232385.1178
121 | 2640809.8272 | 1232383.7154 | 2640791.4964 | 1232384.2743
122 | 2640724.5584 | 1232436.0239 | 2640743.5403 | 1232436.6728
123 | 2640754.8001 | 1232437.0578 | 2640761.674 | 1232437.2928
124 | 2640754.8001 | 1232437.0578 | 2640743.5403 | 1232436.6728
125 | 2640768.3538 | 1232484.5613 | 2640771.0691 | 1232490.2898
126 | 2641136.0854 | 1232257.4807 | 2641116.4224 | 1232260.6705

## bus_geodata
| x | y | coords
0 | 2640233.9271 | 1231148.1535
1 | 2640239.5176 | 1231119.6799
2 | 2640354.2201 | 1231176.076
3 | 2640103.9793 | 1231092.1799
4 | 2640395.1912 | 1231195.8372
5 | 2640838.9673 | 1232253.9239
6 | 2640497.1722 | 1231325.8554
7 | 2640842.9357 | 1232306.0229
8 | 2640075.128 | 1231044.9136
9 | 2640866.9932 | 1232631.0838
10 | 2640843.7006 | 1232630.9691
11 | 2640889.2319 | 1232631.1933
12 | 2640768.8972 | 1232630.6006
13 | 2640707.2791 | 1232597.8027
14 | 2640657.2779 | 1232506.9597
15 | 2640813.3011 | 1232597.9121
16 | 2640840.5982 | 1232597.9403
17 | 2640868.5286 | 1232597.9691
18 | 2640888.7972 | 1232597.99
19 | 2640763.2438 | 1232554.0474
20 | 2640765.7485 | 1232539.6646
21 | 2640811.2483 | 1232542.9972
22 | 2640645.9469 | 1232433.3364
23 | 2640694.2446 | 1232502.141
24 | 2640767.421 | 1232530.0608
25 | 2640819.99 | 1232540.6321
26 | 2640715.2476 | 1232435.7056
27 | 2640725.1408 | 1232500.3345
28 | 2640991.8355 | 1232585.4068
29 | 2640994.1008 | 1232584.8835
30 | 2640972.7336 | 1232589.8197
31 | 2641003.53 | 1232582.7052
32 | 2640975.126 | 1232600.8319
33 | 2640968.9927 | 1232575.9848
34 | 2640960.8551 | 1232548.9875
35 | 2640959.5073 | 1232545.2058
36 | 2640893.2918 | 1232537.0057
37 | 2640920.7307 | 1232536.4175
38 | 2640875.9445 | 1232534.2304
39 | 2640930.564 | 1232532.7795
40 | 2640864.8305 | 1232526.3825
41 | 2640934.5694 | 1232531.0537
42 | 2640871.5101 | 1232520.3465
43 | 2640836.2107 | 1232536.2477
44 | 2640944.8564 | 1232522.6414
45 | 2640897.0655 | 1232491.5669
46 | 2640839.3104 | 1232495.0322
47 | 2640834.7224 | 1232536.6499
48 | 2640771.3802 | 1232507.3266
49 | 2640956.8233 | 1232539.6566
50 | 2640951.5197 | 1232521.4866
51 | 2640968.8367 | 1232512.6724
52 | 2640944.7313 | 1232492.4328
53 | 2640991.8934 | 1232503.8042
54 | 2640903.6901 | 1232484.0244
55 | 2640842.182 | 1232458.4021
56 | 2641066.9907 | 1232480.3075
57 | 2641018.9995 | 1232470.473
58 | 2640994.2153 | 1232465.3207
59 | 2640979.5137 | 1232469.9941
60 | 2640961.6034 | 1232481.3464
61 | 2641033.993 | 1232509.5972
62 | 2641009.299 | 1232503.6915
63 | 2640917.8014 | 1232467.9578
64 | 2640934.5831 | 1232453.6073
65 | 2640956.3592 | 1232437.3874
66 | 2640967.3895 | 1232429.1715
67 | 2641000.5073 | 1232408.3533
68 | 2640948.5849 | 1232405.5998
69 | 2641043.7959 | 1232402.626
70 | 2641056.966 | 1232343.8027
71 | 2640936.8912 | 1232414.1355
72 | 2641093.8257 | 1232265.0855
73 | 2640903.6947 | 1232438.3671
74 | 2640886.2253 | 1232451.1188
75 | 2640870.8105 | 1232465.4093
76 | 2640843.6173 | 1232440.0942
77 | 2640805.9667 | 1232438.807
78 | 2640845.1002 | 1232425.7793
79 | 2640845.8957 | 1232418.1002
80 | 2640847.1368 | 1232406.1193
81 | 2640870.4456 | 1232391.3279
82 | 2640847.6428 | 1232402.3257
83 | 2640875.2484 | 1232388.2801
84 | 2640850.2899 | 1232382.4818
85 | 2640778.814 | 1232437.8787
86 | 2640888.9655 | 1232379.5755
87 | 2640837.696 | 1232382.8658
88 | 2640853.3426 | 1232349.5573
89 | 2640914.677 | 1232320.5438
90 | 2640921.4304 | 1232337.5002
91 | 2640913.7233 | 1232318.9335
92 | 2640920.0967 | 1232358.1071
93 | 2640919.5901 | 1232358.7614
94 | 2640912.343 | 1232364.7404
95 | 2640853.8477 | 1232344.1086
96 | 2640844.4188 | 1232326.7178
97 | 2640838.1847 | 1232318.2698
98 | 2640819.0152 | 1232331.2071
99 | 2640813.8063 | 1232332.1276
100 | 2640814.4647 | 1232383.5741
101 | 2640786.48 | 1232336.1491
102 | 2640901.8966 | 1232371.3696
103 | 2640896.7181 | 1232374.6558
104 | 2640376.2852 | 1231283.496
105 | 2640311.1887 | 1231364.0473
106 | 2640413.7628 | 1231286.9087
107 | 2640425.9071 | 1231298.2839
108 | 2640394.4311 | 1231264.2634
109 | 2640436.1995 | 1231307.7961
110 | 2640417.1223 | 1231217.1215
111 | 2640542.6389 | 1231122.6573
112 | 2640486.5801 | 1231164.4392
113 | 2640785.2138 | 1232336.1197
114 | 2640763.4239 | 1232335.6135
115 | 2640788.1421 | 1232384.3766
116 | 2640763.8322 | 1232385.1178
117 | 2640791.4964 | 1232384.2743
118 | 2640744.3665 | 1232384.7617
119 | 2640809.8272 | 1232383.7154
120 | 2640724.5584 | 1232436.0239
121 | 2640761.674 | 1232437.2928
122 | 2640754.8001 | 1232437.0578
123 | 2640743.5403 | 1232436.6728
124 | 2640771.0691 | 1232490.2898
125 | 2640768.3538 | 1232484.5613
126 | 2641136.0854 | 1232257.4807
127 | 2641116.4224 | 1232260.6705
128 | 2640850.2899 | 1232382.4818

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97724 | -0.16066 | 0.0008584 | 0.00021514
1 | 0.97679 | -0.16391 | 0 | 0
2 | 0.97922 | -0.14652 | 0.0023797 | 0.00059642
3 | 0.97475 | -0.17856 | 0.0090622 | 0.0022712
4 | 0.9801 | -0.1402 | 0 | 0
5 | 0.99708 | -0.020334 | 0 | 0
6 | 0.9849 | -0.10605 | 0 | 0
7 | 0.99751 | -0.017311 | 0.0014291 | 0.00035815
8 | 0.97463 | -0.17938 | 0.0010299 | 0.00025812
9 | 0.97788 | -0.15555 | 0.0015752 | 0.00039478
10 | 0.97801 | -0.15457 | 0.0014799 | 0.00037089
11 | 0.9778 | -0.15612 | 0.0024457 | 0.00061295
12 | 0.97861 | -0.15028 | 0 | 0
13 | 0.97936 | -0.1449 | 0 | 0
14 | 0.98189 | -0.1269 | 0 | 0
15 | 0.97792 | -0.15522 | 0.0026146 | 0.00065529
16 | 0.97765 | -0.15714 | 0.0025955 | 0.0006505
17 | 0.97749 | -0.15834 | 0.001841 | 0.00046141
18 | 0.97742 | -0.15883 | 0.0022845 | 0.00057256
19 | 0.98542 | -0.10155 | 0 | 0
20 | 0.98509 | -0.1039 | 0.0031955 | 0.00080087
21 | 0.98654 | -0.093619 | 0.0025694 | 0.00064394
22 | 0.98459 | -0.1077 | 0 | 0
23 | 0.98139 | -0.13046 | 0.0067012 | 0.0016795
24 | 0.98492 | -0.10515 | 0.0026712 | 0.00066945
25 | 0.98678 | -0.091927 | 0.0055539 | 0.0013919
26 | 0.98701 | -0.090569 | 0.002172 | 0.00054435
27 | 0.98128 | -0.13125 | 0.0024573 | 0.00061586
28 | 0.97109 | -0.20349 | 0.002482 | 0.00062206
29 | 0.97104 | -0.20386 | 0.0036808 | 0.00092249
30 | 0.9716 | -0.19983 | 0 | 0
31 | 0.97087 | -0.20504 | 0.011493 | 0.0028804
32 | 0.9715 | -0.20056 | 0.0061438 | 0.0015398
33 | 0.9721 | -0.19622 | 0.0046239 | 0.0011589
34 | 0.97327 | -0.18776 | 0.0025408 | 0.00063678
35 | 0.97346 | -0.18645 | 0.0015117 | 0.00037887
36 | 0.97985 | -0.14082 | 0.0030347 | 0.00076056
37 | 0.97743 | -0.15804 | 0.0018537 | 0.00046457
38 | 0.98148 | -0.12926 | 0.003119 | 0.0007817
39 | 0.97653 | -0.16443 | 0.0025375 | 0.00063597
40 | 0.9828 | -0.11991 | 0 | 0
41 | 0.97618 | -0.16697 | 0 | 0
42 | 0.98231 | -0.12337 | 0.0017048 | 0.00042728
43 | 0.98736 | -0.087795 | 0 | 0
44 | 0.97509 | -0.17474 | 0 | 0
45 | 0.98033 | -0.13749 | 0.003173 | 0.00079523
46 | 0.98996 | -0.069573 | 0 | 0
47 | 0.9873 | -0.088209 | 0.0024923 | 0.00062462
48 | 0.98459 | -0.10747 | 0.0043122 | 0.0010807
49 | 0.97375 | -0.18434 | 0 | 0
50 | 0.97466 | -0.17782 | 0 | 0
51 | 0.97435 | -0.18006 | 0.0026481 | 0.00066368
52 | 0.97454 | -0.17873 | 0.0019869 | 0.00049797
53 | 0.97405 | -0.18224 | 0.0021265 | 0.00053295
54 | 0.97985 | -0.14085 | 0.0026102 | 0.00065419
55 | 0.99228 | -0.053455 | 0.0038268 | 0.00095908
56 | 0.97353 | -0.18595 | 0.0020532 | 0.00051457
57 | 0.97368 | -0.18489 | 0.0024596 | 0.00061642
58 | 0.97385 | -0.18368 | 0.0016126 | 0.00040416
59 | 0.97399 | -0.18262 | 0.0016124 | 0.00040411
60 | 0.97424 | -0.18089 | 0.0023835 | 0.00059736
61 | 0.97378 | -0.18419 | 0.003001 | 0.00075213
62 | 0.97389 | -0.18338 | 0.0031929 | 0.00080021
63 | 0.97893 | -0.14743 | 0.0020626 | 0.00051694
64 | 0.97804 | -0.1538 | 0.0022693 | 0.00056873
65 | 0.97704 | -0.16096 | 0.0025302 | 0.00063412
66 | 0.97658 | -0.16423 | 0 | 0
67 | 0.97592 | -0.16898 | 0 | 0
68 | 0.97602 | -0.16827 | 0.0016359 | 0.00040999
69 | 0.97567 | -0.1708 | 0.0037464 | 0.00093893
70 | 0.97494 | -0.17605 | 0.00096238 | 0.0002412
71 | 0.97582 | -0.16971 | 0.00065343 | 0.00016376
72 | 0.97404 | -0.18247 | 0 | 0
73 | 0.97529 | -0.17353 | 0.0015425 | 0.00038658
74 | 0.97506 | -0.17518 | 0.0016345 | 0.00040966
75 | 0.97488 | -0.17643 | 0.0056625 | 0.0014192
76 | 0.99347 | -0.04519 | 0 | 0
77 | 0.99134 | -0.060081 | 0.0015907 | 0.00039867
78 | 0.99467 | -0.036839 | 0.0016334 | 0.00040936
79 | 0.99532 | -0.032325 | 0.0025755 | 0.00064547
80 | 0.99635 | -0.02519 | 0 | 0
81 | 0.99566 | -0.030034 | 0.0023315 | 0.00058432
82 | 0.99671 | -0.022702 | 0.0018024 | 0.00045172
83 | 0.99554 | -0.0309 | 0.0023562 | 0.00059051
84 | 0.99861 | -0.0095975 | 0 | 0
85 | 0.98987 | -0.070418 | 0.0021297 | 0.00053374
86 | 0.99524 | -0.032987 | 0.0024987 | 0.00062623
87 | 1 | 0 | -0.24295 | -0.061172
88 | 0.99809 | -0.013217 | 0.0013 | 0.0003258
89 | 0.99453 | -0.038008 | 0.0021129 | 0.00052955
90 | 0.99463 | -0.037304 | 0.0013835 | 0.00034674
91 | 0.99452 | -0.03804 | 0.001676 | 0.00042005
92 | 0.9948 | -0.036109 | 0.00090932 | 0.0002279
93 | 0.99481 | -0.036058 | 0.00051269 | 0.00012849
94 | 0.9949 | -0.035424 | 0.0011161 | 0.00027971
95 | 0.99801 | -0.013793 | 0.0019364 | 0.0004853
96 | 0.99772 | -0.015838 | 0 | 0
97 | 0.99762 | -0.01649 | 0 | 0
98 | 0.99731 | -0.01867 | 0.0014875 | 0.00037281
99 | 0.99724 | -0.019172 | 0.0037306 | 0.00093498
100 | 0.99967 | -0.0022924 | 0.0017576 | 0.0004405
101 | 0.99702 | -0.020763 | 0.0022857 | 0.00057286
102 | 0.99503 | -0.034461 | 0.00079232 | 0.00019857
103 | 0.99511 | -0.033935 | 0.0017433 | 0.00043691
104 | 0.98259 | -0.12253 | 0.00010785 | 2.703e-05
105 | 0.98254 | -0.12288 | 0.00032282 | 8.0907e-05
106 | 0.98261 | -0.12235 | 0 | 0
107 | 0.98299 | -0.11964 | 0.00081744 | 0.00020487
108 | 0.98195 | -0.12707 | 0.00023724 | 5.9459e-05
109 | 0.98333 | -0.11724 | 0.00038334 | 9.6074e-05
110 | 0.98071 | -0.13592 | 0 | 0
111 | 0.98047 | -0.13759 | 0.00018852 | 4.7248e-05
112 | 0.98049 | -0.13745 | 0.0014878 | 0.00037288
113 | 0.99701 | -0.020806 | 0.0012677 | 0.00031772
114 | 0.99694 | -0.021281 | 0.0021663 | 0.00054293
115 | 0.99942 | -0.0040391 | 0.0022446 | 0.00056254
116 | 0.99933 | -0.0047112 | 0.001827 | 0.00045789
117 | 0.99945 | -0.003871 | 0.0015504 | 0.00038857
118 | 0.9993 | -0.0048935 | 0.00093562 | 0.00023449
119 | 0.99962 | -0.0026686 | 0.001556 | 0.00038997
120 | 0.98736 | -0.088065 | 0.0027201 | 0.00068172
121 | 0.98899 | -0.076586 | 0.0024519 | 0.00061451
122 | 0.98866 | -0.07889 | 0.0019844 | 0.00049734
123 | 0.98816 | -0.08244 | 0.0018811 | 0.00047146
124 | 0.98445 | -0.10847 | 0.0030659 | 0.00076839
125 | 0.98443 | -0.10863 | 0.0024 | 0.0006015
126 | 0.97364 | -0.18534 | 0.0057588 | 0.0014433
127 | 0.97381 | -0.18413 | 0.0010907 | 0.00027337
128 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.010117 | 0.0025359 | -0.010113 | -0.0025346 | 4.5465e-06 | 1.3642e-06 | 0.015405 | 0.015405 | 0.015405 | 0.97724 | -0.16066 | 0.97679 | -0.16391 | 5.7057
1 | -0.010976 | -0.0027511 | 0.010997 | 0.0027578 | 2.1522e-05 | 6.7273e-06 | 0.016712 | 0.016712 | 0.016712 | 0.97724 | -0.16066 | 0.97922 | -0.14652 | 6.1898
2 | 0.010113 | 0.0025346 | -0.010092 | -0.0025284 | 2.0482e-05 | 6.1501e-06 | 0.015405 | 0.015406 | 0.015406 | 0.97679 | -0.16391 | 0.97475 | -0.17856 | 5.7059
3 | -0.013377 | -0.0033542 | 0.013389 | 0.0033581 | 1.1729e-05 | 3.9385e-06 | 0.020328 | 0.020328 | 0.020328 | 0.97922 | -0.14652 | 0.9801 | -0.1402 | 7.5289
4 | 0.00103 | 0.00025722 | -0.0010299 | -0.00025812 | 1.1711e-07 | -9.0128e-07 | 0.0015721 | 0.0015724 | 0.0015724 | 0.97475 | -0.17856 | 0.97463 | -0.17938 | 0.58237
5 | -0.013389 | -0.0033581 | 0.013397 | 0.0033608 | 7.9533e-06 | 2.67e-06 | 0.020328 | 0.020328 | 0.020328 | 0.9801 | -0.1402 | 0.98071 | -0.13592 | 7.5288
6 | 0.017212 | 0.0043217 | -0.017008 | -0.0042689 | 0.00020372 | 5.2867e-05 | 0.02569 | 0.025699 | 0.025699 | 0.99708 | -0.020334 | 0.9849 | -0.10605 | 4.759
7 | -0.017212 | -0.0043217 | 0.017219 | 0.0043224 | 7.2303e-06 | 7.1902e-07 | 0.02569 | 0.025689 | 0.02569 | 0.99708 | -0.020334 | 0.99751 | -0.017311 | 3.1716
8 | 0.017008 | 0.0042689 | -0.016982 | -0.0042595 | 2.6386e-05 | 9.3349e-06 | 0.025699 | 0.025699 | 0.025699 | 0.9849 | -0.10605 | 0.98333 | -0.11724 | 9.5182
9 | -0.018648 | -0.0046806 | 0.01865 | 0.0046809 | 2.1244e-06 | 3.0024e-07 | 0.027821 | 0.027821 | 0.027821 | 0.99751 | -0.017311 | 0.99762 | -0.01649 | 3.4347
10 | -0.0040211 | -0.0010075 | 0.0040216 | 0.0010074 | 5.4415e-07 | -8.2968e-08 | 0.0061187 | 0.0061186 | 0.0061187 | 0.97788 | -0.15555 | 0.97801 | -0.15457 | 2.2662
11 | 0.0024459 | 0.00061274 | -0.0024457 | -0.00061295 | 1.9223e-07 | -2.0504e-07 | 0.0037218 | 0.0037219 | 0.0037219 | 0.97788 | -0.15555 | 0.9778 | -0.15612 | 1.3785
12 | -0.0055015 | -0.0013783 | 0.0055047 | 0.0013786 | 3.2701e-06 | 3.1844e-07 | 0.0083701 | 0.0083698 | 0.0083701 | 0.97801 | -0.15457 | 0.97861 | -0.15028 | 3.1
13 | -0.0055047 | -0.0013786 | 0.0055088 | 0.001379 | 4.0951e-06 | 3.9706e-07 | 0.0083698 | 0.0083694 | 0.0083698 | 0.97861 | -0.15028 | 0.97936 | -0.1449 | 3.0999
14 | -0.014861 | -0.0037227 | 0.014898 | 0.0037354 | 3.7068e-05 | 1.2787e-05 | 0.022578 | 0.022577 | 0.022578 | 0.97936 | -0.1449 | 0.98189 | -0.1269 | 8.3622
15 | 0.0093517 | 0.0023436 | -0.0093383 | -0.0023398 | 1.3357e-05 | 3.805e-06 | 0.014209 | 0.014209 | 0.014209 | 0.97936 | -0.1449 | 0.97792 | -0.15522 | 5.2626
16 | -0.024061 | -0.0060317 | 0.024125 | 0.0060554 | 6.4144e-05 | 2.369e-05 | 0.036464 | 0.036464 | 0.036464 | 0.98189 | -0.1269 | 0.98459 | -0.1077 | 13.5052
17 | 0.0091632 | 0.0022963 | -0.0091587 | -0.002295 | 4.5168e-06 | 1.2627e-06 | 0.013887 | 0.013887 | 0.013887 | 0.98189 | -0.1269 | 0.98139 | -0.13046 | 5.1432
18 | 0.0067237 | 0.0016845 | -0.0067219 | -0.0016842 | 1.7828e-06 | 3.4332e-07 | 0.010231 | 0.010231 | 0.010231 | 0.97792 | -0.15522 | 0.97765 | -0.15714 | 3.7892
19 | 0.0041264 | 0.0010337 | -0.0041257 | -0.0010338 | 6.8744e-07 | -8.5773e-08 | 0.0062803 | 0.0062805 | 0.0062805 | 0.97765 | -0.15714 | 0.97749 | -0.15834 | 2.3261
20 | 0.0022847 | 0.00057236 | -0.0022845 | -0.00057256 | 1.5298e-07 | -1.9521e-07 | 0.0034779 | 0.003478 | 0.003478 | 0.97749 | -0.15834 | 0.97742 | -0.15883 | 1.2881
21 | 0.015656 | 0.0039244 | -0.015651 | -0.0039226 | 5.0916e-06 | 1.7724e-06 | 0.023641 | 0.023641 | 0.023641 | 0.98542 | -0.10155 | 0.98509 | -0.1039 | 8.756
22 | -0.015656 | -0.0039244 | 0.015673 | 0.0039303 | 1.7209e-05 | 5.9896e-06 | 0.023641 | 0.023641 | 0.023641 | 0.98542 | -0.10155 | 0.98654 | -0.093619 | 8.756
23 | 0.012455 | 0.0031217 | -0.012453 | -0.003121 | 2.1532e-06 | 7.0409e-07 | 0.018814 | 0.018814 | 0.018814 | 0.98509 | -0.1039 | 0.98492 | -0.10515 | 6.9683
24 | -0.018243 | -0.0045743 | 0.018247 | 0.0045758 | 4.2786e-06 | 1.53e-06 | 0.027516 | 0.027516 | 0.027516 | 0.98654 | -0.093619 | 0.98678 | -0.091927 | 10.1913
25 | -0.024125 | -0.0060554 | 0.024183 | 0.0060767 | 5.753e-05 | 2.1243e-05 | 0.036464 | 0.036463 | 0.036464 | 0.98459 | -0.1077 | 0.98701 | -0.090569 | 13.5051
26 | 0.0024576 | 0.00061557 | -0.0024573 | -0.00061586 | 2.6814e-07 | -2.8788e-07 | 0.0037261 | 0.0037263 | 0.0037263 | 0.98139 | -0.13046 | 0.98128 | -0.13125 | 1.3801
27 | 0.0097821 | 0.0024515 | -0.0097789 | -0.0024506 | 3.1451e-06 | 9.1606e-07 | 0.014779 | 0.014779 | 0.014779 | 0.98492 | -0.10515 | 0.98459 | -0.10747 | 5.4737
28 | -0.023801 | -0.0059678 | 0.023813 | 0.0059723 | 1.2267e-05 | 4.5232e-06 | 0.035891 | 0.035891 | 0.035891 | 0.98678 | -0.091927 | 0.9873 | -0.088209 | 13.2931
29 | -0.026355 | -0.006621 | 0.026364 | 0.0066244 | 9.1798e-06 | 3.4116e-06 | 0.039738 | 0.039738 | 0.039738 | 0.98701 | -0.090569 | 0.98736 | -0.088065 | 14.7177
30 | 0.015176 | 0.0038038 | -0.015176 | -0.0038035 | 7.846e-07 | 2.7301e-07 | 0.023255 | 0.023255 | 0.023255 | 0.97109 | -0.20349 | 0.97104 | -0.20386 | 8.6131
31 | -0.017659 | -0.0044259 | 0.017667 | 0.0044291 | 8.9569e-06 | 3.2023e-06 | 0.027059 | 0.027058 | 0.027059 | 0.97109 | -0.20349 | 0.9716 | -0.19983 | 10.0217
32 | 0.011495 | 0.002881 | -0.011493 | -0.0028804 | 1.8737e-06 | 6.0097e-07 | 0.017615 | 0.017615 | 0.017615 | 0.97104 | -0.20386 | 0.97087 | -0.20504 | 6.524
33 | 0.0061444 | 0.0015399 | -0.0061438 | -0.0015398 | 6.2269e-07 | 9.995e-08 | 0.0094103 | 0.0094103 | 0.0094103 | 0.9716 | -0.19983 | 0.9715 | -0.20056 | 3.4853
34 | -0.023812 | -0.0059689 | 0.023824 | 0.0059733 | 1.1894e-05 | 4.397e-06 | 0.036469 | 0.036469 | 0.036469 | 0.9716 | -0.19983 | 0.9721 | -0.19622 | 13.5069
35 | -0.028448 | -0.0071322 | 0.028481 | 0.0071447 | 3.3384e-05 | 1.249e-05 | 0.043547 | 0.043546 | 0.043547 | 0.9721 | -0.19622 | 0.97327 | -0.18776 | 16.1283
36 | -0.031022 | -0.0077815 | 0.031027 | 0.0077836 | 5.6371e-06 | 2.1182e-06 | 0.047431 | 0.047431 | 0.047431 | 0.97327 | -0.18776 | 0.97346 | -0.18645 | 17.567
37 | -0.032539 | -0.0081624 | 0.032549 | 0.008166 | 9.5414e-06 | 3.5929e-06 | 0.049742 | 0.049742 | 0.049742 | 0.97346 | -0.18645 | 0.97375 | -0.18434 | 18.4228
38 | 0.060361 | 0.015179 | -0.060217 | -0.015123 | 0.00014449 | 5.5229e-05 | 0.091684 | 0.091685 | 0.091685 | 0.97985 | -0.14082 | 0.97743 | -0.15804 | 33.9572
39 | -0.063396 | -0.015939 | 0.063498 | 0.015978 | 0.00010222 | 3.9092e-05 | 0.096293 | 0.096293 | 0.096293 | 0.97985 | -0.14082 | 0.98148 | -0.12926 | 35.664
40 | 0.058363 | 0.014659 | -0.058312 | -0.014639 | 5.1818e-05 | 1.9798e-05 | 0.088863 | 0.088863 | 0.088863 | 0.97743 | -0.15804 | 0.97653 | -0.16443 | 32.9121
41 | -0.066617 | -0.01676 | 0.066704 | 0.016793 | 8.6994e-05 | 3.3286e-05 | 0.10102 | 0.10102 | 0.10102 | 0.98148 | -0.12926 | 0.9828 | -0.11991 | 37.4154
42 | 0.055774 | 0.014003 | -0.055754 | -0.013996 | 1.9661e-05 | 7.5075e-06 | 0.084996 | 0.084996 | 0.084996 | 0.97653 | -0.16443 | 0.97618 | -0.16697 | 31.48
43 | 0.037267 | 0.0093635 | -0.037249 | -0.0093568 | 1.7901e-05 | 6.7708e-06 | 0.056433 | 0.056433 | 0.056433 | 0.9828 | -0.11991 | 0.98231 | -0.12337 | 20.9011
44 | -0.10397 | -0.026157 | 0.10444 | 0.026336 | 0.000468 | 0.00017962 | 0.15745 | 0.15745 | 0.15745 | 0.9828 | -0.11991 | 0.98736 | -0.087795 | 58.3164
45 | 0.055754 | 0.013996 | -0.055694 | -0.013973 | 6.0114e-05 | 2.2954e-05 | 0.084996 | 0.084996 | 0.084996 | 0.97618 | -0.16697 | 0.97509 | -0.17474 | 31.48
46 | 0.035544 | 0.0089295 | -0.035475 | -0.0089032 | 6.966e-05 | 2.6306e-05 | 0.05385 | 0.053851 | 0.053851 | 0.98231 | -0.12337 | 0.98033 | -0.13749 | 19.9447
47 | -0.13075 | -0.032934 | 0.13108 | 0.033061 | 0.00033404 | 0.00012688 | 0.1971 | 0.1971 | 0.1971 | 0.98736 | -0.087795 | 0.98996 | -0.069573 | 24.3336
48 | 0.026307 | 0.0065975 | -0.026305 | -0.0065969 | 1.5122e-06 | 5.6191e-07 | 0.039648 | 0.039648 | 0.039648 | 0.98736 | -0.087795 | 0.9873 | -0.088209 | 14.6843
49 | 0.012122 | 0.0030378 | -0.012115 | -0.0030356 | 6.6986e-06 | 2.1853e-06 | 0.018498 | 0.018498 | 0.018498 | 0.97509 | -0.17474 | 0.97454 | -0.17873 | 6.8511
50 | 0.043573 | 0.010935 | -0.043554 | -0.010928 | 1.8606e-05 | 7.0721e-06 | 0.066498 | 0.066498 | 0.066498 | 0.97509 | -0.17474 | 0.97466 | -0.17782 | 24.6289
51 | 0.032302 | 0.008108 | -0.032287 | -0.0081023 | 1.5061e-05 | 5.6663e-06 | 0.049034 | 0.049034 | 0.049034 | 0.98033 | -0.13749 | 0.97985 | -0.14085 | 18.1609
52 | -0.13108 | -0.033061 | 0.13138 | 0.033174 | 0.0002969 | 0.00011277 | 0.1971 | 0.1971 | 0.1971 | 0.98996 | -0.069573 | 0.99228 | -0.053455 | 24.3335
53 | 0.0054667 | 0.0013699 | -0.005466 | -0.0013698 | 7.5631e-07 | 6.5092e-08 | 0.0082618 | 0.0082619 | 0.0082619 | 0.98459 | -0.10747 | 0.98445 | -0.10847 | 3.06
54 | -0.032549 | -0.008166 | 0.032578 | 0.0081771 | 2.9484e-05 | 1.1102e-05 | 0.049742 | 0.049742 | 0.049742 | 0.97375 | -0.18434 | 0.97466 | -0.17782 | 18.4228
55 | 0.010976 | 0.0027507 | -0.010972 | -0.0027496 | 3.4159e-06 | 1.0709e-06 | 0.016757 | 0.016757 | 0.016757 | 0.97466 | -0.17782 | 0.97435 | -0.18006 | 6.2062
56 | 0.0083242 | 0.0020859 | -0.0083217 | -0.0020853 | 2.5083e-06 | 6.5504e-07 | 0.012713 | 0.012713 | 0.012713 | 0.97435 | -0.18006 | 0.97405 | -0.18224 | 4.7084
57 | 0.010128 | 0.0025376 | -0.010125 | -0.0025367 | 3.0232e-06 | 9.1041e-07 | 0.015464 | 0.015464 | 0.015464 | 0.97454 | -0.17873 | 0.97424 | -0.18089 | 5.7275
58 | 0.0061952 | 0.0015523 | -0.0061942 | -0.0015521 | 9.7796e-07 | 1.5838e-07 | 0.009464 | 0.0094641 | 0.0094641 | 0.97405 | -0.18224 | 0.97389 | -0.18338 | 3.5052
59 | 0.029676 | 0.0074481 | -0.029649 | -0.0074379 | 2.7105e-05 | 1.0156e-05 | 0.04507 | 0.045071 | 0.045071 | 0.97985 | -0.14085 | 0.97893 | -0.14743 | 16.6928
60 | -0.1352 | -0.034133 | 0.13536 | 0.034192 | 0.00015716 | 5.9733e-05 | 0.20284 | 0.20284 | 0.20284 | 0.99228 | -0.053455 | 0.99347 | -0.04519 | 25.0419
61 | -0.0020532 | -0.00051457 | 0.0020535 | 0.00051408 | 3.0103e-07 | -4.9344e-07 | 0.0031382 | 0.003138 | 0.0031382 | 0.97353 | -0.18595 | 0.97368 | -0.18489 | 1.1623
62 | -0.004513 | -0.0011305 | 0.0045138 | 0.0011305 | 7.5133e-07 | -2.5933e-08 | 0.0068968 | 0.0068966 | 0.0068968 | 0.97368 | -0.18489 | 0.97385 | -0.18368 | 2.5544
63 | -0.0061264 | -0.0015346 | 0.0061273 | 0.0015348 | 9.0263e-07 | 1.4173e-07 | 0.0093607 | 0.0093606 | 0.0093607 | 0.97385 | -0.18368 | 0.97399 | -0.18262 | 3.4669
64 | -0.0077397 | -0.0019389 | 0.0077415 | 0.0019393 | 1.8499e-06 | 4.4751e-07 | 0.011824 | 0.011824 | 0.011824 | 0.97399 | -0.18262 | 0.97424 | -0.18089 | 4.3792
65 | -0.003001 | -0.00075213 | 0.0030013 | 0.00075194 | 3.3318e-07 | -1.8775e-07 | 0.0045858 | 0.0045857 | 0.0045858 | 0.97378 | -0.18419 | 0.97389 | -0.18338 | 1.6985
66 | 0.027587 | 0.006921 | -0.027562 | -0.0069119 | 2.4347e-05 | 9.0856e-06 | 0.041935 | 0.041935 | 0.041935 | 0.97893 | -0.14743 | 0.97804 | -0.1538 | 15.5316
67 | 0.025293 | 0.0063432 | -0.025268 | -0.0063339 | 2.5092e-05 | 9.3104e-06 | 0.038483 | 0.038483 | 0.038483 | 0.97804 | -0.1538 | 0.97704 | -0.16096 | 14.253
68 | 0.022738 | 0.0056998 | -0.022727 | -0.005696 | 1.0292e-05 | 3.7863e-06 | 0.03463 | 0.03463 | 0.03463 | 0.97704 | -0.16096 | 0.97658 | -0.16423 | 12.8258
69 | 0.011583 | 0.0029025 | -0.011576 | -0.0029001 | 7.6024e-06 | 2.4349e-06 | 0.017649 | 0.017649 | 0.017649 | 0.97658 | -0.16423 | 0.97592 | -0.16898 | 6.5367
70 | 0.011144 | 0.0027934 | -0.011138 | -0.0027915 | 6.2335e-06 | 1.9643e-06 | 0.016981 | 0.016981 | 0.016981 | 0.97658 | -0.16423 | 0.97602 | -0.16827 | 6.2892
71 | 0.0037473 | 0.00093871 | -0.0037464 | -0.00093893 | 9.4538e-07 | -2.1613e-07 | 0.0057135 | 0.0057137 | 0.0057137 | 0.97592 | -0.16898 | 0.97567 | -0.1708 | 2.1162
72 | 0.0078282 | 0.0019614 | -0.0078205 | -0.0019595 | 7.6604e-06 | 1.8707e-06 | 0.011936 | 0.011936 | 0.011936 | 0.97592 | -0.16898 | 0.97494 | -0.17605 | 4.4208
73 | 0.0095022 | 0.0023815 | -0.0095003 | -0.0023809 | 1.896e-06 | 5.4831e-07 | 0.014487 | 0.014487 | 0.014487 | 0.97602 | -0.16827 | 0.97582 | -0.16971 | 5.3655
74 | 0.0068582 | 0.0017183 | -0.0068521 | -0.0017171 | 6.09e-06 | 1.2326e-06 | 0.010467 | 0.010468 | 0.010468 | 0.97494 | -0.17605 | 0.97404 | -0.18247 | 3.8769
75 | 0.0088468 | 0.0022172 | -0.0088422 | -0.0022159 | 4.6675e-06 | 1.282e-06 | 0.01349 | 0.013491 | 0.013491 | 0.97582 | -0.16971 | 0.97529 | -0.17353 | 4.9965
76 | 0.0068521 | 0.0017171 | -0.0068505 | -0.0017168 | 1.5742e-06 | 3.1896e-07 | 0.010468 | 0.010468 | 0.010468 | 0.97404 | -0.18247 | 0.97381 | -0.18413 | 3.8769
77 | 0.0072997 | 0.0018293 | -0.007298 | -0.0018289 | 1.674e-06 | 3.7403e-07 | 0.011137 | 0.011137 | 0.011137 | 0.97529 | -0.17353 | 0.97506 | -0.17518 | 4.1249
78 | 0.0056635 | 0.0014193 | -0.0056625 | -0.0014192 | 9.8021e-07 | 1.1476e-07 | 0.0086429 | 0.008643 | 0.008643 | 0.97506 | -0.17518 | 0.97488 | -0.17643 | 3.2011
79 | 0.039337 | 0.009903 | -0.039255 | -0.0098721 | 8.1648e-05 | 3.0916e-05 | 0.058934 | 0.058934 | 0.058934 | 0.99347 | -0.04519 | 0.99134 | -0.060081 | 21.8275
80 | -0.1747 | -0.044095 | 0.1749 | 0.044174 | 0.00020513 | 7.8335e-05 | 0.26177 | 0.26177 | 0.26177 | 0.99347 | -0.04519 | 0.99467 | -0.036839 | 32.3177
81 | 0.037664 | 0.0094734 | -0.03761 | -0.0094529 | 5.4208e-05 | 2.05e-05 | 0.056547 | 0.056547 | 0.056547 | 0.99134 | -0.060081 | 0.98987 | -0.070418 | 20.9433
82 | -0.17654 | -0.044583 | 0.17665 | 0.044626 | 0.0001121 | 4.2815e-05 | 0.26422 | 0.26422 | 0.26422 | 0.99467 | -0.036839 | 0.99532 | -0.032325 | 32.6193
83 | -0.17922 | -0.045271 | 0.1794 | 0.04534 | 0.00018003 | 6.8774e-05 | 0.26807 | 0.26807 | 0.26807 | 0.99532 | -0.032325 | 0.99635 | -0.02519 | 33.0947
84 | 0.017455 | 0.0043758 | -0.017443 | -0.0043716 | 1.1706e-05 | 4.1431e-06 | 0.026068 | 0.026068 | 0.026068 | 0.99635 | -0.02519 | 0.99566 | -0.030034 | 9.6549
85 | -0.19686 | -0.049716 | 0.19693 | 0.049742 | 6.8872e-05 | 2.634e-05 | 0.29413 | 0.29413 | 0.29413 | 0.99635 | -0.02519 | 0.99671 | -0.022702 | 36.3129
86 | 0.015111 | 0.0037873 | -0.01511 | -0.0037867 | 1.8103e-06 | 6.2231e-07 | 0.022584 | 0.022584 | 0.022584 | 0.99566 | -0.030034 | 0.99554 | -0.0309 | 8.3644
87 | -0.19873 | -0.050194 | 0.1991 | 0.050334 | 0.00036688 | 0.00014032 | 0.29683 | 0.29683 | 0.29683 | 0.99671 | -0.022702 | 0.99861 | -0.0095975 | 36.6451
88 | 0.012753 | 0.0031962 | -0.01275 | -0.003195 | 3.6837e-06 | 1.2056e-06 | 0.019062 | 0.019062 | 0.019062 | 0.99554 | -0.0309 | 0.99524 | -0.032987 | 7.0601
89 | -0.23196 | -0.058577 | 0.23227 | 0.058697 | 0.00031337 | 0.00012003 | 0.34579 | 0.34579 | 0.34579 | 0.99861 | -0.0095975 | 1 | 0 | 42.6904
90 | 0.03286 | 0.0082431 | -0.032844 | -0.0082381 | 1.6491e-05 | 5.0457e-06 | 0.048967 | 0.048968 | 0.048968 | 0.99861 | -0.0095975 | 0.99809 | -0.013217 | 6.0454
91 | 0.03548 | 0.0089192 | -0.03545 | -0.0089077 | 3.0454e-05 | 1.1493e-05 | 0.053345 | 0.053345 | 0.053345 | 0.98987 | -0.070418 | 0.98899 | -0.076586 | 19.7576
92 | 0.010251 | 0.0025687 | -0.01025 | -0.0025683 | 1.3459e-06 | 3.9834e-07 | 0.015326 | 0.015327 | 0.015327 | 0.99524 | -0.032987 | 0.99511 | -0.033935 | 5.6765
93 | 0.0098762 | 0.0024747 | -0.0098731 | -0.0024738 | 3.1322e-06 | 8.9987e-07 | 0.014696 | 0.014696 | 0.014696 | 1 | 0 | 0.99967 | -0.0022924 | 5.4429
94 | 0.031544 | 0.0079123 | -0.031541 | -0.0079115 | 2.5175e-06 | 7.5372e-07 | 0.04703 | 0.04703 | 0.04703 | 0.99809 | -0.013217 | 0.99801 | -0.013793 | 5.8061
95 | -0.003789 | -0.00094958 | 0.0037893 | 0.00094949 | 3.6915e-07 | -9.6905e-08 | 0.0056691 | 0.005669 | 0.0056691 | 0.99453 | -0.038008 | 0.99463 | -0.037304 | 2.0997
96 | 0.001676 | 0.00042003 | -0.001676 | -0.00042005 | 7.3439e-09 | -2.146e-08 | 0.0025077 | 0.0025077 | 0.0025077 | 0.99453 | -0.038008 | 0.99452 | -0.03804 | 0.92878
97 | -0.0051729 | -0.0012962 | 0.0051737 | 0.0012963 | 8.5588e-07 | 3.1884e-08 | 0.0077388 | 0.0077387 | 0.0077388 | 0.99463 | -0.037304 | 0.9948 | -0.036109 | 2.8662
98 | -0.006083 | -0.0015242 | 0.0060831 | 0.0015242 | 4.2749e-08 | 5.6982e-09 | 0.0090988 | 0.0090988 | 0.0090988 | 0.9948 | -0.036109 | 0.99481 | -0.036058 | 3.3699
99 | -0.0065958 | -0.0016527 | 0.0065963 | 0.0016528 | 5.7859e-07 | 9.8839e-08 | 0.0098657 | 0.0098657 | 0.0098657 | 0.99481 | -0.036058 | 0.9949 | -0.035424 | 3.654
100 | -0.0077124 | -0.0019325 | 0.0077134 | 0.0019327 | 1.0272e-06 | 2.344e-07 | 0.011535 | 0.011535 | 0.011535 | 0.9949 | -0.035424 | 0.99503 | -0.034461 | 4.2722
101 | 0.029605 | 0.0074262 | -0.029596 | -0.0074238 | 8.3959e-06 | 2.4174e-06 | 0.044143 | 0.044143 | 0.044143 | 0.99801 | -0.013793 | 0.99772 | -0.015838 | 5.4497
102 | 0.018652 | 0.0046811 | -0.01865 | -0.0046809 | 1.6886e-06 | 2.3856e-07 | 0.02782 | 0.027821 | 0.027821 | 0.99772 | -0.015838 | 0.99762 | -0.01649 | 3.4346
103 | 0.010944 | 0.0027427 | -0.01094 | -0.0027414 | 4.2887e-06 | 1.3128e-06 | 0.016322 | 0.016323 | 0.016323 | 0.99772 | -0.015838 | 0.99731 | -0.01867 | 6.0454
104 | 0.0094524 | 0.0023686 | -0.0094518 | -0.0023684 | 6.565e-07 | 1.8348e-07 | 0.014103 | 0.014103 | 0.014103 | 0.99731 | -0.01867 | 0.99724 | -0.019172 | 5.2234
105 | 0.0057212 | 0.0014334 | -0.0057199 | -0.0014333 | 1.2591e-06 | 1.231e-07 | 0.0085366 | 0.0085367 | 0.0085367 | 0.99724 | -0.019172 | 0.99702 | -0.020763 | 3.1617
106 | 0.0081155 | 0.0020333 | -0.0081151 | -0.0020332 | 4.2245e-07 | 1.0166e-07 | 0.01208 | 0.01208 | 0.01208 | 0.99967 | -0.0022924 | 0.99962 | -0.0026686 | 4.474
107 | 0.0034342 | 0.00086041 | -0.0034342 | -0.00086042 | 2.0761e-08 | -8.5321e-09 | 0.0051253 | 0.0051253 | 0.0051253 | 0.99702 | -0.020763 | 0.99701 | -0.020806 | 1.8983
108 | -0.0085058 | -0.0021313 | 0.0085064 | 0.0021314 | 6.1919e-07 | 1.5848e-07 | 0.01272 | 0.01272 | 0.01272 | 0.99503 | -0.034461 | 0.99511 | -0.033935 | 4.711
109 | 0.00032284 | 7.9584e-05 | -0.00032282 | -8.0907e-05 | 1.564e-08 | -1.3234e-06 | 0.00048844 | 0.00048891 | 0.00048891 | 0.98259 | -0.12253 | 0.98254 | -0.12288 | 0.18108
110 | -0.00043069 | -0.00010661 | 0.0004307 | 0.00010613 | 1.0133e-08 | -4.8044e-07 | 0.00065176 | 0.00065159 | 0.00065176 | 0.98259 | -0.12253 | 0.98261 | -0.12235 | 0.24139
111 | -0.01577 | -0.0039546 | 0.015776 | 0.0039566 | 5.9219e-06 | 2.0668e-06 | 0.023882 | 0.023882 | 0.023882 | 0.98261 | -0.12235 | 0.98299 | -0.11964 | 8.8451
112 | 0.015339 | 0.0038484 | -0.015329 | -0.003845 | 1.0031e-05 | 3.481e-06 | 0.02323 | 0.02323 | 0.02323 | 0.98261 | -0.12235 | 0.98195 | -0.12707 | 8.6038
113 | -0.016593 | -0.0041615 | 0.016599 | 0.0041635 | 5.523e-06 | 1.9463e-06 | 0.025119 | 0.025119 | 0.025119 | 0.98299 | -0.11964 | 0.98333 | -0.11724 | 9.3034
114 | 0.015092 | 0.0037855 | -0.015073 | -0.0037791 | 1.8496e-05 | 6.398e-06 | 0.022871 | 0.022871 | 0.022871 | 0.98195 | -0.12707 | 0.98071 | -0.13592 | 8.4708
115 | 0.0016767 | 0.00041828 | -0.0016763 | -0.00041925 | 3.5318e-07 | -9.6778e-07 | 0.0025434 | 0.0025437 | 0.0025437 | 0.98071 | -0.13592 | 0.98049 | -0.13745 | 0.94213
116 | -0.00018852 | -4.7248e-05 | 0.00018853 | 4.6367e-05 | 3.5712e-09 | -8.8136e-07 | 0.00028611 | 0.0002858 | 0.00028611 | 0.98047 | -0.13759 | 0.98049 | -0.13745 | 0.10597
117 | 0.0021665 | 0.0005427 | -0.0021663 | -0.00054293 | 1.4219e-07 | -2.2953e-07 | 0.0032333 | 0.0032334 | 0.0032334 | 0.99701 | -0.020806 | 0.99694 | -0.021281 | 1.1976
118 | 0.0027629 | 0.00069191 | -0.0027626 | -0.00069213 | 2.568e-07 | -2.1991e-07 | 0.0041134 | 0.0041135 | 0.0041135 | 0.99942 | -0.0040391 | 0.99933 | -0.0047112 | 1.5235
119 | -0.0050075 | -0.0012545 | 0.0050076 | 0.0012545 | 1.1639e-07 | 7.8872e-10 | 0.0074553 | 0.0074553 | 0.0074553 | 0.99942 | -0.0040391 | 0.99945 | -0.003871 | 2.7612
120 | 0.00093564 | 0.00023424 | -0.00093562 | -0.00023449 | 2.3582e-08 | -2.4604e-07 | 0.0013931 | 0.0013932 | 0.0013932 | 0.99933 | -0.0047112 | 0.9993 | -0.0048935 | 0.51599
121 | -0.006558 | -0.001643 | 0.0065591 | 0.0016432 | 1.0909e-06 | 1.792e-07 | 0.0097636 | 0.0097635 | 0.0097636 | 0.99945 | -0.003871 | 0.99962 | -0.0026686 | 3.6161
122 | -0.029084 | -0.0073062 | 0.029107 | 0.0073147 | 2.2775e-05 | 8.5166e-06 | 0.043837 | 0.043837 | 0.043837 | 0.98736 | -0.088065 | 0.98816 | -0.08244 | 16.236
123 | 0.032998 | 0.0082932 | -0.032987 | -0.0082892 | 1.0583e-05 | 3.982e-06 | 0.049656 | 0.049656 | 0.049656 | 0.98899 | -0.076586 | 0.98866 | -0.07889 | 18.3912
124 | 0.031003 | 0.0077919 | -0.030988 | -0.0077861 | 1.5312e-05 | 5.7449e-06 | 0.04667 | 0.04667 | 0.04667 | 0.98866 | -0.07889 | 0.98816 | -0.08244 | 17.2851
125 | 0.0024001 | 0.00060144 | -0.0024 | -0.0006015 | 5.2061e-08 | -6.0577e-08 | 0.0036277 | 0.0036278 | 0.0036278 | 0.98445 | -0.10847 | 0.98443 | -0.10863 | 1.3436
126 | -0.0057588 | -0.0014433 | 0.0057598 | 0.0014434 | 9.6282e-07 | 1.2253e-07 | 0.0088011 | 0.008801 | 0.0088011 | 0.97364 | -0.18534 | 0.97381 | -0.18413 | 3.2597

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24531 | 0.061764

## res_load
| p_mw | q_mvar
0 | 0.0008584 | 0.00021514
1 | 0.0023797 | 0.00059642
2 | 0.0090622 | 0.0022712
3 | 0.0014291 | 0.00035815
4 | 0.0010299 | 0.00025812
5 | 0.0015752 | 0.00039478
6 | 0.0014799 | 0.00037089
7 | 0.0024457 | 0.00061295
8 | 0.0026146 | 0.00065529
9 | 0.0025955 | 0.0006505
10 | 0.001841 | 0.00046141
11 | 0.0022845 | 0.00057256
12 | 0.0031955 | 0.00080087
13 | 0.0025694 | 0.00064394
14 | 0.0067012 | 0.0016795
15 | 0.0026712 | 0.00066945
16 | 0.0055539 | 0.0013919
17 | 0.002172 | 0.00054435
18 | 0.0024573 | 0.00061586
19 | 0.002482 | 0.00062206
20 | 0.0036808 | 0.00092249
21 | 0.011493 | 0.0028804
22 | 0.0061438 | 0.0015398
23 | 0.0046239 | 0.0011589
24 | 0.0025408 | 0.00063678
25 | 0.0015117 | 0.00037887
26 | 0.0030347 | 0.00076056
27 | 0.0018537 | 0.00046457
28 | 0.003119 | 0.0007817
29 | 0.0025375 | 0.00063597
30 | 0.0017048 | 0.00042728
31 | 0.003173 | 0.00079523
32 | 0.0024923 | 0.00062462
33 | 0.0043122 | 0.0010807
34 | 0.0026481 | 0.00066368
35 | 0.0019869 | 0.00049797
36 | 0.0021265 | 0.00053295
37 | 0.0026102 | 0.00065419
38 | 0.0038268 | 0.00095908
39 | 0.0020532 | 0.00051457
40 | 0.0024596 | 0.00061642
41 | 0.0016126 | 0.00040416
42 | 0.0016124 | 0.00040411
43 | 0.0023835 | 0.00059736
44 | 0.003001 | 0.00075213
45 | 0.0031929 | 0.00080021
46 | 0.0020626 | 0.00051694
47 | 0.0022693 | 0.00056873
48 | 0.0025302 | 0.00063412
49 | 0.0016359 | 0.00040999
50 | 0.0037464 | 0.00093893
51 | 0.00096238 | 0.0002412
52 | 0.00065343 | 0.00016376
53 | 0.0015425 | 0.00038658
54 | 0.0016345 | 0.00040966
55 | 0.0056625 | 0.0014192
56 | 0.0015907 | 0.00039867
57 | 0.0016334 | 0.00040936
58 | 0.0025755 | 0.00064547
59 | 0.0023315 | 0.00058432
60 | 0.0018024 | 0.00045172
61 | 0.0023562 | 0.00059051
62 | 0.0021297 | 0.00053374
63 | 0.0024987 | 0.00062623
64 | 0.0023626 | 0.00059212
65 | 0.0013 | 0.0003258
66 | 0.0021129 | 0.00052955
67 | 0.0013835 | 0.00034674
68 | 0.001676 | 0.00042005
69 | 0.00090932 | 0.0002279
70 | 0.00051269 | 0.00012849
71 | 0.0011161 | 0.00027971
72 | 0.0019364 | 0.0004853
73 | 0.0014875 | 0.00037281
74 | 0.0037306 | 0.00093498
75 | 0.0017576 | 0.0004405
76 | 0.0022857 | 0.00057286
77 | 0.00079232 | 0.00019857
78 | 0.0017433 | 0.00043691
79 | 0.00010785 | 2.703e-05
80 | 0.00032282 | 8.0907e-05
81 | 0.00081744 | 0.00020487
82 | 0.00023724 | 5.9459e-05
83 | 0.00038334 | 9.6074e-05
84 | 0.00018852 | 4.7248e-05
85 | 0.0014878 | 0.00037288
86 | 0.0012677 | 0.00031772
87 | 0.0021663 | 0.00054293
88 | 0.0022446 | 0.00056254
89 | 0.001827 | 0.00045789
90 | 0.0015504 | 0.00038857
91 | 0.00093562 | 0.00023449
92 | 0.001556 | 0.00038997
93 | 0.0027201 | 0.00068172
94 | 0.0024519 | 0.00061451
95 | 0.0019844 | 0.00049734
96 | 0.0018811 | 0.00047146
97 | 0.0030659 | 0.00076839
98 | 0.0024 | 0.0006015
99 | 0.0057588 | 0.0014433
100 | 0.0010907 | 0.00027337

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1