## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2016-1_1_2_node_31 | 0.4 | n |  | TRUE
1 | bus_LV_2016-1_1_2_node_32 | 0.4 | n |  | TRUE
2 | bus_LV_2016-1_1_2_node_33 | 0.4 | n |  | TRUE
3 | bus_LV_2016-1_1_2_node_34 | 0.4 | n |  | TRUE
4 | bus_LV_2016-1_1_2_node_36 | 0.4 | n |  | TRUE
5 | bus_LV_2016-1_1_2_node_37 | 0.4 | n |  | TRUE
6 | bus_LV_2016-1_1_2_node_38 | 0.4 | n |  | TRUE
7 | bus_LV_2016-1_1_2_node_39 | 0.4 | n |  | TRUE
8 | bus_LV_2016-1_1_2_node_40 | 0.4 | n |  | TRUE
9 | bus_LV_2016-1_1_2_node_43 | 0.4 | n |  | TRUE
10 | bus_LV_2016-1_1_2_node_41 | 0.4 | n |  | TRUE
11 | bus_LV_2016-1_1_2_node_42 | 0.4 | n |  | TRUE
12 | bus_LV_2016-1_1_2_node_44 | 0.4 | n |  | TRUE
13 | bus_LV_2016-1_1_2_node_45 | 0.4 | n |  | TRUE
14 | bus_LV_2016-1_1_2_node_46 | 0.4 | n |  | TRUE
15 | bus_LV_2016-1_1_2_node_47 | 0.4 | n |  | TRUE
16 | bus_LV_2016-1_1_2_node_48 | 0.4 | n |  | TRUE
17 | bus_LV_2016-1_1_2_node_49 | 0.4 | n |  | TRUE
18 | bus_LV_2016-1_1_2_node_51 | 0.4 | n |  | TRUE
19 | bus_LV_2016-1_1_2_node_50 | 0.4 | n |  | TRUE
20 | bus_LV_2016-1_1_2_node_52 | 0.4 | n |  | TRUE
21 | bus_LV_2016-1_1_2_node_53 | 0.4 | n |  | TRUE
22 | bus_LV_2016-1_1_2_node_57 | 0.4 | n |  | TRUE
23 | bus_LV_2016-1_1_2_node_58 | 0.4 | n |  | TRUE
24 | bus_LV_2016-1_1_2_node_54 | 0.4 | n |  | TRUE
25 | bus_LV_2016-1_1_2_node_55 | 0.4 | n |  | TRUE
26 | bus_LV_2016-1_1_2_node_56 | 0.4 | n |  | TRUE
27 | bus_LV_2016-1_1_2_node_59 | 0.4 | n |  | TRUE
28 | bus_MV_477_0_node_2 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2016-1_1_2_load_31 | 0 | 0.015011 | 0.0037621 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2016-1_1_2_load_32 | 1 | 0.014733 | 0.0036925 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2016-1_1_2_load_36 | 4 | 0.0067072 | 0.001681 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2016-1_1_2_load_37 | 5 | 0.0023909 | 0.00059921 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2016-1_1_2_load_40 | 8 | 0.0079817 | 0.0020004 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2016-1_1_2_load_43 | 9 | 0.0025812 | 0.0006469 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2016-1_1_2_load_41 | 10 | 0.0021705 | 0.00054397 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2016-1_1_2_load_42 | 11 | 0.0020679 | 0.00051827 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2016-1_1_2_load_44 | 12 | 0.0030893 | 0.00077426 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2016-1_1_2_load_45 | 13 | 0.0071331 | 0.0017877 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2016-1_1_2_load_46 | 14 | 0.0028162 | 0.00070581 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2016-1_1_2_load_47 | 15 | 0.0031797 | 0.00079692 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2016-1_1_2_load_48 | 16 | 0.00059981 | 0.00015033 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2016-1_1_2_load_51 | 18 | 0.0012595 | 0.00031566 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2016-1_1_2_load_50 | 19 | 0.0084503 | 0.0021178 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2016-1_1_2_load_52 | 20 | 0.001456 | 0.00036491 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2016-1_1_2_load_53 | 21 | 0.0016206 | 0.00040616 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2016-1_1_2_load_57 | 22 | 0.00079724 | 0.00019981 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2016-1_1_2_load_58 | 23 | 0.002129 | 0.00053358 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2016-1_1_2_load_54 | 24 | 0.0013255 | 0.0003322 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2016-1_1_2_load_55 | 25 | 0.00116 | 0.00029072 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2016-1_1_2_load_56 | 26 | 0.00081683 | 0.00020472 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2016-1_1_2_load_59 | 27 | 0.0038745 | 0.00097104 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2016-1_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2016-1_1_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.024792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2016-1_1_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.057756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2016-1_1_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.03766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2016-1_1_2_line_4 | NAYY 4x150 SE | 4 | 5 | 0.020292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2016-1_1_2_line_5 | NAYY 4x150 SE | 5 | 6 | 0.016867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2016-1_1_2_line_6 | NAYY 4x150 SE | 6 | 7 | 0.016142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2016-1_1_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.033604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2016-1_1_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.001884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2016-1_1_2_line_9 | NAYY 4x150 SE | 7 | 10 | 0.023733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2016-1_1_2_line_10 | NAYY 4x150 SE | 9 | 12 | 0.031095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2016-1_1_2_line_11 | NAYY 4x150 SE | 10 | 11 | 0.0098718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2016-1_1_2_line_12 | NAYY 4x150 SE | 12 | 13 | 0.00048293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2016-1_1_2_line_13 | NAYY 4x150 SE | 13 | 14 | 0.024392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2016-1_1_2_line_14 | NAYY 4x150 SE | 14 | 15 | 0.020355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2016-1_1_2_line_15 | NAYY 4x150 SE | 15 | 16 | 0.030972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2016-1_1_2_line_16 | NAYY 4x150 SE | 16 | 17 | 0.003783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2016-1_1_2_line_17 | NAYY 4x150 SE | 17 | 18 | 0.010219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2016-1_1_2_line_18 | NAYY 4x150 SE | 17 | 19 | 0.024837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2016-1_1_2_line_19 | NAYY 4x150 SE | 18 | 20 | 0.042468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2016-1_1_2_line_20 | NAYY 4x150 SE | 20 | 21 | 0.024068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2016-1_1_2_line_21 | NAYY 4x150 SE | 20 | 22 | 0.056023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2016-1_1_2_line_22 | NAYY 4x150 SE | 21 | 23 | 0.0045841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2016-1_1_2_line_23 | NAYY 4x150 SE | 22 | 26 | 0.023657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2016-1_1_2_line_24 | NAYY 4x150 SE | 23 | 27 | 0.027015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2016-1_1_2_line_25 | NAYY 4x150 SE | 24 | 25 | 0.024347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2016-1_1_2_line_26 | NAYY 4x150 SE | 24 | 26 | 0.034359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2016-1_1_2_trafo_43 | 0.25 MVA 20/0.4 kV | 28 | 9 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2560569.2241 | 1183683.9773 | 2560559.8981 | 1183659.0592 | 2560546.1864 | 1183645.7715
1 | 2560576.8749 | 1183707.5399 | 2560573.0385 | 1183694.1691 | 2560569.2241 | 1183683.9773
2 | 2560520.9114 | 1183722.4395 | 2560576.8749 | 1183707.5399
3 | 2560520.9114 | 1183722.4395 | 2560492.5822 | 1183697.6248
4 | 2560492.5822 | 1183697.6248 | 2560477.3177 | 1183684.2541
5 | 2560464.6302 | 1183673.1406 | 2560477.3177 | 1183684.2541
6 | 2560452.445 | 1183662.5155 | 2560464.6302 | 1183673.1406
7 | 2560486.2694 | 1183647.3837 | 2560464.6302 | 1183673.1406
8 | 2560452.445 | 1183662.5155 | 2560450.9698 | 1183661.3437
9 | 2560452.445 | 1183662.5155 | 2560437.9267 | 1183681.2899
10 | 2560426.6217 | 1183642.0027 | 2560450.9698 | 1183661.3437
11 | 2560431.8878 | 1183689.0991 | 2560437.9267 | 1183681.2899
12 | 2560426.6217 | 1183642.0027 | 2560426.2435 | 1183641.7023
13 | 2560407.1445 | 1183626.5309 | 2560426.2435 | 1183641.7023
14 | 2560407.1445 | 1183626.5309 | 2560391.2059 | 1183613.87
15 | 2560391.2059 | 1183613.87 | 2560366.9542 | 1183594.6057
16 | 2560363.992 | 1183592.2527 | 2560366.9542 | 1183594.6057
17 | 2560363.992 | 1183592.2527 | 2560355.9895 | 1183585.8969
18 | 2560363.992 | 1183592.2527 | 2560348.1093 | 1183611.3481
19 | 2560355.9895 | 1183585.8969 | 2560322.7337 | 1183559.4844
20 | 2560322.7337 | 1183559.4844 | 2560303.8863 | 1183544.5155
21 | 2560322.7337 | 1183559.4844 | 2560353.3937 | 1183512.5961
22 | 2560300.2967 | 1183541.6645 | 2560303.8863 | 1183544.5155
23 | 2560371.8537 | 1183527.3905 | 2560353.3937 | 1183512.5961
24 | 2560300.2967 | 1183541.6645 | 2560293.9327 | 1183536.61 | 2560280.8231 | 1183523.0129
25 | 2560400.195 | 1183546.6661 | 2560417.6005 | 1183552.4539 | 2560423.4433 | 1183553.8376
26 | 2560400.195 | 1183546.6661 | 2560400.195 | 1183546.6661 | 2560383.7096 | 1183536.8923 | 2560371.8537 | 1183527.3905

## bus_geodata
| x | y | coords
0 | 2560569.2241 | 1183683.9773
1 | 2560546.1864 | 1183645.7715
2 | 2560576.8749 | 1183707.5399
3 | 2560520.9114 | 1183722.4395
4 | 2560492.5822 | 1183697.6248
5 | 2560477.3177 | 1183684.2541
6 | 2560464.6302 | 1183673.1406
7 | 2560452.445 | 1183662.5155
8 | 2560486.2694 | 1183647.3837
9 | 2560450.9698 | 1183661.3437
10 | 2560437.9267 | 1183681.2899
11 | 2560431.8878 | 1183689.0991
12 | 2560426.6217 | 1183642.0027
13 | 2560426.2435 | 1183641.7023
14 | 2560407.1445 | 1183626.5309
15 | 2560391.2059 | 1183613.87
16 | 2560366.9542 | 1183594.6057
17 | 2560363.992 | 1183592.2527
18 | 2560355.9895 | 1183585.8969
19 | 2560348.1093 | 1183611.3481
20 | 2560322.7337 | 1183559.4844
21 | 2560303.8863 | 1183544.5155
22 | 2560353.3937 | 1183512.5961
23 | 2560300.2967 | 1183541.6645
24 | 2560400.195 | 1183546.666
25 | 2560423.4433 | 1183553.8376
26 | 2560371.8537 | 1183527.3905
27 | 2560280.8231 | 1183523.0129
28 | 2560452.445 | 1183662.5155

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99163 | -0.058622 | 0.015011 | 0.0037621
1 | 0.99066 | -0.065464 | 0.014733 | 0.0036925
2 | 0.99269 | -0.051145 | 0 | 0
3 | 0.99516 | -0.033784 | 0 | 0
4 | 0.99677 | -0.022508 | 0.0067072 | 0.001681
5 | 0.99784 | -0.015082 | 0.0023909 | 0.00059921
6 | 0.99878 | -0.0085183 | 0 | 0
7 | 0.99986 | -0.00096079 | 0 | 0
8 | 0.99839 | -0.011203 | 0.0079817 | 0.0020004
9 | 1 | 0 | -0.092033 | -0.022919
10 | 0.99972 | -0.0019656 | 0.0021705 | 0.00054397
11 | 0.99969 | -0.0021696 | 0.0020679 | 0.00051827
12 | 0.99823 | -0.012356 | 0.0030893 | 0.00077426
13 | 0.99821 | -0.012533 | 0.0071331 | 0.0017877
14 | 0.99718 | -0.019752 | 0.0028162 | 0.00070581
15 | 0.9964 | -0.025211 | 0.0031797 | 0.00079692
16 | 0.99536 | -0.032541 | 0.00059981 | 0.00015033
17 | 0.99523 | -0.033414 | 0 | 0
18 | 0.99502 | -0.034904 | 0.0012595 | 0.00031566
19 | 0.99493 | -0.03553 | 0.0084503 | 0.0021178
20 | 0.99422 | -0.040559 | 0.001456 | 0.00036491
21 | 0.99395 | -0.042414 | 0.0016206 | 0.00040616
22 | 0.99389 | -0.042885 | 0.00079724 | 0.00019981
23 | 0.99392 | -0.042692 | 0.002129 | 0.00053358
24 | 0.99365 | -0.044541 | 0.0013255 | 0.0003322
25 | 0.99361 | -0.044826 | 0.00116 | 0.00029072
26 | 0.99378 | -0.043676 | 0.00081683 | 0.00020472
27 | 0.99376 | -0.04375 | 0.0038745 | 0.00097104
28 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.014747 | 0.0036972 | -0.014733 | -0.0036925 | 1.3965e-05 | 4.7822e-06 | 0.022129 | 0.02213 | 0.02213 | 0.99163 | -0.058622 | 0.99066 | -0.065464 | 8.1962
1 | -0.029758 | -0.0074594 | 0.029789 | 0.0074709 | 3.0849e-05 | 1.1545e-05 | 0.044655 | 0.044654 | 0.044655 | 0.99163 | -0.058622 | 0.99269 | -0.051145 | 16.5387
2 | -0.029789 | -0.0074709 | 0.029861 | 0.0074978 | 7.1864e-05 | 2.6891e-05 | 0.044654 | 0.044654 | 0.044654 | 0.99269 | -0.051145 | 0.99516 | -0.033784 | 16.5387
3 | -0.029861 | -0.0074978 | 0.029908 | 0.0075153 | 4.6859e-05 | 1.7533e-05 | 0.044654 | 0.044654 | 0.044654 | 0.99516 | -0.033784 | 0.99677 | -0.022508 | 16.5386
4 | -0.036615 | -0.0091963 | 0.036653 | 0.0092106 | 3.7841e-05 | 1.429e-05 | 0.054667 | 0.054667 | 0.054667 | 0.99677 | -0.022508 | 0.99784 | -0.015082 | 20.247
5 | -0.039044 | -0.0098098 | 0.039079 | 0.0098233 | 3.5689e-05 | 1.3506e-05 | 0.058232 | 0.058232 | 0.058232 | 0.99784 | -0.015082 | 0.99878 | -0.0085183 | 21.5674
6 | -0.047064 | -0.011824 | 0.047113 | 0.011843 | 4.9536e-05 | 1.8841e-05 | 0.070128 | 0.070128 | 0.070128 | 0.99878 | -0.0085183 | 0.99986 | -0.00096079 | 25.9732
7 | 0.0079846 | 0.0020011 | -0.0079817 | -0.0020004 | 2.9673e-06 | 7.0167e-07 | 0.011896 | 0.011896 | 0.011896 | 0.99878 | -0.0085183 | 0.99839 | -0.011203 | 4.4059
8 | -0.051352 | -0.012905 | 0.051359 | 0.012908 | 6.8687e-06 | 2.6171e-06 | 0.076436 | 0.076436 | 0.076436 | 0.99986 | -0.00096079 | 1 | 0 | 28.3097
9 | 0.004239 | 0.001062 | -0.0042384 | -0.0010621 | 5.8939e-07 | -8.4544e-08 | 0.0063085 | 0.0063086 | 0.0063086 | 0.99986 | -0.00096079 | 0.99972 | -0.0019656 | 2.3365
10 | 0.039874 | 0.010011 | -0.039806 | -0.0099848 | 6.8322e-05 | 2.587e-05 | 0.059339 | 0.059339 | 0.059339 | 1 | 0 | 0.99823 | -0.012356 | 21.9775
11 | 0.002068 | 0.00051817 | -0.0020679 | -0.00051827 | 5.8363e-08 | -1.0699e-07 | 0.003078 | 0.0030781 | 0.0030781 | 0.99972 | -0.0019656 | 0.99969 | -0.0021696 | 1.14
12 | 0.036716 | 0.0092105 | -0.036715 | -0.0092102 | 9.0279e-07 | 3.4092e-07 | 0.054734 | 0.054734 | 0.054734 | 0.99823 | -0.012356 | 0.99821 | -0.012533 | 20.2719
13 | 0.029582 | 0.0074224 | -0.029553 | -0.0074114 | 2.9602e-05 | 1.1067e-05 | 0.044101 | 0.044101 | 0.044101 | 0.99821 | -0.012533 | 0.99718 | -0.019752 | 16.3337
14 | 0.026736 | 0.0067056 | -0.026716 | -0.0066981 | 2.022e-05 | 7.5115e-06 | 0.039899 | 0.039899 | 0.039899 | 0.99718 | -0.019752 | 0.9964 | -0.025211 | 14.7773
15 | 0.023536 | 0.0059011 | -0.023513 | -0.0058924 | 2.3878e-05 | 8.781e-06 | 0.03515 | 0.03515 | 0.03515 | 0.9964 | -0.025211 | 0.99536 | -0.032541 | 13.0186
16 | 0.022913 | 0.005742 | -0.02291 | -0.005741 | 2.7697e-06 | 1.0161e-06 | 0.034253 | 0.034254 | 0.034254 | 0.99536 | -0.032541 | 0.99523 | -0.033414 | 12.6865
17 | 0.014457 | 0.0036225 | -0.014454 | -0.0036215 | 2.9795e-06 | 1.0132e-06 | 0.021615 | 0.021615 | 0.021615 | 0.99523 | -0.033414 | 0.99502 | -0.034904 | 8.0057
18 | 0.0084528 | 0.0021185 | -0.0084503 | -0.0021178 | 2.4755e-06 | 6.2946e-07 | 0.012638 | 0.012638 | 0.012638 | 0.99523 | -0.033414 | 0.99493 | -0.03553 | 4.6808
19 | 0.013195 | 0.0033059 | -0.013184 | -0.0033024 | 1.0318e-05 | 3.4172e-06 | 0.019732 | 0.019732 | 0.019732 | 0.99502 | -0.034904 | 0.99422 | -0.040559 | 7.3082
20 | 0.0076268 | 0.0019111 | -0.0076249 | -0.0019107 | 1.9569e-06 | 4.4062e-07 | 0.011415 | 0.011415 | 0.011415 | 0.99422 | -0.040559 | 0.99395 | -0.042414 | 4.2277
21 | 0.0041015 | 0.0010264 | -0.0041002 | -0.0010266 | 1.3172e-06 | -2.1966e-07 | 0.0061381 | 0.0061384 | 0.0061384 | 0.99422 | -0.040559 | 0.99389 | -0.042885 | 2.2735
22 | 0.0060043 | 0.0015045 | -0.0060041 | -0.0015045 | 2.3112e-07 | 2.9479e-08 | 0.0089887 | 0.0089888 | 0.0089888 | 0.99395 | -0.042414 | 0.99392 | -0.042692 | 3.3292
23 | 0.003303 | 0.00082683 | -0.0033026 | -0.000827 | 3.6095e-07 | -1.6772e-07 | 0.0049448 | 0.0049449 | 0.0049449 | 0.99389 | -0.042885 | 0.99378 | -0.043676 | 1.8314
24 | 0.003875 | 0.0009709 | -0.0038745 | -0.00097104 | 5.6735e-07 | -1.3185e-07 | 0.0058013 | 0.0058015 | 0.0058015 | 0.99392 | -0.042692 | 0.99376 | -0.04375 | 2.1487
25 | 0.00116 | 0.00029042 | -0.00116 | -0.00029072 | 4.5843e-08 | -2.9773e-07 | 0.001737 | 0.0017371 | 0.0017371 | 0.99365 | -0.044541 | 0.99361 | -0.044826 | 0.64339
26 | -0.0024855 | -0.00062261 | 0.0024858 | 0.00062228 | 2.9699e-07 | -3.3088e-07 | 0.003722 | 0.0037218 | 0.003722 | 0.99365 | -0.044541 | 0.99378 | -0.043676 | 1.3785

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.094614 | 0.023566

## res_load
| p_mw | q_mvar
0 | 0.015011 | 0.0037621
1 | 0.014733 | 0.0036925
2 | 0.0067072 | 0.001681
3 | 0.0023909 | 0.00059921
4 | 0.0079817 | 0.0020004
5 | 0.0025812 | 0.0006469
6 | 0.0021705 | 0.00054397
7 | 0.0020679 | 0.00051827
8 | 0.0030893 | 0.00077426
9 | 0.0071331 | 0.0017877
10 | 0.0028162 | 0.00070581
11 | 0.0031797 | 0.00079692
12 | 0.00059981 | 0.00015033
13 | 0.0012595 | 0.00031566
14 | 0.0084503 | 0.0021178
15 | 0.001456 | 0.00036491
16 | 0.0016206 | 0.00040616
17 | 0.00079724 | 0.00019981
18 | 0.002129 | 0.00053358
19 | 0.0013255 | 0.0003322
20 | 0.00116 | 0.00029072
21 | 0.00081683 | 0.00020472
22 | 0.0038745 | 0.00097104

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1