## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2022-6_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2022-6_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2022-6_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2022-6_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2022-6_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2022-6_0_2_node_76 | 0.4 | n |  | TRUE
6 | bus_LV_2022-6_0_2_node_77 | 0.4 | n |  | TRUE
7 | bus_LV_2022-6_0_2_node_67 | 0.4 | n |  | TRUE
8 | bus_LV_2022-6_0_2_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2022-6_0_2_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_2022-6_0_2_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2022-6_0_2_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_2022-6_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2022-6_0_2_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2022-6_0_2_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2022-6_0_2_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2022-6_0_2_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2022-6_0_2_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_2022-6_0_2_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_2022-6_0_2_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2022-6_0_2_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_2022-6_0_2_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_2022-6_0_2_node_27 | 0.4 | n |  | TRUE
23 | bus_LV_2022-6_0_2_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_2022-6_0_2_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_2022-6_0_2_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_2022-6_0_2_node_63 | 0.4 | n |  | TRUE
27 | bus_LV_2022-6_0_2_node_34 | 0.4 | n |  | TRUE
28 | bus_LV_2022-6_0_2_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_2022-6_0_2_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_2022-6_0_2_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_2022-6_0_2_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_2022-6_0_2_node_43 | 0.4 | n |  | TRUE
33 | bus_LV_2022-6_0_2_node_37 | 0.4 | n |  | TRUE
34 | bus_LV_2022-6_0_2_node_40 | 0.4 | n |  | TRUE
35 | bus_LV_2022-6_0_2_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_2022-6_0_2_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_2022-6_0_2_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_2022-6_0_2_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_2022-6_0_2_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_2022-6_0_2_node_49 | 0.4 | n |  | TRUE
41 | bus_LV_2022-6_0_2_node_48 | 0.4 | n |  | TRUE
42 | bus_LV_2022-6_0_2_node_55 | 0.4 | n |  | TRUE
43 | bus_LV_2022-6_0_2_node_58 | 0.4 | n |  | TRUE
44 | bus_LV_2022-6_0_2_node_60 | 0.4 | n |  | TRUE
45 | bus_LV_2022-6_0_2_node_45 | 0.4 | n |  | TRUE
46 | bus_LV_2022-6_0_2_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_2022-6_0_2_node_38 | 0.4 | n |  | TRUE
48 | bus_LV_2022-6_0_2_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_2022-6_0_2_node_64 | 0.4 | n |  | TRUE
50 | bus_LV_2022-6_0_2_node_69 | 0.4 | n |  | TRUE
51 | bus_LV_2022-6_0_2_node_42 | 0.4 | n |  | TRUE
52 | bus_LV_2022-6_0_2_node_65 | 0.4 | n |  | TRUE
53 | bus_LV_2022-6_0_2_node_66 | 0.4 | n |  | TRUE
54 | bus_LV_2022-6_0_2_node_44 | 0.4 | n |  | TRUE
55 | bus_LV_2022-6_0_2_node_46 | 0.4 | n |  | TRUE
56 | bus_LV_2022-6_0_2_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_2022-6_0_2_node_50 | 0.4 | n |  | TRUE
58 | bus_LV_2022-6_0_2_node_51 | 0.4 | n |  | TRUE
59 | bus_LV_2022-6_0_2_node_52 | 0.4 | n |  | TRUE
60 | bus_LV_2022-6_0_2_node_56 | 0.4 | n |  | TRUE
61 | bus_LV_2022-6_0_2_node_57 | 0.4 | n |  | TRUE
62 | bus_LV_2022-6_0_2_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_2022-6_0_2_node_61 | 0.4 | n |  | TRUE
64 | bus_LV_2022-6_0_2_node_72 | 0.4 | n |  | TRUE
65 | bus_LV_2022-6_0_2_node_54 | 0.4 | n |  | TRUE
66 | bus_LV_2022-6_0_2_node_127 | 0.4 | n |  | TRUE
67 | bus_LV_2022-6_0_2_node_129 | 0.4 | n |  | TRUE
68 | bus_LV_2022-6_0_2_node_130 | 0.4 | n |  | TRUE
69 | bus_LV_2022-6_0_2_node_128 | 0.4 | n |  | TRUE
70 | bus_LV_2022-6_0_2_node_62 | 0.4 | n |  | TRUE
71 | bus_LV_2022-6_0_2_node_73 | 0.4 | n |  | TRUE
72 | bus_LV_2022-6_0_2_node_126 | 0.4 | n |  | TRUE
73 | bus_LV_2022-6_0_2_node_131 | 0.4 | n |  | TRUE
74 | bus_LV_2022-6_0_2_node_133 | 0.4 | n |  | TRUE
75 | bus_LV_2022-6_0_2_node_125 | 0.4 | n |  | TRUE
76 | bus_LV_2022-6_0_2_node_111 | 0.4 | n |  | TRUE
77 | bus_LV_2022-6_0_2_node_103 | 0.4 | n |  | TRUE
78 | bus_LV_2022-6_0_2_node_102 | 0.4 | n |  | TRUE
79 | bus_LV_2022-6_0_2_node_68 | 0.4 | n |  | TRUE
80 | bus_LV_2022-6_0_2_node_74 | 0.4 | n |  | TRUE
81 | bus_LV_2022-6_0_2_node_71 | 0.4 | n |  | TRUE
82 | bus_LV_2022-6_0_2_node_70 | 0.4 | n |  | TRUE
83 | bus_LV_2022-6_0_2_node_75 | 0.4 | n |  | TRUE
84 | bus_LV_2022-6_0_2_node_79 | 0.4 | n |  | TRUE
85 | bus_LV_2022-6_0_2_node_80 | 0.4 | n |  | TRUE
86 | bus_LV_2022-6_0_2_node_81 | 0.4 | n |  | TRUE
87 | bus_LV_2022-6_0_2_node_84 | 0.4 | n |  | TRUE
88 | bus_LV_2022-6_0_2_node_89 | 0.4 | n |  | TRUE
89 | bus_LV_2022-6_0_2_node_82 | 0.4 | n |  | TRUE
90 | bus_LV_2022-6_0_2_node_98 | 0.4 | n |  | TRUE
91 | bus_LV_2022-6_0_2_node_83 | 0.4 | n |  | TRUE
92 | bus_LV_2022-6_0_2_node_99 | 0.4 | n |  | TRUE
93 | bus_LV_2022-6_0_2_node_97 | 0.4 | n |  | TRUE
94 | bus_LV_2022-6_0_2_node_90 | 0.4 | n |  | TRUE
95 | bus_LV_2022-6_0_2_node_85 | 0.4 | n |  | TRUE
96 | bus_LV_2022-6_0_2_node_86 | 0.4 | n |  | TRUE
97 | bus_LV_2022-6_0_2_node_87 | 0.4 | n |  | TRUE
98 | bus_LV_2022-6_0_2_node_88 | 0.4 | n |  | TRUE
99 | bus_LV_2022-6_0_2_node_91 | 0.4 | n |  | TRUE
100 | bus_LV_2022-6_0_2_node_93 | 0.4 | n |  | TRUE
101 | bus_LV_2022-6_0_2_node_94 | 0.4 | n |  | TRUE
102 | bus_LV_2022-6_0_2_node_118 | 0.4 | n |  | TRUE
103 | bus_LV_2022-6_0_2_node_115 | 0.4 | n |  | TRUE
104 | bus_LV_2022-6_0_2_node_95 | 0.4 | n |  | TRUE
105 | bus_LV_2022-6_0_2_node_96 | 0.4 | n |  | TRUE
106 | bus_LV_2022-6_0_2_node_101 | 0.4 | n |  | TRUE
107 | bus_LV_2022-6_0_2_node_100 | 0.4 | n |  | TRUE
108 | bus_LV_2022-6_0_2_node_113 | 0.4 | n |  | TRUE
109 | bus_LV_2022-6_0_2_node_112 | 0.4 | n |  | TRUE
110 | bus_LV_2022-6_0_2_node_104 | 0.4 | n |  | TRUE
111 | bus_LV_2022-6_0_2_node_105 | 0.4 | n |  | TRUE
112 | bus_LV_2022-6_0_2_node_106 | 0.4 | n |  | TRUE
113 | bus_LV_2022-6_0_2_node_107 | 0.4 | n |  | TRUE
114 | bus_LV_2022-6_0_2_node_108 | 0.4 | n |  | TRUE
115 | bus_LV_2022-6_0_2_node_109 | 0.4 | n |  | TRUE
116 | bus_LV_2022-6_0_2_node_110 | 0.4 | n |  | TRUE
117 | bus_LV_2022-6_0_2_node_124 | 0.4 | n |  | TRUE
118 | bus_LV_2022-6_0_2_node_117 | 0.4 | n |  | TRUE
119 | bus_LV_2022-6_0_2_node_114 | 0.4 | n |  | TRUE
120 | bus_LV_2022-6_0_2_node_116 | 0.4 | n |  | TRUE
121 | bus_LV_2022-6_0_2_node_119 | 0.4 | n |  | TRUE
122 | bus_LV_2022-6_0_2_node_120 | 0.4 | n |  | TRUE
123 | bus_LV_2022-6_0_2_node_121 | 0.4 | n |  | TRUE
124 | bus_LV_2022-6_0_2_node_123 | 0.4 | n |  | TRUE
125 | bus_LV_2022-6_0_2_node_132 | 0.4 | n |  | TRUE
126 | bus_LV_2022-6_0_2_node_134 | 0.4 | n |  | TRUE
127 | bus_MV_0_node_12 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2022-6_0_2_load_0 | 0 | 0.0048259 | 0.0012095 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2022-6_0_2_load_1 | 1 | 0.0033918 | 0.00085006 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2022-6_0_2_load_3 | 3 | 0.0030957 | 0.00077586 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2022-6_0_2_load_4 | 4 | 0.0040452 | 0.0010138 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2022-6_0_2_load_76 | 5 | 0.00069419 | 0.00017398 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2022-6_0_2_load_77 | 6 | 0.00069263 | 0.00017359 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2022-6_0_2_load_67 | 7 | 0.0011021 | 0.00027622 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2022-6_0_2_load_5 | 8 | 0.0032979 | 0.00082652 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2022-6_0_2_load_12 | 9 | 0.0016908 | 0.00042376 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2022-6_0_2_load_6 | 10 | 0.0042956 | 0.0010766 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2022-6_0_2_load_11 | 11 | 0.0014085 | 0.000353 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2022-6_0_2_load_7 | 12 | 0.0023511 | 0.00058923 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2022-6_0_2_load_8 | 13 | 0.0037266 | 0.00093396 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2022-6_0_2_load_9 | 14 | 0.010554 | 0.0026452 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2022-6_0_2_load_10 | 15 | 0.0081586 | 0.0020447 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2022-6_0_2_load_13 | 16 | 9.0077e-05 | 2.2575e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2022-6_0_2_load_14 | 17 | 0.00010994 | 2.7554e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2022-6_0_2_load_16 | 19 | 8.9459e-05 | 2.2421e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2022-6_0_2_load_17 | 20 | 0.00010655 | 2.6703e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2022-6_0_2_load_27 | 22 | 0.00012484 | 3.1288e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2022-6_0_2_load_28 | 23 | 0.00010333 | 2.5896e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2022-6_0_2_load_21 | 24 | 9.6768e-05 | 2.4252e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2022-6_0_2_load_22 | 25 | 0.00011917 | 2.9866e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2022-6_0_2_load_63 | 26 | 0.00013515 | 3.3873e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2022-6_0_2_load_34 | 27 | 9.8226e-05 | 2.4618e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2022-6_0_2_load_23 | 28 | 8.3486e-05 | 2.0924e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2022-6_0_2_load_24 | 29 | 8.3496e-05 | 2.0926e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2022-6_0_2_load_25 | 30 | 0.00010091 | 2.529e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2022-6_0_2_load_43 | 32 | 0.00011146 | 2.7934e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2022-6_0_2_load_37 | 33 | 9.6474e-05 | 2.4179e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2022-6_0_2_load_40 | 34 | 8.3715e-05 | 2.0981e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2022-6_0_2_load_41 | 35 | 0.0001167 | 2.9247e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2022-6_0_2_load_29 | 36 | 8.6957e-05 | 2.1794e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2022-6_0_2_load_32 | 38 | 0.00010793 | 2.705e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2022-6_0_2_load_33 | 39 | 0.00011091 | 2.7798e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2022-6_0_2_load_49 | 40 | 0.0001065 | 2.6692e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2022-6_0_2_load_48 | 41 | 8.7522e-05 | 2.1935e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2022-6_0_2_load_58 | 43 | 0.00015322 | 3.84e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2022-6_0_2_load_45 | 45 | 9.4422e-05 | 2.3664e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2022-6_0_2_load_36 | 46 | 9.7947e-05 | 2.4548e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2022-6_0_2_load_38 | 47 | 0.00011809 | 2.9596e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2022-6_0_2_load_39 | 48 | 0.00026122 | 6.5467e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2022-6_0_2_load_64 | 49 | 0.0001089 | 2.7293e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2022-6_0_2_load_69 | 50 | 0.00012876 | 3.2271e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2022-6_0_2_load_42 | 51 | 0.00012241 | 3.0679e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2022-6_0_2_load_66 | 53 | 0.00015432 | 3.8676e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2022-6_0_2_load_44 | 54 | 9.2474e-05 | 2.3176e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2022-6_0_2_load_47 | 56 | 8.8734e-05 | 2.2239e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2022-6_0_2_load_50 | 57 | 8.1911e-05 | 2.0529e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2022-6_0_2_load_51 | 58 | 0.00015632 | 3.9179e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2022-6_0_2_load_56 | 60 | 9.8517e-05 | 2.4691e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2022-6_0_2_load_57 | 61 | 0.00010432 | 2.6144e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2022-6_0_2_load_53 | 62 | 0.0001186 | 2.9725e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2022-6_0_2_load_61 | 63 | 0.00011821 | 2.9626e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2022-6_0_2_load_72 | 64 | 0.0001151 | 2.8846e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2022-6_0_2_load_54 | 65 | 0.00010984 | 2.7527e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2022-6_0_2_load_127 | 66 | 0.00010267 | 2.5733e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2022-6_0_2_load_129 | 67 | 0.00010775 | 2.7005e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2022-6_0_2_load_128 | 69 | 0.00012895 | 3.2319e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2022-6_0_2_load_62 | 70 | 0.00010839 | 2.7165e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2022-6_0_2_load_73 | 71 | 0.00011216 | 2.8111e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2022-6_0_2_load_126 | 72 | 0.00011584 | 2.9033e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2022-6_0_2_load_131 | 73 | 0.00012012 | 3.0105e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2022-6_0_2_load_133 | 74 | 0.00017593 | 4.4093e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2022-6_0_2_load_111 | 76 | 0.00016627 | 4.1671e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2022-6_0_2_load_103 | 77 | 8.9627e-05 | 2.2463e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2022-6_0_2_load_102 | 78 | 8.3154e-05 | 2.084e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2022-6_0_2_load_68 | 79 | 0.00013948 | 3.4957e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2022-6_0_2_load_74 | 80 | 9.5098e-05 | 2.3834e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2022-6_0_2_load_70 | 82 | 0.00010122 | 2.5367e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2022-6_0_2_load_75 | 83 | 0.00010615 | 2.6604e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2022-6_0_2_load_80 | 85 | 0.00014188 | 3.5559e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2022-6_0_2_load_81 | 86 | 9.3182e-05 | 2.3354e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2022-6_0_2_load_84 | 87 | 0.00063841 | 0.00016 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2022-6_0_2_load_89 | 88 | 0.0013024 | 0.00032641 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2022-6_0_2_load_82 | 89 | 0.000104 | 2.6065e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2022-6_0_2_load_83 | 91 | 0.00059097 | 0.00014811 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2022-6_0_2_load_99 | 92 | 0.00010021 | 2.5115e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2022-6_0_2_load_97 | 93 | 8.9065e-05 | 2.2322e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2022-6_0_2_load_85 | 95 | 8.2483e-05 | 2.0672e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2022-6_0_2_load_86 | 96 | 0.00010302 | 2.5819e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2022-6_0_2_load_87 | 97 | 0.00089631 | 0.00022464 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2022-6_0_2_load_88 | 98 | 0.00010962 | 2.7475e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2022-6_0_2_load_91 | 99 | 9.6499e-05 | 2.4185e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2022-6_0_2_load_93 | 100 | 0.00014993 | 3.7576e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2022-6_0_2_load_94 | 101 | 9.3338e-05 | 2.3393e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2022-6_0_2_load_118 | 102 | 0.00015664 | 3.9257e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2022-6_0_2_load_95 | 104 | 8.237e-05 | 2.0644e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2022-6_0_2_load_101 | 106 | 0.00010053 | 2.5196e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2022-6_0_2_load_100 | 107 | 0.00011259 | 2.8217e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2022-6_0_2_load_113 | 108 | 0.0001836 | 4.6014e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2022-6_0_2_load_112 | 109 | 0.00010561 | 2.6468e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2022-6_0_2_load_105 | 111 | 0.00010283 | 2.5772e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2022-6_0_2_load_106 | 112 | 9.924e-05 | 2.4872e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2022-6_0_2_load_107 | 113 | 0.00010159 | 2.5461e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2022-6_0_2_load_109 | 115 | 8.8683e-05 | 2.2226e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2022-6_0_2_load_124 | 117 | 0.00028662 | 7.1834e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2022-6_0_2_load_117 | 118 | 0.00010747 | 2.6935e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2022-6_0_2_load_114 | 119 | 0.00014569 | 3.6513e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2022-6_0_2_load_116 | 120 | 0.00022248 | 5.5759e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2022-6_0_2_load_119 | 121 | 0.0001286 | 3.223e-05 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2022-6_0_2_load_120 | 122 | 0.00011705 | 2.9337e-05 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2022-6_0_2_load_121 | 123 | 0.00012582 | 3.1533e-05 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2022-6_0_2_load_123 | 124 | 0.00011941 | 2.9928e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2022-6_0_2_load_132 | 125 | 0.00012857 | 3.2223e-05 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2022-6_0_2_load_134 | 126 | 0.00023259 | 5.8293e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2022-6_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0085703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2022-6_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.040379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2022-6_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.033518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2022-6_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.046139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2022-6_0_2_line_4 | NAYY 4x150 SE | 3 | 8 | 0.0036748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2022-6_0_2_line_5 | NAYY 4x150 SE | 4 | 9 | 0.074388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2022-6_0_2_line_6 | NAYY 4x150 SE | 4 | 5 | 0.2658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2022-6_0_2_line_7 | NAYY 4x150 SE | 5 | 6 | 0.019697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2022-6_0_2_line_8 | NAYY 4x150 SE | 5 | 7 | 0.026677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2022-6_0_2_line_9 | NAYY 4x150 SE | 7 | 52 | 0.0098095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2022-6_0_2_line_10 | NAYY 4x150 SE | 8 | 10 | 0.019543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2022-6_0_2_line_11 | NAYY 4x150 SE | 9 | 11 | 0.004299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2022-6_0_2_line_12 | NAYY 4x150 SE | 10 | 12 | 0.0026816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2022-6_0_2_line_13 | NAYY 4x150 SE | 12 | 13 | 0.019428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2022-6_0_2_line_14 | NAYY 4x150 SE | 13 | 14 | 0.0073526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2022-6_0_2_line_15 | NAYY 4x150 SE | 14 | 15 | 0.024545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2022-6_0_2_line_16 | NAYY 4x150 SE | 16 | 17 | 0.016307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2022-6_0_2_line_17 | NAYY 4x150 SE | 16 | 18 | 0.010649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2022-6_0_2_line_18 | NAYY 4x150 SE | 17 | 19 | 0.013738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2022-6_0_2_line_19 | NAYY 4x150 SE | 18 | 20 | 0.003795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2022-6_0_2_line_20 | NAYY 4x150 SE | 19 | 21 | 0.010126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2022-6_0_2_line_21 | NAYY 4x150 SE | 21 | 22 | 0.010713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2022-6_0_2_line_22 | NAYY 4x150 SE | 21 | 23 | 0.019707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2022-6_0_2_line_23 | NAYY 4x150 SE | 22 | 34 | 0.014017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2022-6_0_2_line_24 | NAYY 4x150 SE | 23 | 31 | 0.0075194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2022-6_0_2_line_25 | NAYY 4x150 SE | 24 | 25 | 0.01289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2022-6_0_2_line_26 | NAYY 4x150 SE | 25 | 28 | 0.001466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2022-6_0_2_line_27 | NAYY 4x150 SE | 26 | 27 | 0.0057138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2022-6_0_2_line_28 | NAYY 4x150 SE | 27 | 37 | 0.032489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2022-6_0_2_line_29 | NAYY 4x150 SE | 28 | 29 | 0.014373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2022-6_0_2_line_30 | NAYY 4x150 SE | 29 | 30 | 0.017535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2022-6_0_2_line_31 | NAYY 4x150 SE | 30 | 31 | 0.0077826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2022-6_0_2_line_32 | NAYY 4x150 SE | 31 | 32 | 0.0087399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2022-6_0_2_line_33 | NAYY 4x150 SE | 31 | 33 | 0.0093041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2022-6_0_2_line_34 | NAYY 4x150 SE | 32 | 45 | 0.014772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2022-6_0_2_line_35 | NAYY 4x150 SE | 33 | 46 | 0.0094488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2022-6_0_2_line_36 | NAYY 4x150 SE | 34 | 35 | 0.012358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2022-6_0_2_line_37 | NAYY 4x150 SE | 35 | 51 | 0.028004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2022-6_0_2_line_38 | NAYY 4x150 SE | 36 | 37 | 0.011845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2022-6_0_2_line_39 | NAYY 4x150 SE | 37 | 38 | 0.0082173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2022-6_0_2_line_40 | NAYY 4x150 SE | 37 | 39 | 0.0058137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2022-6_0_2_line_41 | NAYY 4x150 SE | 38 | 40 | 0.008139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2022-6_0_2_line_42 | NAYY 4x150 SE | 40 | 41 | 0.014108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2022-6_0_2_line_43 | NAYY 4x150 SE | 41 | 55 | 0.0025505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2022-6_0_2_line_44 | NAYY 4x150 SE | 42 | 43 | 0.026891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2022-6_0_2_line_45 | NAYY 4x150 SE | 42 | 44 | 0.038262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2022-6_0_2_line_46 | NAYY 4x150 SE | 43 | 66 | 0.0091108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2022-6_0_2_line_47 | NAYY 4x150 SE | 44 | 67 | 0.028707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2022-6_0_2_line_48 | NAYY 4x150 SE | 44 | 68 | 0.11495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2022-6_0_2_line_49 | NAYY 4x150 SE | 44 | 69 | 0.013832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2022-6_0_2_line_50 | NAYY 4x150 SE | 45 | 54 | 0.0002582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2022-6_0_2_line_51 | NAYY 4x150 SE | 46 | 47 | 0.011194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2022-6_0_2_line_52 | NAYY 4x150 SE | 47 | 48 | 0.0021533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2022-6_0_2_line_53 | NAYY 4x150 SE | 49 | 50 | 0.0032604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2022-6_0_2_line_54 | NAYY 4x150 SE | 50 | 79 | 0.006653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2022-6_0_2_line_55 | NAYY 4x150 SE | 52 | 53 | 0.018182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2022-6_0_2_line_56 | NAYY 4x150 SE | 53 | 80 | 0.0055352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2022-6_0_2_line_57 | NAYY 4x150 SE | 54 | 55 | 0.012996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2022-6_0_2_line_58 | NAYY 4x150 SE | 55 | 56 | 0.018739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2022-6_0_2_line_59 | NAYY 4x150 SE | 56 | 57 | 0.016129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2022-6_0_2_line_60 | NAYY 4x150 SE | 57 | 58 | 0.0027348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2022-6_0_2_line_61 | NAYY 4x150 SE | 58 | 59 | 0.016635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2022-6_0_2_line_62 | NAYY 4x150 SE | 59 | 60 | 0.0091447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2022-6_0_2_line_63 | NAYY 4x150 SE | 59 | 61 | 0.012068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2022-6_0_2_line_64 | NAYY 4x150 SE | 59 | 62 | 0.0082476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2022-6_0_2_line_65 | NAYY 4x150 SE | 60 | 63 | 0.011242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2022-6_0_2_line_66 | NAYY 4x150 SE | 61 | 64 | 0.0014157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2022-6_0_2_line_67 | NAYY 4x150 SE | 62 | 65 | 0.012722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2022-6_0_2_line_68 | NAYY 4x150 SE | 63 | 70 | 0.0023677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2022-6_0_2_line_69 | NAYY 4x150 SE | 64 | 71 | 0.015929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2022-6_0_2_line_70 | NAYY 4x150 SE | 66 | 72 | 0.008128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2022-6_0_2_line_71 | NAYY 4x150 SE | 67 | 73 | 0.018514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2022-6_0_2_line_72 | NAYY 4x150 SE | 68 | 74 | 0.011105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2022-6_0_2_line_73 | NAYY 4x150 SE | 68 | 75 | 0.026149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2022-6_0_2_line_74 | NAYY 4x150 SE | 69 | 76 | 0.021581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2022-6_0_2_line_75 | NAYY 4x150 SE | 70 | 77 | 0.005177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2022-6_0_2_line_76 | NAYY 4x150 SE | 71 | 81 | 0.010785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2022-6_0_2_line_77 | NAYY 4x150 SE | 72 | 112 | 0.0080372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2022-6_0_2_line_78 | NAYY 4x150 SE | 73 | 125 | 0.0021037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2022-6_0_2_line_79 | NAYY 4x150 SE | 75 | 126 | 0.012829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2022-6_0_2_line_80 | NAYY 4x150 SE | 76 | 114 | 0.011811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2022-6_0_2_line_81 | NAYY 4x150 SE | 77 | 78 | 0.011946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2022-6_0_2_line_82 | NAYY 4x150 SE | 78 | 110 | 0.0088799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2022-6_0_2_line_83 | NAYY 4x150 SE | 79 | 82 | 0.0083836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2022-6_0_2_line_84 | NAYY 4x150 SE | 80 | 81 | 0.019676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2022-6_0_2_line_85 | NAYY 4x150 SE | 81 | 83 | 0.0067604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2022-6_0_2_line_86 | NAYY 4x150 SE | 81 | 82 | 0.012034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2022-6_0_2_line_87 | NAYY 4x150 SE | 84 | 85 | 0.022277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2022-6_0_2_line_88 | NAYY 4x150 SE | 84 | 86 | 0.013109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2022-6_0_2_line_89 | NAYY 4x150 SE | 85 | 89 | 0.0013365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2022-6_0_2_line_90 | NAYY 4x150 SE | 86 | 90 | 0.011562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2022-6_0_2_line_91 | NAYY 4x150 SE | 87 | 88 | 0.019274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2022-6_0_2_line_92 | NAYY 4x150 SE | 88 | 94 | 0.01675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2022-6_0_2_line_93 | NAYY 4x150 SE | 89 | 91 | 0.0038129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2022-6_0_2_line_94 | NAYY 4x150 SE | 90 | 92 | 0.0028187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2022-6_0_2_line_95 | NAYY 4x150 SE | 90 | 93 | 0.0076202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2022-6_0_2_line_96 | NAYY 4x150 SE | 92 | 107 | 0.005844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2022-6_0_2_line_97 | NAYY 4x150 SE | 93 | 98 | 0.010991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2022-6_0_2_line_98 | NAYY 4x150 SE | 94 | 99 | 0.01151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2022-6_0_2_line_99 | NAYY 4x150 SE | 95 | 96 | 0.01035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2022-6_0_2_line_100 | NAYY 4x150 SE | 95 | 97 | 0.0045919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2022-6_0_2_line_101 | NAYY 4x150 SE | 96 | 98 | 0.0015576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2022-6_0_2_line_102 | NAYY 4x150 SE | 99 | 100 | 0.010022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2022-6_0_2_line_103 | NAYY 4x150 SE | 100 | 101 | 0.0046006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2022-6_0_2_line_104 | NAYY 4x150 SE | 101 | 104 | 0.0069863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2022-6_0_2_line_105 | NAYY 4x150 SE | 102 | 103 | 0.0063367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2022-6_0_2_line_106 | NAYY 4x150 SE | 103 | 118 | 0.017295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2022-6_0_2_line_107 | NAYY 4x150 SE | 103 | 119 | 0.011575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2022-6_0_2_line_108 | NAYY 4x150 SE | 104 | 105 | 0.0058154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2022-6_0_2_line_109 | NAYY 4x150 SE | 105 | 106 | 0.0092193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2022-6_0_2_line_110 | NAYY 4x150 SE | 105 | 107 | 0.017987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2022-6_0_2_line_111 | NAYY 4x150 SE | 106 | 108 | 0.0023994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2022-6_0_2_line_112 | NAYY 4x150 SE | 108 | 109 | 0.016525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2022-6_0_2_line_113 | NAYY 4x150 SE | 109 | 111 | 0.0040757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2022-6_0_2_line_114 | NAYY 4x150 SE | 110 | 111 | 0.01004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2022-6_0_2_line_115 | NAYY 4x150 SE | 110 | 112 | 0.014266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2022-6_0_2_line_116 | NAYY 4x150 SE | 113 | 114 | 0.019371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2022-6_0_2_line_117 | NAYY 4x150 SE | 113 | 115 | 0.00053984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2022-6_0_2_line_118 | NAYY 4x150 SE | 114 | 116 | 0.04496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2022-6_0_2_line_119 | NAYY 4x150 SE | 116 | 117 | 0.012169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2022-6_0_2_line_120 | NAYY 4x150 SE | 116 | 118 | 0.004755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2022-6_0_2_line_121 | NAYY 4x150 SE | 119 | 120 | 0.0030896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_2022-6_0_2_line_122 | NAYY 4x150 SE | 121 | 122 | 0.019951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_2022-6_0_2_line_123 | NAYY 4x150 SE | 121 | 123 | 0.010138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_2022-6_0_2_line_124 | NAYY 4x150 SE | 123 | 124 | 0.0095823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_2022-6_0_2_line_125 | NAYY 4x150 SE | 124 | 125 | 0.01389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2022-6_0_2_trafo_12 | 0.25 MVA 20/0.4 kV | 127 | 9 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2562219.5217 | 1195026.1339 | 2562223.9443 | 1195033.4749
1 | 2562198.6848 | 1194991.5469 | 2562219.5217 | 1195026.1339
2 | 2562241.2408 | 1195062.1852 | 2562223.9443 | 1195033.4749
3 | 2562198.6848 | 1194991.5469 | 2562162.1879 | 1195019.7749
4 | 2562241.2408 | 1195062.1852 | 2562243.1371 | 1195065.3329
5 | 2562162.1879 | 1195019.7749 | 2562160.5546 | 1195021.0381 | 2562202.6515 | 1195079.8471
6 | 2561905.863 | 1195090.0952 | 2562162.1879 | 1195019.7749
7 | 2561905.863 | 1195090.0952 | 2561909.8716 | 1195103.0452 | 2561908.5335 | 1195109.0382
8 | 2561905.863 | 1195090.0952 | 2561903.8578 | 1195083.6174 | 2561894.1683 | 1195066.2409
9 | 2561889.3908 | 1195057.6733 | 2561894.1683 | 1195066.2409
10 | 2562253.2221 | 1195082.0728 | 2562243.1371 | 1195065.3329
11 | 2562205.1538 | 1195083.3429 | 2562202.6515 | 1195079.8471
12 | 2562253.2221 | 1195082.0728 | 2562254.6059 | 1195084.3698
13 | 2562254.6059 | 1195084.3698 | 2562264.6317 | 1195101.0114
14 | 2562264.6317 | 1195101.0114 | 2562268.4259 | 1195107.3094
15 | 2562281.0919 | 1195128.3337 | 2562268.4259 | 1195107.3094
16 | 2561791.6664 | 1194944.4766 | 2561802.5843 | 1194956.5886
17 | 2561784.5361 | 1194936.5665 | 2561791.6664 | 1194944.4766
18 | 2561802.5843 | 1194956.5886 | 2561811.7822 | 1194966.7924
19 | 2561784.5361 | 1194936.5665 | 2561781.7947 | 1194933.9421
20 | 2561818.5621 | 1194974.3138 | 2561811.7822 | 1194966.7924
21 | 2561818.5621 | 1194974.3138 | 2561826.095 | 1194981.9307
22 | 2561818.5621 | 1194974.3138 | 2561807.0556 | 1194990.3121
23 | 2561835.9512 | 1194991.8968 | 2561826.095 | 1194981.9307
24 | 2561802.665 | 1194996.4166 | 2561807.0556 | 1194990.3121
25 | 2561758.4726 | 1194965.3023 | 2561769.0123 | 1194972.7229
26 | 2561770.211 | 1194973.5669 | 2561769.0123 | 1194972.7229
27 | 2561746.9858 | 1195017.1265 | 2561750.3248 | 1195021.7631
28 | 2561761.042 | 1195052.4251 | 2561750.4384 | 1195021.9208 | 2561750.3248 | 1195021.7631
29 | 2561770.211 | 1194973.5669 | 2561781.9636 | 1194981.8415
30 | 2561781.9636 | 1194981.8415 | 2561796.3015 | 1194991.9362
31 | 2561802.665 | 1194996.4166 | 2561796.3015 | 1194991.9362
32 | 2561802.665 | 1194996.4166 | 2561797.4703 | 1195003.4452
33 | 2561802.665 | 1194996.4166 | 2561809.886 | 1195002.2837
34 | 2561797.4703 | 1195003.4452 | 2561788.6902 | 1195015.3246
35 | 2561817.2193 | 1195008.2422 | 2561809.886 | 1195002.2837
36 | 2561835.9512 | 1194991.8968 | 2561844.6408 | 1195000.6834
37 | 2561844.6408 | 1195000.6834 | 2561854.2227 | 1195010.3721 | 2561862.8009 | 1195021.9098
38 | 2561761.042 | 1195052.4251 | 2561751.1944 | 1195045.8424
39 | 2561761.042 | 1195052.4251 | 2561765.9626 | 1195045.8441
40 | 2561761.042 | 1195052.4251 | 2561757.6276 | 1195057.1306
41 | 2561765.9626 | 1195045.8441 | 2561770.8364 | 1195039.3256
42 | 2561770.8364 | 1195039.3256 | 2561779.2847 | 1195028.0266
43 | 2561780.812 | 1195025.9839 | 2561779.2847 | 1195028.0266
44 | 2561741.5425 | 1195083.0114 | 2561756.3544 | 1195090.1648 | 2561765.0584 | 1195095.9339
45 | 2561719.7708 | 1195114.4684 | 2561728.0256 | 1195103.1091 | 2561741.5425 | 1195083.0114
46 | 2561765.0584 | 1195095.9339 | 2561772.6525 | 1195100.9673
47 | 2561719.7708 | 1195114.4684 | 2561721.7795 | 1195130.6644 | 2561726.4031 | 1195142.1565
48 | 2561712.948 | 1195198.1359 | 2561677.8307 | 1195171.8803 | 2561695.3485 | 1195147.2209 | 2561719.7708 | 1195114.4684
49 | 2561719.7708 | 1195114.4684 | 2561731.0917 | 1195122.4159
50 | 2561788.6902 | 1195015.3246 | 2561788.5367 | 1195015.5323
51 | 2561817.2193 | 1195008.2422 | 2561820.5032 | 1195010.9104 | 2561824.3728 | 1195016.6993
52 | 2561824.3728 | 1195016.6993 | 2561825.5695 | 1195018.4894
53 | 2561836.271 | 1195036.6181 | 2561837.5608 | 1195039.6126
54 | 2561840.1927 | 1195045.7228 | 2561837.5608 | 1195039.6126
55 | 2561889.3908 | 1195057.6733 | 2561871.475 | 1195060.7738
56 | 2561866.0209 | 1195061.7177 | 2561871.475 | 1195060.7738
57 | 2561780.812 | 1195025.9839 | 2561788.5367 | 1195015.5323
58 | 2561780.812 | 1195025.9839 | 2561793.9978 | 1195039.2988
59 | 2561801.3791 | 1195053.1211 | 2561798.6114 | 1195043.9575 | 2561793.9978 | 1195039.2988
60 | 2561801.3791 | 1195053.1211 | 2561802.1699 | 1195055.7392
61 | 2561806.9796 | 1195071.6636 | 2561802.1699 | 1195055.7392
62 | 2561806.9796 | 1195071.6636 | 2561807.3549 | 1195080.8006
63 | 2561806.9796 | 1195071.6636 | 2561818.8845 | 1195069.685
64 | 2561806.9796 | 1195071.6636 | 2561798.8484 | 1195073.0446
65 | 2561807.3549 | 1195080.8006 | 2561807.8163 | 1195092.0332
66 | 2561820.2811 | 1195069.4528 | 2561818.8845 | 1195069.685
67 | 2561798.8484 | 1195073.0446 | 2561786.3056 | 1195075.1748
68 | 2561807.9135 | 1195094.399 | 2561807.8163 | 1195092.0332
69 | 2561820.2811 | 1195069.4528 | 2561835.9943 | 1195066.8412
70 | 2561779.4274 | 1195105.4578 | 2561772.6525 | 1195100.9673
71 | 2561735.6123 | 1195157.983 | 2561729.948 | 1195150.9676 | 2561726.4031 | 1195142.1565
72 | 2561712.948 | 1195198.1359 | 2561720.1316 | 1195189.6518
73 | 2561712.948 | 1195198.1359 | 2561734.4007 | 1195213.1732
74 | 2561748.7546 | 1195134.8156 | 2561731.0917 | 1195122.4159
75 | 2561807.9135 | 1195094.399 | 2561808.126 | 1195099.5716 | 2561808.126 | 1195099.5716
76 | 2561846.6334 | 1195065.0729 | 2561835.9943 | 1195066.8412
77 | 2561779.4274 | 1195105.4578 | 2561786.1267 | 1195109.8982
78 | 2561736.9338 | 1195159.6198 | 2561735.6123 | 1195157.983
79 | 2561734.4007 | 1195213.1732 | 2561743.1249 | 1195203.7454
80 | 2561758.4215 | 1195141.602 | 2561748.7546 | 1195134.8156
81 | 2561802.3278 | 1195110.016 | 2561808.126 | 1195099.5716
82 | 2561798.0177 | 1195117.7797 | 2561802.3278 | 1195110.016
83 | 2561840.1927 | 1195045.7228 | 2561842.1423 | 1195050.2491 | 2561843.1441 | 1195053.556
84 | 2561846.6334 | 1195065.0729 | 2561866.0209 | 1195061.7177
85 | 2561846.6334 | 1195065.0729 | 2561846.8139 | 1195071.8309
86 | 2561846.6334 | 1195065.0729 | 2561843.1441 | 1195053.556
87 | 2561847.3548 | 1195092.0832 | 2561869.5358 | 1195094.1536
88 | 2561847.3548 | 1195092.0832 | 2561845.9137 | 1195103.821 | 2561845.6196 | 1195105.07
89 | 2561869.5358 | 1195094.1536 | 2561870.8666 | 1195094.2778
90 | 2561842.969 | 1195116.3245 | 2561845.6196 | 1195105.07
91 | 2561877.9046 | 1195151.1959 | 2561890.795 | 1195136.8662
92 | 2561865.6884 | 1195162.6491 | 2561877.1482 | 1195152.0367 | 2561877.9046 | 1195151.1959
93 | 2561874.663 | 1195094.6322 | 2561870.8666 | 1195094.2778
94 | 2561842.969 | 1195116.3245 | 2561841.9397 | 1195118.9486
95 | 2561842.969 | 1195116.3245 | 2561850.2265 | 1195118.6474
96 | 2561839.8058 | 1195124.3891 | 2561841.9397 | 1195118.9486
97 | 2561860.6946 | 1195121.998 | 2561850.2265 | 1195118.6474
98 | 2561865.6884 | 1195162.6491 | 2561856.0951 | 1195156.2885
99 | 2561872.0359 | 1195125.6279 | 2561862.178 | 1195122.4728
100 | 2561876.4092 | 1195127.0277 | 2561872.0359 | 1195125.6279
101 | 2561862.178 | 1195122.4728 | 2561860.6946 | 1195121.998
102 | 2561856.0951 | 1195156.2885 | 2561847.742 | 1195150.7502
103 | 2561847.742 | 1195150.7502 | 2561843.9077 | 1195148.2079
104 | 2561843.9077 | 1195148.2079 | 2561838.0849 | 1195144.3473
105 | 2561813.3279 | 1195180.1604 | 2561818.5143 | 1195183.8011
106 | 2561813.3279 | 1195180.1604 | 2561799.1728 | 1195170.2233
107 | 2561813.3279 | 1195180.1604 | 2561821.2119 | 1195171.6859
108 | 2561833.2381 | 1195141.1337 | 2561838.0849 | 1195144.3473
109 | 2561833.2381 | 1195141.1337 | 2561825.5545 | 1195136.0389
110 | 2561833.2381 | 1195141.1337 | 2561839.8058 | 1195124.3891
111 | 2561823.5548 | 1195134.7129 | 2561825.5545 | 1195136.0389
112 | 2561809.7824 | 1195125.5806 | 2561823.5548 | 1195134.7129
113 | 2561806.3856 | 1195123.3282 | 2561809.7824 | 1195125.5806
114 | 2561798.0177 | 1195117.7797 | 2561806.3856 | 1195123.3282
115 | 2561798.0177 | 1195117.7797 | 2561786.1267 | 1195109.8982
116 | 2561758.4215 | 1195141.602 | 2561769.7509 | 1195125.8897
117 | 2561770.0666 | 1195125.4519 | 2561769.7509 | 1195125.8897
118 | 2561795.281 | 1195167.4912 | 2561758.4215 | 1195141.602
119 | 2561795.281 | 1195167.4912 | 2561801.6832 | 1195157.1334
120 | 2561795.281 | 1195167.4912 | 2561799.1728 | 1195170.2233
121 | 2561823.3163 | 1195169.4239 | 2561821.2119 | 1195171.6859
122 | 2561762.0845 | 1195181.6009 | 2561767.734 | 1195185.8667 | 2561779.3658 | 1195191.3785
123 | 2561753.9938 | 1195175.4918 | 2561762.0845 | 1195181.6009
124 | 2561753.9938 | 1195175.4918 | 2561746.3466 | 1195169.7177
125 | 2561736.9338 | 1195159.6198 | 2561743.1195 | 1195167.2809 | 2561746.3466 | 1195169.7177

## bus_geodata
| x | y | coords
0 | 2562219.5217 | 1195026.1339
1 | 2562223.9443 | 1195033.4749
2 | 2562198.6848 | 1194991.5469
3 | 2562241.2408 | 1195062.1852
4 | 2562162.1879 | 1195019.7749
5 | 2561905.863 | 1195090.0952
6 | 2561908.5335 | 1195109.0382
7 | 2561894.1683 | 1195066.2409
8 | 2562243.1371 | 1195065.3329
9 | 2562202.6515 | 1195079.8471
10 | 2562253.2221 | 1195082.0728
11 | 2562205.1538 | 1195083.3429
12 | 2562254.6059 | 1195084.3698
13 | 2562264.6317 | 1195101.0114
14 | 2562268.4259 | 1195107.3094
15 | 2562281.0919 | 1195128.3337
16 | 2561791.6664 | 1194944.4766
17 | 2561802.5843 | 1194956.5886
18 | 2561784.5361 | 1194936.5665
19 | 2561811.7822 | 1194966.7924
20 | 2561781.7947 | 1194933.9421
21 | 2561818.5621 | 1194974.3138
22 | 2561826.095 | 1194981.9307
23 | 2561807.0556 | 1194990.3121
24 | 2561758.4726 | 1194965.3023
25 | 2561769.0123 | 1194972.7229
26 | 2561746.9858 | 1195017.1265
27 | 2561750.3248 | 1195021.7631
28 | 2561770.211 | 1194973.5669
29 | 2561781.9636 | 1194981.8415
30 | 2561796.3015 | 1194991.9362
31 | 2561802.665 | 1194996.4166
32 | 2561797.4703 | 1195003.4452
33 | 2561809.886 | 1195002.2837
34 | 2561835.9512 | 1194991.8968
35 | 2561844.6408 | 1195000.6834
36 | 2561751.1944 | 1195045.8424
37 | 2561761.042 | 1195052.4251
38 | 2561765.9626 | 1195045.8441
39 | 2561757.6276 | 1195057.1306
40 | 2561770.8364 | 1195039.3256
41 | 2561779.2847 | 1195028.0266
42 | 2561741.5425 | 1195083.0114
43 | 2561765.0584 | 1195095.9339
44 | 2561719.7708 | 1195114.4684
45 | 2561788.6902 | 1195015.3246
46 | 2561817.2193 | 1195008.2422
47 | 2561824.3728 | 1195016.6993
48 | 2561825.5695 | 1195018.4894
49 | 2561836.271 | 1195036.6181
50 | 2561837.5608 | 1195039.6126
51 | 2561862.8009 | 1195021.9098
52 | 2561889.3908 | 1195057.6733
53 | 2561871.475 | 1195060.7738
54 | 2561788.5367 | 1195015.5323
55 | 2561780.812 | 1195025.9839
56 | 2561793.9978 | 1195039.2988
57 | 2561801.3791 | 1195053.1211
58 | 2561802.1699 | 1195055.7392
59 | 2561806.9796 | 1195071.6636
60 | 2561807.3549 | 1195080.8006
61 | 2561818.8845 | 1195069.685
62 | 2561798.8484 | 1195073.0446
63 | 2561807.8163 | 1195092.0332
64 | 2561820.2811 | 1195069.4528
65 | 2561786.3056 | 1195075.1748
66 | 2561772.6525 | 1195100.9673
67 | 2561726.4031 | 1195142.1565
68 | 2561712.948 | 1195198.1359
69 | 2561731.0917 | 1195122.4159
70 | 2561807.9135 | 1195094.399
71 | 2561835.9943 | 1195066.8412
72 | 2561779.4274 | 1195105.4578
73 | 2561735.6123 | 1195157.983
74 | 2561720.1316 | 1195189.6518
75 | 2561734.4007 | 1195213.1732
76 | 2561748.7546 | 1195134.8156
77 | 2561808.126 | 1195099.5716
78 | 2561802.3278 | 1195110.016
79 | 2561840.1927 | 1195045.7228
80 | 2561866.0209 | 1195061.7177
81 | 2561846.6334 | 1195065.0729
82 | 2561843.1441 | 1195053.556
83 | 2561846.8139 | 1195071.8309
84 | 2561847.3548 | 1195092.0832
85 | 2561869.5358 | 1195094.1536
86 | 2561845.6196 | 1195105.07
87 | 2561890.795 | 1195136.8662
88 | 2561877.9046 | 1195151.1959
89 | 2561870.8666 | 1195094.2778
90 | 2561842.969 | 1195116.3245
91 | 2561874.663 | 1195094.6322
92 | 2561841.9397 | 1195118.9486
93 | 2561850.2265 | 1195118.6474
94 | 2561865.6884 | 1195162.6491
95 | 2561872.0359 | 1195125.6279
96 | 2561862.178 | 1195122.4728
97 | 2561876.4092 | 1195127.0277
98 | 2561860.6946 | 1195121.998
99 | 2561856.0951 | 1195156.2885
100 | 2561847.742 | 1195150.7502
101 | 2561843.9077 | 1195148.2079
102 | 2561818.5143 | 1195183.8011
103 | 2561813.3279 | 1195180.1604
104 | 2561838.0849 | 1195144.3473
105 | 2561833.2381 | 1195141.1337
106 | 2561825.5545 | 1195136.0389
107 | 2561839.8058 | 1195124.3891
108 | 2561823.5548 | 1195134.7129
109 | 2561809.7824 | 1195125.5806
110 | 2561798.0177 | 1195117.7797
111 | 2561806.3856 | 1195123.3282
112 | 2561786.1267 | 1195109.8982
113 | 2561769.7509 | 1195125.8897
114 | 2561758.4215 | 1195141.602
115 | 2561770.0666 | 1195125.4519
116 | 2561795.281 | 1195167.4912
117 | 2561801.6832 | 1195157.1334
118 | 2561799.1728 | 1195170.2233
119 | 2561821.2119 | 1195171.6859
120 | 2561823.3163 | 1195169.4239
121 | 2561762.0845 | 1195181.6009
122 | 2561779.3658 | 1195191.3785
123 | 2561753.9938 | 1195175.4918
124 | 2561746.3466 | 1195169.7177
125 | 2561736.9338 | 1195159.6198
126 | 2561743.1249 | 1195203.7454
127 | 2562202.6515 | 1195079.8471

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98765 | -0.086386 | 0.0048259 | 0.0012095
1 | 0.98717 | -0.089797 | 0.0033918 | 0.00085006
2 | 0.9902 | -0.068374 | 0 | 0
3 | 0.98544 | -0.102 | 0.0030957 | 0.00077586
4 | 0.99312 | -0.047904 | 0.0040452 | 0.0010138
5 | 0.98691 | -0.092027 | 0.00069419 | 0.00017398
6 | 0.98689 | -0.092167 | 0.00069263 | 0.00017359
7 | 0.98634 | -0.096102 | 0.0011021 | 0.00027622
8 | 0.98527 | -0.10322 | 0.0032979 | 0.00082652
9 | 1 | 0 | -0.067043 | -0.016703
10 | 0.98445 | -0.10907 | 0.0042956 | 0.0010766
11 | 0.99999 | -6.0441e-05 | 0.0014085 | 0.000353
12 | 0.98435 | -0.10976 | 0.0023511 | 0.00058923
13 | 0.98372 | -0.11425 | 0.0037266 | 0.00093396
14 | 0.98352 | -0.11567 | 0.010554 | 0.0026452
15 | 0.98323 | -0.11774 | 0.0081586 | 0.0020447
16 | 0.98414 | -0.11186 | 9.0077e-05 | 2.2575e-05
17 | 0.98414 | -0.11182 | 0.00010994 | 2.7554e-05
18 | 0.98414 | -0.11187 | 0 | 0
19 | 0.98415 | -0.11178 | 8.9459e-05 | 2.2421e-05
20 | 0.98414 | -0.11187 | 0.00010655 | 2.6703e-05
21 | 0.98416 | -0.11174 | 0 | 0
22 | 0.98415 | -0.11179 | 0.00012484 | 3.1288e-05
23 | 0.98418 | -0.11156 | 0.00010333 | 2.5896e-05
24 | 0.98417 | -0.11166 | 9.6768e-05 | 2.4252e-05
25 | 0.98417 | -0.11165 | 0.00011917 | 2.9866e-05
26 | 0.98427 | -0.11095 | 0.00013515 | 3.3873e-05
27 | 0.98427 | -0.11094 | 9.8226e-05 | 2.4618e-05
28 | 0.98417 | -0.11164 | 8.3486e-05 | 2.0924e-05
29 | 0.98418 | -0.1116 | 8.3496e-05 | 2.0926e-05
30 | 0.98419 | -0.11153 | 0.00010091 | 2.529e-05
31 | 0.98419 | -0.11149 | 0 | 0
32 | 0.98422 | -0.11131 | 0.00011146 | 2.7934e-05
33 | 0.98418 | -0.11155 | 9.6474e-05 | 2.4179e-05
34 | 0.98414 | -0.11184 | 8.3715e-05 | 2.0981e-05
35 | 0.98414 | -0.11187 | 0.0001167 | 2.9247e-05
36 | 0.98428 | -0.11087 | 8.6957e-05 | 2.1794e-05
37 | 0.98428 | -0.11086 | 0 | 0
38 | 0.98428 | -0.11082 | 0.00010793 | 2.705e-05
39 | 0.98428 | -0.11087 | 0.00011091 | 2.7798e-05
40 | 0.98429 | -0.11078 | 0.0001065 | 2.6692e-05
41 | 0.9843 | -0.11068 | 8.7522e-05 | 2.1935e-05
42 | 0.98367 | -0.11525 | 0 | 0
43 | 0.98377 | -0.1145 | 0.00015322 | 3.84e-05
44 | 0.98352 | -0.11631 | 0 | 0
45 | 0.98426 | -0.11098 | 9.4422e-05 | 2.3664e-05
46 | 0.98418 | -0.11159 | 9.7947e-05 | 2.4548e-05
47 | 0.98417 | -0.11164 | 0.00011809 | 2.9596e-05
48 | 0.98417 | -0.11164 | 0.00026122 | 6.5467e-05
49 | 0.98528 | -0.10369 | 0.0001089 | 2.7293e-05
50 | 0.98528 | -0.10369 | 0.00012876 | 3.2271e-05
51 | 0.98413 | -0.1119 | 0.00012241 | 3.0679e-05
52 | 0.98614 | -0.097491 | 0 | 0
53 | 0.98578 | -0.10007 | 0.00015432 | 3.8676e-05
54 | 0.98426 | -0.11098 | 9.2474e-05 | 2.3176e-05
55 | 0.98431 | -0.11066 | 0 | 0
56 | 0.98439 | -0.11007 | 8.8734e-05 | 2.2239e-05
57 | 0.98446 | -0.10955 | 8.1911e-05 | 2.0529e-05
58 | 0.98447 | -0.10946 | 0.00015632 | 3.9179e-05
59 | 0.98455 | -0.10887 | 0 | 0
60 | 0.98444 | -0.10972 | 9.8517e-05 | 2.4691e-05
61 | 0.98477 | -0.10731 | 0.00010432 | 2.6144e-05
62 | 0.98455 | -0.10889 | 0.0001186 | 2.9725e-05
63 | 0.98429 | -0.11075 | 0.00011821 | 2.9626e-05
64 | 0.9848 | -0.10712 | 0.0001151 | 2.8846e-05
65 | 0.98455 | -0.10891 | 0.00010984 | 2.7527e-05
66 | 0.98381 | -0.11423 | 0.00010267 | 2.5733e-05
67 | 0.98349 | -0.11657 | 0.00010775 | 2.7005e-05
68 | 0.98345 | -0.11681 | 0 | 0
69 | 0.98349 | -0.11652 | 0.00012895 | 3.2319e-05
70 | 0.98426 | -0.11096 | 0.00010839 | 2.7165e-05
71 | 0.98509 | -0.10502 | 0.00011216 | 2.8111e-05
72 | 0.98384 | -0.11398 | 0.00011584 | 2.9033e-05
73 | 0.98347 | -0.11671 | 0.00012012 | 3.0105e-05
74 | 0.98345 | -0.11683 | 0.00017593 | 4.4093e-05
75 | 0.98344 | -0.11687 | 0 | 0
76 | 0.98345 | -0.1168 | 0.00016627 | 4.1671e-05
77 | 0.9842 | -0.11142 | 8.9627e-05 | 2.2463e-05
78 | 0.98405 | -0.11248 | 8.3154e-05 | 2.084e-05
79 | 0.98528 | -0.10367 | 0.00013948 | 3.4957e-05
80 | 0.98567 | -0.10084 | 9.5098e-05 | 2.3834e-05
81 | 0.98529 | -0.10358 | 0 | 0
82 | 0.98528 | -0.10364 | 0.00010122 | 2.5367e-05
83 | 0.98529 | -0.10359 | 0.00010615 | 2.6604e-05
84 | 0.98351 | -0.11635 | 0 | 0
85 | 0.98348 | -0.11654 | 0.00014188 | 3.5559e-05
86 | 0.98353 | -0.11623 | 9.3182e-05 | 2.3354e-05
87 | 0.98345 | -0.11678 | 0.00063841 | 0.00016
88 | 0.98347 | -0.11666 | 0.0013024 | 0.00032641
89 | 0.98348 | -0.11655 | 0.000104 | 2.6065e-05
90 | 0.98354 | -0.11612 | 0 | 0
91 | 0.98348 | -0.11657 | 0.00059097 | 0.00014811
92 | 0.98355 | -0.11606 | 0.00010021 | 2.5115e-05
93 | 0.98353 | -0.11622 | 8.9065e-05 | 2.2322e-05
94 | 0.98351 | -0.11632 | 0 | 0
95 | 0.98349 | -0.11648 | 8.2483e-05 | 2.0672e-05
96 | 0.98351 | -0.11638 | 0.00010302 | 2.5819e-05
97 | 0.98349 | -0.11652 | 0.00089631 | 0.00022464
98 | 0.98351 | -0.11636 | 0.00010962 | 2.7475e-05
99 | 0.98355 | -0.11609 | 9.6499e-05 | 2.4185e-05
100 | 0.98358 | -0.11588 | 0.00014993 | 3.7576e-05
101 | 0.98359 | -0.11577 | 9.3338e-05 | 2.3393e-05
102 | 0.98336 | -0.1175 | 0.00015664 | 3.9257e-05
103 | 0.98336 | -0.11749 | 0 | 0
104 | 0.98361 | -0.11561 | 8.237e-05 | 2.0644e-05
105 | 0.98363 | -0.11547 | 0 | 0
106 | 0.9837 | -0.11501 | 0.00010053 | 2.5196e-05
107 | 0.98357 | -0.11592 | 0.00011259 | 2.8217e-05
108 | 0.98371 | -0.11489 | 0.0001836 | 4.6014e-05
109 | 0.98384 | -0.11402 | 0.00010561 | 2.6468e-05
110 | 0.98394 | -0.11325 | 0 | 0
111 | 0.98387 | -0.1138 | 0.00010283 | 2.5772e-05
112 | 0.98388 | -0.11372 | 9.924e-05 | 2.4872e-05
113 | 0.98343 | -0.11698 | 0.00010159 | 2.5461e-05
114 | 0.98343 | -0.11694 | 0 | 0
115 | 0.98343 | -0.11698 | 8.8683e-05 | 2.2226e-05
116 | 0.98337 | -0.11737 | 0 | 0
117 | 0.98337 | -0.1174 | 0.00028662 | 7.1834e-05
118 | 0.98337 | -0.1174 | 0.00010747 | 2.6935e-05
119 | 0.98335 | -0.11754 | 0.00014569 | 3.6513e-05
120 | 0.98335 | -0.11755 | 0.00022248 | 5.5759e-05
121 | 0.98345 | -0.11686 | 0.0001286 | 3.223e-05
122 | 0.98344 | -0.11688 | 0.00011705 | 2.9337e-05
123 | 0.98345 | -0.11683 | 0.00012582 | 3.1533e-05
124 | 0.98345 | -0.11679 | 0.00011941 | 2.9928e-05
125 | 0.98346 | -0.11672 | 0.00012857 | 3.2223e-05
126 | 0.98344 | -0.1169 | 0.00023259 | 5.8293e-05
127 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.039002 | 0.0097907 | -0.038983 | -0.0097837 | 1.8469e-05 | 6.9938e-06 | 0.058767 | 0.058767 | 0.058767 | 0.98765 | -0.086386 | 0.98717 | -0.089797 | 21.7654
1 | -0.043828 | -0.011 | 0.043938 | 0.011042 | 0.00010988 | 4.1743e-05 | 0.066037 | 0.066037 | 0.066037 | 0.98765 | -0.086386 | 0.9902 | -0.068374 | 24.4583
2 | 0.035592 | 0.0089336 | -0.035531 | -0.0089109 | 6.021e-05 | 2.273e-05 | 0.053654 | 0.053654 | 0.053654 | 0.98717 | -0.089797 | 0.98544 | -0.102 | 19.8719
3 | -0.043938 | -0.011042 | 0.044063 | 0.01109 | 0.00012555 | 4.7695e-05 | 0.066037 | 0.066037 | 0.066037 | 0.9902 | -0.068374 | 0.99312 | -0.047904 | 24.4582
4 | 0.032436 | 0.008135 | -0.03243 | -0.008133 | 5.5011e-06 | 2.069e-06 | 0.04898 | 0.04898 | 0.04898 | 0.98544 | -0.102 | 0.98527 | -0.10322 | 18.1406
5 | -0.064403 | -0.016184 | 0.064835 | 0.01635 | 0.00043235 | 0.00016532 | 0.096511 | 0.096511 | 0.096511 | 0.99312 | -0.047904 | 1 | 0 | 35.7448
6 | 0.016294 | 0.0040809 | -0.016195 | -0.0040463 | 9.8855e-05 | 3.4603e-05 | 0.024413 | 0.024414 | 0.024414 | 0.99312 | -0.047904 | 0.98691 | -0.092027 | 9.0423
7 | 0.00069264 | 0.00017334 | -0.00069263 | -0.00017359 | 1.3404e-08 | -2.4652e-07 | 0.0010442 | 0.0010443 | 0.0010443 | 0.98691 | -0.092027 | 0.98689 | -0.092167 | 0.38679
8 | 0.014809 | 0.003699 | -0.0148 | -0.0036962 | 8.2953e-06 | 2.8498e-06 | 0.022323 | 0.022323 | 0.022323 | 0.98691 | -0.092027 | 0.98634 | -0.096102 | 8.2679
9 | 0.013698 | 0.0034199 | -0.013696 | -0.0034191 | 2.6129e-06 | 8.7979e-07 | 0.020661 | 0.020661 | 0.020661 | 0.98634 | -0.096102 | 0.98614 | -0.097491 | 7.6521
10 | 0.029132 | 0.0073065 | -0.029109 | -0.0072976 | 2.3608e-05 | 8.8315e-06 | 0.043999 | 0.043999 | 0.043999 | 0.98527 | -0.10322 | 0.98445 | -0.10907 | 16.296
11 | 0.0014085 | 0.00035295 | -0.0014085 | -0.000353 | 1.1784e-08 | -5.1868e-08 | 0.0020958 | 0.0020959 | 0.0020959 | 1 | 0 | 0.99999 | -6.0441e-05 | 0.77624
12 | 0.024813 | 0.006221 | -0.024811 | -0.0062202 | 2.3539e-06 | 8.7125e-07 | 0.037506 | 0.037506 | 0.037506 | 0.98445 | -0.10907 | 0.98435 | -0.10976 | 13.8912
13 | 0.02246 | 0.0056309 | -0.022446 | -0.0056258 | 1.3975e-05 | 5.1283e-06 | 0.033952 | 0.033952 | 0.033952 | 0.98435 | -0.10976 | 0.98372 | -0.11425 | 12.575
14 | 0.018719 | 0.0046919 | -0.018715 | -0.0046905 | 3.6785e-06 | 1.3215e-06 | 0.028315 | 0.028315 | 0.028315 | 0.98372 | -0.11425 | 0.98352 | -0.11567 | 10.4872
15 | 0.0081609 | 0.0020453 | -0.0081586 | -0.0020447 | 2.3349e-06 | 5.8666e-07 | 0.012347 | 0.012347 | 0.012347 | 0.98352 | -0.11567 | 0.98323 | -0.11774 | 4.573
16 | -0.00019662 | -4.9095e-05 | 0.00019662 | 4.8888e-05 | 8.987e-10 | -2.0685e-07 | 0.00029723 | 0.00029715 | 0.00029723 | 0.98414 | -0.11186 | 0.98414 | -0.11182 | 0.11008
17 | 0.00010655 | 2.6519e-05 | -0.00010655 | -2.6655e-05 | 1.7237e-10 | -1.3525e-07 | 0.00016103 | 0.00016108 | 0.00016108 | 0.98414 | -0.11186 | 0.98414 | -0.11187 | 0.059659
18 | -0.00030656 | -7.6442e-05 | 0.00030657 | 7.6268e-05 | 1.8404e-09 | -1.7385e-07 | 0.00046338 | 0.00046332 | 0.00046338 | 0.98414 | -0.11182 | 0.98415 | -0.11178 | 0.17162
19 | 0.00010655 | 2.6655e-05 | -0.00010655 | -2.6703e-05 | 6.1447e-11 | -4.8198e-08 | 0.00016108 | 0.0001611 | 0.0001611 | 0.98414 | -0.11187 | 0.98414 | -0.11187 | 0.059665
20 | -0.00039602 | -9.8688e-05 | 0.00039603 | 9.856e-05 | 2.2638e-09 | -1.278e-07 | 0.00059858 | 0.00059853 | 0.00059858 | 0.98415 | -0.11178 | 0.98416 | -0.11174 | 0.2217
21 | 0.00044767 | 0.00011137 | -0.00044767 | -0.00011151 | 3.0601e-09 | -1.3495e-07 | 0.00067657 | 0.00067662 | 0.00067662 | 0.98416 | -0.11174 | 0.98415 | -0.11179 | 0.2506
22 | -0.0008437 | -0.00020993 | 0.00084372 | 0.00020969 | 1.9992e-08 | -2.4272e-07 | 0.0012751 | 0.001275 | 0.0012751 | 0.98416 | -0.11174 | 0.98418 | -0.11156 | 0.47226
23 | 0.00032283 | 8.0217e-05 | -0.00032282 | -8.0395e-05 | 2.082e-09 | -1.773e-07 | 0.00048786 | 0.00048793 | 0.00048793 | 0.98415 | -0.11179 | 0.98414 | -0.11184 | 0.18071
24 | -0.00094704 | -0.00023558 | 0.00094705 | 0.00023549 | 9.6113e-09 | -9.1857e-08 | 0.0014312 | 0.0014312 | 0.0014312 | 0.98418 | -0.11156 | 0.98419 | -0.11149 | 0.53009
25 | -9.6768e-05 | -2.4252e-05 | 9.6768e-05 | 2.4089e-05 | 1.7212e-10 | -1.6373e-07 | 0.00014631 | 0.00014625 | 0.00014631 | 0.98417 | -0.11166 | 0.98417 | -0.11165 | 0.054188
26 | -0.00021593 | -5.3954e-05 | 0.00021593 | 5.3936e-05 | 9.7477e-11 | -1.8591e-08 | 0.00032642 | 0.00032642 | 0.00032642 | 0.98417 | -0.11165 | 0.98417 | -0.11164 | 0.1209
27 | -0.00013515 | -3.3873e-05 | 0.00013515 | 3.38e-05 | 1.4881e-10 | -7.2563e-08 | 0.00020432 | 0.0002043 | 0.00020432 | 0.98427 | -0.11095 | 0.98427 | -0.11094 | 0.075676
28 | -0.00023338 | -5.8418e-05 | 0.00023338 | 5.8006e-05 | 2.5223e-09 | -4.1196e-07 | 0.0003528 | 0.00035265 | 0.0003528 | 0.98427 | -0.11094 | 0.98428 | -0.11086 | 0.13067
29 | -0.00029942 | -7.4859e-05 | 0.00029942 | 7.4677e-05 | 1.8373e-09 | -1.8194e-07 | 0.00045264 | 0.00045258 | 0.00045264 | 0.98417 | -0.11164 | 0.98418 | -0.1116 | 0.16765
30 | -0.00038292 | -9.5603e-05 | 0.00038292 | 9.5382e-05 | 3.6654e-09 | -2.2142e-07 | 0.00057882 | 0.00057874 | 0.00057882 | 0.98418 | -0.1116 | 0.98419 | -0.11153 | 0.21438
31 | -0.00048383 | -0.00012067 | 0.00048383 | 0.00012057 | 2.5971e-09 | -9.79e-08 | 0.00073131 | 0.00073127 | 0.00073131 | 0.98419 | -0.11153 | 0.98419 | -0.11149 | 0.27085
32 | -0.0020046 | -0.00049945 | 0.0020047 | 0.00049936 | 5.0062e-08 | -9.1813e-08 | 0.0030298 | 0.0030297 | 0.0030298 | 0.98419 | -0.11149 | 0.98422 | -0.11131 | 1.1221
33 | 0.00057374 | 0.00014338 | -0.00057373 | -0.0001435 | 4.3673e-09 | -1.1655e-07 | 0.0008673 | 0.00086734 | 0.00086734 | 0.98419 | -0.11149 | 0.98418 | -0.11155 | 0.32124
34 | -0.0021161 | -0.00052729 | 0.0021162 | 0.00052714 | 9.4284e-08 | -1.5147e-07 | 0.0031982 | 0.0031982 | 0.0031982 | 0.98422 | -0.11131 | 0.98426 | -0.11098 | 1.1845
35 | 0.00047726 | 0.00011932 | -0.00047725 | -0.00011944 | 3.0693e-09 | -1.1889e-07 | 0.00072148 | 0.00072152 | 0.00072152 | 0.98418 | -0.11155 | 0.98418 | -0.11159 | 0.26723
36 | 0.00023911 | 5.9414e-05 | -0.00023911 | -5.957e-05 | 1.007e-09 | -1.5664e-07 | 0.00036135 | 0.0003614 | 0.0003614 | 0.98414 | -0.11184 | 0.98414 | -0.11187 | 0.13385
37 | 0.00012241 | 3.0323e-05 | -0.00012241 | -3.0679e-05 | 5.982e-10 | -3.556e-07 | 0.00018496 | 0.00018508 | 0.00018508 | 0.98414 | -0.11187 | 0.98413 | -0.1119 | 0.06855
38 | -8.6957e-05 | -2.1794e-05 | 8.6957e-05 | 2.1643e-05 | 1.2769e-10 | -1.505e-07 | 0.00013146 | 0.00013141 | 0.00013146 | 0.98428 | -0.11087 | 0.98428 | -0.11086 | 0.048689
39 | -0.00043125 | -0.00010737 | 0.00043126 | 0.00010727 | 2.1777e-09 | -1.036e-07 | 0.00065171 | 0.00065167 | 0.00065171 | 0.98428 | -0.11086 | 0.98428 | -0.11082 | 0.24137
40 | 0.00011091 | 2.7724e-05 | -0.00011091 | -2.7798e-05 | 1.0198e-10 | -7.3853e-08 | 0.00016765 | 0.00016768 | 0.00016768 | 0.98428 | -0.11086 | 0.98428 | -0.11087 | 0.062103
41 | -0.00053919 | -0.00013432 | 0.00053919 | 0.00013422 | 3.3719e-09 | -1.0215e-07 | 0.00081484 | 0.0008148 | 0.00081484 | 0.98428 | -0.11082 | 0.98429 | -0.11078 | 0.30179
42 | -0.00064569 | -0.00016091 | 0.0006457 | 0.00016073 | 8.3823e-09 | -1.761e-07 | 0.00097581 | 0.00097575 | 0.00097581 | 0.98429 | -0.11078 | 0.9843 | -0.11068 | 0.36141
43 | -0.00073322 | -0.00018267 | 0.00073323 | 0.00018264 | 1.954e-09 | -3.1667e-08 | 0.0011081 | 0.001108 | 0.0011081 | 0.9843 | -0.11068 | 0.98431 | -0.11066 | 0.41039
44 | -0.0026609 | -0.00066096 | 0.0026612 | 0.00066073 | 2.7158e-07 | -2.3694e-07 | 0.0040231 | 0.004023 | 0.0040231 | 0.98367 | -0.11525 | 0.98377 | -0.1145 | 1.49
45 | 0.0026609 | 0.00066096 | -0.0026605 | -0.0006613 | 3.8645e-07 | -3.37e-07 | 0.0040231 | 0.0040233 | 0.0040233 | 0.98367 | -0.11525 | 0.98352 | -0.11631 | 1.4901
46 | -0.0028144 | -0.00069913 | 0.0028145 | 0.00069905 | 1.0291e-07 | -7.6101e-08 | 0.0042547 | 0.0042547 | 0.0042547 | 0.98377 | -0.1145 | 0.98381 | -0.11423 | 1.5758
47 | 0.00084738 | 0.00021108 | -0.00084735 | -0.00021143 | 2.9425e-08 | -3.5298e-07 | 0.0012816 | 0.0012817 | 0.0012817 | 0.98352 | -0.11631 | 0.98349 | -0.11657 | 0.47471
48 | 0.00040855 | 0.0001003 | -0.00040853 | -0.00010175 | 2.7363e-08 | -1.4482e-06 | 0.00061738 | 0.0006179 | 0.0006179 | 0.98352 | -0.11631 | 0.98345 | -0.11681 | 0.22885
49 | 0.0014046 | 0.00034992 | -0.0014045 | -0.00035008 | 3.8951e-08 | -1.6055e-07 | 0.0021243 | 0.0021244 | 0.0021244 | 0.98352 | -0.11631 | 0.98349 | -0.11652 | 0.7868
50 | -0.0022106 | -0.00055081 | 0.0022106 | 0.0005508 | 1.7983e-09 | -2.5898e-09 | 0.0033409 | 0.0033409 | 0.0033409 | 0.98426 | -0.11098 | 0.98426 | -0.11098 | 1.2374
51 | 0.00037931 | 9.4894e-05 | -0.0003793 | -9.5035e-05 | 2.2971e-09 | -1.4137e-07 | 0.00057343 | 0.00057348 | 0.00057348 | 0.98418 | -0.11159 | 0.98417 | -0.11164 | 0.2124
52 | 0.00026122 | 6.544e-05 | -0.00026122 | -6.5467e-05 | 2.0964e-10 | -2.7282e-08 | 0.00039494 | 0.00039495 | 0.00039495 | 0.98417 | -0.11164 | 0.98417 | -0.11164 | 0.14628
53 | -0.0001089 | -2.7293e-05 | 0.0001089 | 2.7252e-05 | 5.5041e-11 | -4.1503e-08 | 0.00016447 | 0.00016445 | 0.00016447 | 0.98528 | -0.10369 | 0.98528 | -0.10369 | 0.060914
54 | -0.00023766 | -5.9522e-05 | 0.00023766 | 5.9438e-05 | 5.3475e-10 | -8.4526e-08 | 0.00035891 | 0.00035888 | 0.00035891 | 0.98528 | -0.10369 | 0.98528 | -0.10367 | 0.13293
55 | 0.013696 | 0.0034191 | -0.013691 | -0.0034174 | 4.8431e-06 | 1.6308e-06 | 0.020661 | 0.020661 | 0.020661 | 0.98614 | -0.097491 | 0.98578 | -0.10007 | 7.6522
56 | 0.013536 | 0.0033787 | -0.013535 | -0.0033783 | 1.4413e-06 | 4.838e-07 | 0.020428 | 0.020428 | 0.020428 | 0.98578 | -0.10007 | 0.98567 | -0.10084 | 7.5659
57 | -0.0023031 | -0.00057398 | 0.0023032 | 0.00057385 | 9.8252e-08 | -1.274e-07 | 0.0034807 | 0.0034807 | 0.0034807 | 0.98426 | -0.11098 | 0.98431 | -0.11066 | 1.2892
58 | -0.0030364 | -0.00075649 | 0.0030367 | 0.00075635 | 2.4621e-07 | -1.4351e-07 | 0.0045887 | 0.0045886 | 0.0045887 | 0.98431 | -0.11066 | 0.98439 | -0.11007 | 1.6995
59 | -0.0031254 | -0.00077858 | 0.0031256 | 0.00077847 | 2.2448e-07 | -1.1872e-07 | 0.0047228 | 0.0047227 | 0.0047228 | 0.98439 | -0.11007 | 0.98446 | -0.10955 | 1.7492
60 | -0.0032076 | -0.00079899 | 0.0032076 | 0.00079898 | 4.0084e-08 | -1.9356e-08 | 0.0048465 | 0.0048465 | 0.0048465 | 0.98446 | -0.10955 | 0.98447 | -0.10946 | 1.795
61 | -0.0033639 | -0.00083815 | 0.0033642 | 0.00083805 | 2.6816e-07 | -1.0839e-07 | 0.0050828 | 0.0050827 | 0.0050828 | 0.98447 | -0.10946 | 0.98455 | -0.10887 | 1.8825
62 | 0.0089168 | 0.0022255 | -0.0089158 | -0.0022253 | 1.0359e-06 | 2.8213e-07 | 0.013473 | 0.013473 | 0.013473 | 0.98455 | -0.10887 | 0.98444 | -0.10972 | 4.9901
63 | -0.012509 | -0.0031206 | 0.012512 | 0.0031215 | 2.6903e-06 | 8.8123e-07 | 0.018901 | 0.018901 | 0.018901 | 0.98455 | -0.10887 | 0.98477 | -0.10731 | 7.0004
64 | 0.00022844 | 5.6986e-05 | -0.00022844 | -5.7091e-05 | 6.132e-10 | -1.0465e-07 | 0.00034516 | 0.0003452 | 0.0003452 | 0.98455 | -0.10887 | 0.98455 | -0.10889 | 0.12785
65 | 0.0088173 | 0.0022006 | -0.008816 | -0.0022002 | 1.2455e-06 | 3.3611e-07 | 0.013324 | 0.013324 | 0.013324 | 0.98444 | -0.10972 | 0.98429 | -0.11075 | 4.935
66 | -0.012616 | -0.0031476 | 0.012617 | 0.0031477 | 3.2088e-07 | 1.054e-07 | 0.019059 | 0.019059 | 0.019059 | 0.98477 | -0.10731 | 0.9848 | -0.10712 | 7.0588
67 | 0.00010984 | 2.7366e-05 | -0.00010984 | -2.7527e-05 | 2.1869e-10 | -1.6171e-07 | 0.00016594 | 0.000166 | 0.000166 | 0.98455 | -0.10889 | 0.98455 | -0.10891 | 0.061482
68 | 0.0086978 | 0.0021706 | -0.0086976 | -0.0021705 | 2.5532e-07 | 6.8107e-08 | 0.013146 | 0.013146 | 0.013146 | 0.98429 | -0.11075 | 0.98426 | -0.11096 | 4.8688
69 | -0.012732 | -0.0031766 | 0.012736 | 0.0031778 | 3.6766e-06 | 1.2113e-06 | 0.019233 | 0.019233 | 0.019233 | 0.9848 | -0.10712 | 0.98509 | -0.10502 | 7.1232
70 | -0.0029172 | -0.00072478 | 0.0029173 | 0.00072472 | 9.8636e-08 | -6.5275e-08 | 0.00441 | 0.0044099 | 0.00441 | 0.98381 | -0.11423 | 0.98384 | -0.11398 | 1.6333
71 | 0.0007396 | 0.00018442 | -0.00073959 | -0.00018465 | 1.4459e-08 | -2.2937e-07 | 0.0011187 | 0.0011188 | 0.0011188 | 0.98349 | -0.11657 | 0.98347 | -0.11671 | 0.41436
72 | 0.00017593 | 4.3952e-05 | -0.00017593 | -4.4093e-05 | 4.9093e-10 | -1.4072e-07 | 0.00026615 | 0.0002662 | 0.0002662 | 0.98345 | -0.11681 | 0.98345 | -0.11683 | 0.098591
73 | 0.00023259 | 5.7799e-05 | -0.00023259 | -5.813e-05 | 2.0195e-09 | -3.3102e-07 | 0.00035175 | 0.00035187 | 0.00035187 | 0.98345 | -0.11681 | 0.98344 | -0.11687 | 0.13032
74 | 0.0012756 | 0.00031776 | -0.0012755 | -0.00031802 | 5.0125e-08 | -2.5456e-07 | 0.0019293 | 0.0019294 | 0.0019294 | 0.98349 | -0.11652 | 0.98345 | -0.1168 | 0.71458
75 | 0.0085892 | 0.0021434 | -0.0085886 | -0.0021432 | 5.4443e-07 | 1.436e-07 | 0.012982 | 0.012982 | 0.012982 | 0.98426 | -0.11096 | 0.9842 | -0.11142 | 4.8081
76 | -0.012848 | -0.0032059 | 0.01285 | 0.0032067 | 2.5333e-06 | 8.3703e-07 | 0.019402 | 0.019402 | 0.019402 | 0.98509 | -0.10502 | 0.98529 | -0.10358 | 7.1859
77 | -0.0030331 | -0.00075375 | 0.0030332 | 0.00075369 | 1.0544e-07 | -6.1514e-08 | 0.0045851 | 0.0045851 | 0.0045851 | 0.98384 | -0.11398 | 0.98388 | -0.11372 | 1.6982
78 | 0.00061946 | 0.00015455 | -0.00061946 | -0.00015457 | 1.1525e-09 | -2.6251e-08 | 0.00093702 | 0.00093703 | 0.00093703 | 0.98347 | -0.11671 | 0.98346 | -0.11672 | 0.34705
79 | 0.00023259 | 5.813e-05 | -0.00023259 | -5.8293e-05 | 9.9131e-10 | -1.624e-07 | 0.00035187 | 0.00035193 | 0.00035193 | 0.98344 | -0.11687 | 0.98344 | -0.1169 | 0.13034
80 | 0.0011093 | 0.00027635 | -0.0011092 | -0.00027649 | 2.0747e-08 | -1.4189e-07 | 0.0016778 | 0.0016778 | 0.0016778 | 0.98345 | -0.1168 | 0.98343 | -0.11694 | 0.62142
81 | 0.008499 | 0.0021208 | -0.0084978 | -0.0021205 | 1.2302e-06 | 3.2136e-07 | 0.012846 | 0.012846 | 0.012846 | 0.9842 | -0.11142 | 0.98405 | -0.11248 | 4.7579
82 | 0.0084146 | 0.0020996 | -0.0084137 | -0.0020994 | 8.9663e-07 | 2.3206e-07 | 0.012721 | 0.012721 | 0.012721 | 0.98405 | -0.11248 | 0.98394 | -0.11325 | 4.7114
83 | -0.00037714 | -9.4395e-05 | 0.00037714 | 9.4289e-05 | 1.6968e-09 | -1.0612e-07 | 0.00056953 | 0.0005695 | 0.00056953 | 0.98528 | -0.10367 | 0.98528 | -0.10364 | 0.21094
84 | 0.01344 | 0.0033544 | -0.013435 | -0.0033527 | 5.0517e-06 | 1.6923e-06 | 0.020284 | 0.020284 | 0.020284 | 0.98567 | -0.10084 | 0.98529 | -0.10358 | 7.5128
85 | 0.00010615 | 2.6517e-05 | -0.00010615 | -2.6604e-05 | 1.0839e-10 | -8.606e-08 | 0.00016028 | 0.00016031 | 0.00016031 | 0.98529 | -0.10358 | 0.98529 | -0.10359 | 0.059374
86 | 0.00047836 | 0.0001195 | -0.00047836 | -0.00011966 | 3.918e-09 | -1.5176e-07 | 0.0007223 | 0.00072236 | 0.00072236 | 0.98529 | -0.10358 | 0.98528 | -0.10364 | 0.26754
87 | 0.00083688 | 0.0002094 | -0.00083686 | -0.00020967 | 2.2284e-08 | -2.7413e-07 | 0.001266 | 0.0012662 | 0.0012662 | 0.98351 | -0.11635 | 0.98348 | -0.11654 | 0.46894
88 | -0.00083688 | -0.0002094 | 0.0008369 | 0.00020924 | 1.3111e-08 | -1.6132e-07 | 0.001266 | 0.001266 | 0.001266 | 0.98351 | -0.11635 | 0.98353 | -0.11623 | 0.46891
89 | 0.00069498 | 0.00017411 | -0.00069498 | -0.00017413 | 9.2208e-10 | -1.6605e-08 | 0.0010515 | 0.0010515 | 0.0010515 | 0.98348 | -0.11654 | 0.98348 | -0.11655 | 0.38944
90 | -0.00093008 | -0.00023259 | 0.00093009 | 0.00023245 | 1.4282e-08 | -1.4124e-07 | 0.001407 | 0.0014069 | 0.001407 | 0.98353 | -0.11623 | 0.98354 | -0.11612 | 0.5211
91 | -0.00063841 | -0.00016 | 0.00063842 | 0.00015976 | 1.1221e-08 | -2.4025e-07 | 0.00096596 | 0.00096587 | 0.00096596 | 0.98345 | -0.11678 | 0.98347 | -0.11666 | 0.35776
92 | -0.0019408 | -0.00048617 | 0.0019409 | 0.00048599 | 9.012e-08 | -1.7789e-07 | 0.0029364 | 0.0029363 | 0.0029364 | 0.98347 | -0.11666 | 0.98351 | -0.11632 | 1.0876
93 | 0.00059097 | 0.00014806 | -0.00059097 | -0.00014811 | 1.9022e-09 | -4.7652e-08 | 0.00089413 | 0.00089415 | 0.00089415 | 0.98348 | -0.11655 | 0.98348 | -0.11657 | 0.33117
94 | -0.0022107 | -0.00055295 | 0.0022107 | 0.00055292 | 1.967e-08 | -2.8207e-08 | 0.0033441 | 0.0033441 | 0.0033441 | 0.98354 | -0.11612 | 0.98355 | -0.11606 | 1.2386
95 | 0.0012806 | 0.0003205 | -0.0012805 | -0.00032059 | 1.7845e-08 | -8.9844e-08 | 0.0019372 | 0.0019373 | 0.0019373 | 0.98354 | -0.11612 | 0.98353 | -0.11622 | 0.7175
96 | -0.0023109 | -0.00057804 | 0.0023109 | 0.00057798 | 4.4563e-08 | -5.703e-08 | 0.0034957 | 0.0034957 | 0.0034957 | 0.98355 | -0.11606 | 0.98357 | -0.11592 | 1.2947
97 | 0.0011915 | 0.00029827 | -0.0011915 | -0.0002984 | 2.2284e-08 | -1.3091e-07 | 0.0018025 | 0.0018026 | 0.0018026 | 0.98353 | -0.11622 | 0.98351 | -0.11636 | 0.66761
98 | -0.0019409 | -0.00048599 | 0.001941 | 0.00048587 | 6.1927e-08 | -1.2226e-07 | 0.0029363 | 0.0029363 | 0.0029363 | 0.98351 | -0.11632 | 0.98355 | -0.11609 | 1.0875
99 | -0.0009788 | -0.00024525 | 0.00097881 | 0.00024513 | 1.4164e-08 | -1.259e-07 | 0.0014809 | 0.0014808 | 0.0014809 | 0.98349 | -0.11648 | 0.98351 | -0.11638 | 0.54848
100 | 0.00089631 | 0.00022458 | -0.00089631 | -0.00022464 | 5.2694e-09 | -5.6243e-08 | 0.0013561 | 0.0013561 | 0.0013561 | 0.98349 | -0.11648 | 0.98349 | -0.11652 | 0.50226
101 | -0.0010818 | -0.00027094 | 0.0010818 | 0.00027093 | 2.6036e-09 | -1.8764e-08 | 0.0016367 | 0.0016367 | 0.0016367 | 0.98351 | -0.11638 | 0.98351 | -0.11636 | 0.60619
102 | -0.0020375 | -0.00051005 | 0.0020375 | 0.00050995 | 5.9414e-08 | -1.0435e-07 | 0.0030823 | 0.0030822 | 0.0030823 | 0.98355 | -0.11609 | 0.98358 | -0.11588 | 1.1416
103 | -0.0021874 | -0.00054753 | 0.0021875 | 0.00054748 | 3.1434e-08 | -4.6301e-08 | 0.0033091 | 0.003309 | 0.0033091 | 0.98358 | -0.11588 | 0.98359 | -0.11577 | 1.2256
104 | -0.0022808 | -0.00057087 | 0.0022809 | 0.0005708 | 5.1896e-08 | -6.8715e-08 | 0.0034502 | 0.0034502 | 0.0034502 | 0.98359 | -0.11577 | 0.98361 | -0.11561 | 1.2779
105 | -0.00015664 | -3.9257e-05 | 0.00015664 | 3.9177e-05 | 2.2213e-10 | -8.0303e-08 | 0.00023702 | 0.000237 | 0.00023702 | 0.98336 | -0.1175 | 0.98336 | -0.11749 | 0.087787
106 | -0.00052481 | -0.00013126 | 0.00052482 | 0.00013105 | 6.8039e-09 | -2.1679e-07 | 0.00079405 | 0.00079397 | 0.00079405 | 0.98336 | -0.11749 | 0.98337 | -0.1174 | 0.29409
107 | 0.00036817 | 9.2087e-05 | -0.00036817 | -9.2233e-05 | 2.2415e-09 | -1.4598e-07 | 0.00055705 | 0.00055711 | 0.00055711 | 0.98336 | -0.11749 | 0.98335 | -0.11754 | 0.20634
108 | -0.0023632 | -0.00059145 | 0.0023633 | 0.00059139 | 4.6373e-08 | -5.5979e-08 | 0.0035748 | 0.0035748 | 0.0035748 | 0.98361 | -0.11561 | 0.98363 | -0.11547 | 1.324
109 | -0.004787 | -0.0011974 | 0.0047873 | 0.0011974 | 3.0161e-07 | -1.0272e-09 | 0.0072408 | 0.0072407 | 0.0072408 | 0.98363 | -0.11547 | 0.9837 | -0.11501 | 2.6818
110 | 0.0024237 | 0.00060603 | -0.0024235 | -0.0006062 | 1.5084e-07 | -1.7028e-07 | 0.003666 | 0.003666 | 0.003666 | 0.98363 | -0.11547 | 0.98357 | -0.11592 | 1.3578
111 | -0.0048878 | -0.0012226 | 0.0048879 | 0.0012226 | 8.1829e-08 | 1.0114e-09 | 0.0073928 | 0.0073928 | 0.0073928 | 0.9837 | -0.11501 | 0.98371 | -0.11489 | 2.7381
112 | -0.0050715 | -0.0012686 | 0.0050721 | 0.0012687 | 6.0669e-07 | 2.3525e-08 | 0.0076705 | 0.0076704 | 0.0076705 | 0.98371 | -0.11489 | 0.98384 | -0.11402 | 2.8409
113 | -0.0051777 | -0.0012951 | 0.0051778 | 0.0012951 | 1.5593e-07 | 8.2153e-09 | 0.0078301 | 0.0078301 | 0.0078301 | 0.98384 | -0.11402 | 0.98387 | -0.1138 | 2.9001
114 | 0.0052811 | 0.0013209 | -0.0052807 | -0.0013209 | 3.9953e-07 | 2.615e-08 | 0.0079856 | 0.0079857 | 0.0079857 | 0.98394 | -0.11325 | 0.98387 | -0.1138 | 2.9577
115 | 0.0031327 | 0.00077846 | -0.0031325 | -0.00077856 | 1.996e-07 | -1.0442e-07 | 0.0047351 | 0.0047352 | 0.0047352 | 0.98394 | -0.11325 | 0.98388 | -0.11372 | 1.7538
116 | -0.00019027 | -4.768e-05 | 0.00019027 | 4.7435e-05 | 1.0016e-09 | -2.454e-07 | 0.0002879 | 0.00028781 | 0.0002879 | 0.98343 | -0.11698 | 0.98343 | -0.11694 | 0.10663
117 | 8.8683e-05 | 2.2219e-05 | -8.8683e-05 | -2.2226e-05 | 5.9446e-12 | -6.8472e-09 | 0.00013418 | 0.00013419 | 0.00013419 | 0.98343 | -0.11698 | 0.98343 | -0.11698 | 0.049698
118 | 0.00091897 | 0.00022905 | -0.00091892 | -0.0002296 | 5.4215e-08 | -5.4958e-07 | 0.00139 | 0.0013902 | 0.0013902 | 0.98343 | -0.11694 | 0.98337 | -0.11737 | 0.5149
119 | 0.00028662 | 7.1681e-05 | -0.00028662 | -7.1834e-05 | 1.4282e-09 | -1.5383e-07 | 0.00043366 | 0.00043371 | 0.00043371 | 0.98337 | -0.11737 | 0.98337 | -0.1174 | 0.16063
120 | 0.00063229 | 0.00015792 | -0.00063229 | -0.00015798 | 2.7151e-09 | -5.9281e-08 | 0.00095658 | 0.0009566 | 0.0009566 | 0.98337 | -0.11737 | 0.98337 | -0.1174 | 0.3543
121 | 0.00022248 | 5.572e-05 | -0.00022248 | -5.5759e-05 | 2.1853e-10 | -3.911e-08 | 0.00033665 | 0.00033666 | 0.00033666 | 0.98335 | -0.11754 | 0.98335 | -0.11755 | 0.12469
122 | 0.00011706 | 2.9084e-05 | -0.00011705 | -2.9337e-05 | 3.9031e-10 | -2.5299e-07 | 0.00017702 | 0.00017711 | 0.00017711 | 0.98345 | -0.11686 | 0.98344 | -0.11688 | 0.065597
123 | -0.00024565 | -6.1313e-05 | 0.00024565 | 6.1185e-05 | 8.7345e-10 | -1.283e-07 | 0.0003716 | 0.00037155 | 0.0003716 | 0.98345 | -0.11686 | 0.98345 | -0.11683 | 0.13763
124 | -0.00037147 | -9.2718e-05 | 0.00037148 | 9.2598e-05 | 1.8879e-09 | -1.2086e-07 | 0.00056193 | 0.00056188 | 0.00056193 | 0.98345 | -0.11683 | 0.98345 | -0.11679 | 0.20812
125 | -0.00049089 | -0.00012253 | 0.00049089 | 0.00012235 | 4.7789e-09 | -1.7442e-07 | 0.00074256 | 0.0007425 | 0.00074256 | 0.98345 | -0.11679 | 0.98346 | -0.11672 | 0.27502

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.068734 | 0.017126

## res_load
| p_mw | q_mvar
0 | 0.0048259 | 0.0012095
1 | 0.0033918 | 0.00085006
2 | 0.0030957 | 0.00077586
3 | 0.0040452 | 0.0010138
4 | 0.00069419 | 0.00017398
5 | 0.00069263 | 0.00017359
6 | 0.0011021 | 0.00027622
7 | 0.0032979 | 0.00082652
8 | 0.0016908 | 0.00042376
9 | 0.0042956 | 0.0010766
10 | 0.0014085 | 0.000353
11 | 0.0023511 | 0.00058923
12 | 0.0037266 | 0.00093396
13 | 0.010554 | 0.0026452
14 | 0.0081586 | 0.0020447
15 | 9.0077e-05 | 2.2575e-05
16 | 0.00010994 | 2.7554e-05
17 | 8.9459e-05 | 2.2421e-05
18 | 0.00010655 | 2.6703e-05
19 | 0.00012484 | 3.1288e-05
20 | 0.00010333 | 2.5896e-05
21 | 9.6768e-05 | 2.4252e-05
22 | 0.00011917 | 2.9866e-05
23 | 0.00013515 | 3.3873e-05
24 | 9.8226e-05 | 2.4618e-05
25 | 8.3486e-05 | 2.0924e-05
26 | 8.3496e-05 | 2.0926e-05
27 | 0.00010091 | 2.529e-05
28 | 0.00011146 | 2.7934e-05
29 | 9.6474e-05 | 2.4179e-05
30 | 8.3715e-05 | 2.0981e-05
31 | 0.0001167 | 2.9247e-05
32 | 8.6957e-05 | 2.1794e-05
33 | 0.00010793 | 2.705e-05
34 | 0.00011091 | 2.7798e-05
35 | 0.0001065 | 2.6692e-05
36 | 8.7522e-05 | 2.1935e-05
37 | 0.00015322 | 3.84e-05
38 | 9.4422e-05 | 2.3664e-05
39 | 9.7947e-05 | 2.4548e-05
40 | 0.00011809 | 2.9596e-05
41 | 0.00026122 | 6.5467e-05
42 | 0.0001089 | 2.7293e-05
43 | 0.00012876 | 3.2271e-05
44 | 0.00012241 | 3.0679e-05
45 | 0.00015432 | 3.8676e-05
46 | 9.2474e-05 | 2.3176e-05
47 | 8.8734e-05 | 2.2239e-05
48 | 8.1911e-05 | 2.0529e-05
49 | 0.00015632 | 3.9179e-05
50 | 9.8517e-05 | 2.4691e-05
51 | 0.00010432 | 2.6144e-05
52 | 0.0001186 | 2.9725e-05
53 | 0.00011821 | 2.9626e-05
54 | 0.0001151 | 2.8846e-05
55 | 0.00010984 | 2.7527e-05
56 | 0.00010267 | 2.5733e-05
57 | 0.00010775 | 2.7005e-05
58 | 0.00012895 | 3.2319e-05
59 | 0.00010839 | 2.7165e-05
60 | 0.00011216 | 2.8111e-05
61 | 0.00011584 | 2.9033e-05
62 | 0.00012012 | 3.0105e-05
63 | 0.00017593 | 4.4093e-05
64 | 0.00016627 | 4.1671e-05
65 | 8.9627e-05 | 2.2463e-05
66 | 8.3154e-05 | 2.084e-05
67 | 0.00013948 | 3.4957e-05
68 | 9.5098e-05 | 2.3834e-05
69 | 0.00010122 | 2.5367e-05
70 | 0.00010615 | 2.6604e-05
71 | 0.00014188 | 3.5559e-05
72 | 9.3182e-05 | 2.3354e-05
73 | 0.00063841 | 0.00016
74 | 0.0013024 | 0.00032641
75 | 0.000104 | 2.6065e-05
76 | 0.00059097 | 0.00014811
77 | 0.00010021 | 2.5115e-05
78 | 8.9065e-05 | 2.2322e-05
79 | 8.2483e-05 | 2.0672e-05
80 | 0.00010302 | 2.5819e-05
81 | 0.00089631 | 0.00022464
82 | 0.00010962 | 2.7475e-05
83 | 9.6499e-05 | 2.4185e-05
84 | 0.00014993 | 3.7576e-05
85 | 9.3338e-05 | 2.3393e-05
86 | 0.00015664 | 3.9257e-05
87 | 8.237e-05 | 2.0644e-05
88 | 0.00010053 | 2.5196e-05
89 | 0.00011259 | 2.8217e-05
90 | 0.0001836 | 4.6014e-05
91 | 0.00010561 | 2.6468e-05
92 | 0.00010283 | 2.5772e-05
93 | 9.924e-05 | 2.4872e-05
94 | 0.00010159 | 2.5461e-05
95 | 8.8683e-05 | 2.2226e-05
96 | 0.00028662 | 7.1834e-05
97 | 0.00010747 | 2.6935e-05
98 | 0.00014569 | 3.6513e-05
99 | 0.00022248 | 5.5759e-05
100 | 0.0001286 | 3.223e-05
101 | 0.00011705 | 2.9337e-05
102 | 0.00012582 | 3.1533e-05
103 | 0.00011941 | 2.9928e-05
104 | 0.00012857 | 3.2223e-05
105 | 0.00023259 | 5.8293e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1