## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2022-7_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2022-7_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2022-7_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2022-7_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2022-7_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_2022-7_0_3_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_2022-7_0_3_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2022-7_0_3_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_2022-7_0_3_node_14 | 0.4 | n |  | TRUE
9 | bus_LV_2022-7_0_3_node_75 | 0.4 | n |  | TRUE
10 | bus_LV_2022-7_0_3_node_77 | 0.4 | n |  | TRUE
11 | bus_LV_2022-7_0_3_node_76 | 0.4 | n |  | TRUE
12 | bus_LV_2022-7_0_3_node_102 | 0.4 | n |  | TRUE
13 | bus_LV_2022-7_0_3_node_101 | 0.4 | n |  | TRUE
14 | bus_LV_2022-7_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2022-7_0_3_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_2022-7_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2022-7_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2022-7_0_3_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_2022-7_0_3_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2022-7_0_3_node_30 | 0.4 | n |  | TRUE
21 | bus_LV_2022-7_0_3_node_48 | 0.4 | n |  | TRUE
22 | bus_LV_2022-7_0_3_node_49 | 0.4 | n |  | TRUE
23 | bus_LV_2022-7_0_3_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_2022-7_0_3_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_2022-7_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_2022-7_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_2022-7_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_2022-7_0_3_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_2022-7_0_3_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_2022-7_0_3_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_2022-7_0_3_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_2022-7_0_3_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_2022-7_0_3_node_38 | 0.4 | n |  | TRUE
34 | bus_LV_2022-7_0_3_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_2022-7_0_3_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_2022-7_0_3_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_2022-7_0_3_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_2022-7_0_3_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_2022-7_0_3_node_47 | 0.4 | n |  | TRUE
40 | bus_LV_2022-7_0_3_node_46 | 0.4 | n |  | TRUE
41 | bus_LV_2022-7_0_3_node_52 | 0.4 | n |  | TRUE
42 | bus_LV_2022-7_0_3_node_45 | 0.4 | n |  | TRUE
43 | bus_LV_2022-7_0_3_node_32 | 0.4 | n |  | TRUE
44 | bus_LV_2022-7_0_3_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_2022-7_0_3_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_2022-7_0_3_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_2022-7_0_3_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_2022-7_0_3_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_2022-7_0_3_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_2022-7_0_3_node_43 | 0.4 | n |  | TRUE
51 | bus_LV_2022-7_0_3_node_44 | 0.4 | n |  | TRUE
52 | bus_LV_2022-7_0_3_node_41 | 0.4 | n |  | TRUE
53 | bus_LV_2022-7_0_3_node_53 | 0.4 | n |  | TRUE
54 | bus_LV_2022-7_0_3_node_51 | 0.4 | n |  | TRUE
55 | bus_LV_2022-7_0_3_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_2022-7_0_3_node_54 | 0.4 | n |  | TRUE
57 | bus_LV_2022-7_0_3_node_72 | 0.4 | n |  | TRUE
58 | bus_LV_2022-7_0_3_node_70 | 0.4 | n |  | TRUE
59 | bus_LV_2022-7_0_3_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_2022-7_0_3_node_56 | 0.4 | n |  | TRUE
61 | bus_LV_2022-7_0_3_node_57 | 0.4 | n |  | TRUE
62 | bus_LV_2022-7_0_3_node_58 | 0.4 | n |  | TRUE
63 | bus_LV_2022-7_0_3_node_59 | 0.4 | n |  | TRUE
64 | bus_LV_2022-7_0_3_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_2022-7_0_3_node_61 | 0.4 | n |  | TRUE
66 | bus_LV_2022-7_0_3_node_62 | 0.4 | n |  | TRUE
67 | bus_LV_2022-7_0_3_node_64 | 0.4 | n |  | TRUE
68 | bus_LV_2022-7_0_3_node_79 | 0.4 | n |  | TRUE
69 | bus_LV_2022-7_0_3_node_63 | 0.4 | n |  | TRUE
70 | bus_LV_2022-7_0_3_node_73 | 0.4 | n |  | TRUE
71 | bus_LV_2022-7_0_3_node_69 | 0.4 | n |  | TRUE
72 | bus_LV_2022-7_0_3_node_80 | 0.4 | n |  | TRUE
73 | bus_LV_2022-7_0_3_node_118 | 0.4 | n |  | TRUE
74 | bus_LV_2022-7_0_3_node_67 | 0.4 | n |  | TRUE
75 | bus_LV_2022-7_0_3_node_65 | 0.4 | n |  | TRUE
76 | bus_LV_2022-7_0_3_node_66 | 0.4 | n |  | TRUE
77 | bus_LV_2022-7_0_3_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_2022-7_0_3_node_71 | 0.4 | n |  | TRUE
79 | bus_LV_2022-7_0_3_node_126 | 0.4 | n |  | TRUE
80 | bus_LV_2022-7_0_3_node_127 | 0.4 | n |  | TRUE
81 | bus_LV_2022-7_0_3_node_115 | 0.4 | n |  | TRUE
82 | bus_LV_2022-7_0_3_node_78 | 0.4 | n |  | TRUE
83 | bus_LV_2022-7_0_3_node_82 | 0.4 | n |  | TRUE
84 | bus_LV_2022-7_0_3_node_92 | 0.4 | n |  | TRUE
85 | bus_LV_2022-7_0_3_node_83 | 0.4 | n |  | TRUE
86 | bus_LV_2022-7_0_3_node_81 | 0.4 | n |  | TRUE
87 | bus_LV_2022-7_0_3_node_100 | 0.4 | n |  | TRUE
88 | bus_LV_2022-7_0_3_node_84 | 0.4 | n |  | TRUE
89 | bus_LV_2022-7_0_3_node_85 | 0.4 | n |  | TRUE
90 | bus_LV_2022-7_0_3_node_86 | 0.4 | n |  | TRUE
91 | bus_LV_2022-7_0_3_node_87 | 0.4 | n |  | TRUE
92 | bus_LV_2022-7_0_3_node_88 | 0.4 | n |  | TRUE
93 | bus_LV_2022-7_0_3_node_89 | 0.4 | n |  | TRUE
94 | bus_LV_2022-7_0_3_node_90 | 0.4 | n |  | TRUE
95 | bus_LV_2022-7_0_3_node_91 | 0.4 | n |  | TRUE
96 | bus_LV_2022-7_0_3_node_93 | 0.4 | n |  | TRUE
97 | bus_LV_2022-7_0_3_node_94 | 0.4 | n |  | TRUE
98 | bus_LV_2022-7_0_3_node_95 | 0.4 | n |  | TRUE
99 | bus_LV_2022-7_0_3_node_96 | 0.4 | n |  | TRUE
100 | bus_LV_2022-7_0_3_node_97 | 0.4 | n |  | TRUE
101 | bus_LV_2022-7_0_3_node_107 | 0.4 | n |  | TRUE
102 | bus_LV_2022-7_0_3_node_104 | 0.4 | n |  | TRUE
103 | bus_LV_2022-7_0_3_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_2022-7_0_3_node_154 | 0.4 | n |  | TRUE
105 | bus_LV_2022-7_0_3_node_105 | 0.4 | n |  | TRUE
106 | bus_LV_2022-7_0_3_node_99 | 0.4 | n |  | TRUE
107 | bus_LV_2022-7_0_3_node_110 | 0.4 | n |  | TRUE
108 | bus_LV_2022-7_0_3_node_114 | 0.4 | n |  | TRUE
109 | bus_LV_2022-7_0_3_node_111 | 0.4 | n |  | TRUE
110 | bus_LV_2022-7_0_3_node_106 | 0.4 | n |  | TRUE
111 | bus_LV_2022-7_0_3_node_108 | 0.4 | n |  | TRUE
112 | bus_LV_2022-7_0_3_node_109 | 0.4 | n |  | TRUE
113 | bus_LV_2022-7_0_3_node_156 | 0.4 | n |  | TRUE
114 | bus_LV_2022-7_0_3_node_152 | 0.4 | n |  | TRUE
115 | bus_LV_2022-7_0_3_node_116 | 0.4 | n |  | TRUE
116 | bus_LV_2022-7_0_3_node_112 | 0.4 | n |  | TRUE
117 | bus_LV_2022-7_0_3_node_113 | 0.4 | n |  | TRUE
118 | bus_LV_2022-7_0_3_node_117 | 0.4 | n |  | TRUE
119 | bus_LV_2022-7_0_3_node_120 | 0.4 | n |  | TRUE
120 | bus_LV_2022-7_0_3_node_119 | 0.4 | n |  | TRUE
121 | bus_LV_2022-7_0_3_node_121 | 0.4 | n |  | TRUE
122 | bus_LV_2022-7_0_3_node_125 | 0.4 | n |  | TRUE
123 | bus_LV_2022-7_0_3_node_122 | 0.4 | n |  | TRUE
124 | bus_LV_2022-7_0_3_node_123 | 0.4 | n |  | TRUE
125 | bus_LV_2022-7_0_3_node_124 | 0.4 | n |  | TRUE
126 | bus_LV_2022-7_0_3_node_157 | 0.4 | n |  | TRUE
127 | bus_LV_2022-7_0_3_node_144 | 0.4 | n |  | TRUE
128 | bus_LV_2022-7_0_3_node_130 | 0.4 | n |  | TRUE
129 | bus_LV_2022-7_0_3_node_158 | 0.4 | n |  | TRUE
130 | bus_LV_2022-7_0_3_node_129 | 0.4 | n |  | TRUE
131 | bus_LV_2022-7_0_3_node_128 | 0.4 | n |  | TRUE
132 | bus_LV_2022-7_0_3_node_131 | 0.4 | n |  | TRUE
133 | bus_LV_2022-7_0_3_node_132 | 0.4 | n |  | TRUE
134 | bus_LV_2022-7_0_3_node_140 | 0.4 | n |  | TRUE
135 | bus_LV_2022-7_0_3_node_141 | 0.4 | n |  | TRUE
136 | bus_LV_2022-7_0_3_node_133 | 0.4 | n |  | TRUE
137 | bus_LV_2022-7_0_3_node_134 | 0.4 | n |  | TRUE
138 | bus_LV_2022-7_0_3_node_135 | 0.4 | n |  | TRUE
139 | bus_LV_2022-7_0_3_node_137 | 0.4 | n |  | TRUE
140 | bus_LV_2022-7_0_3_node_136 | 0.4 | n |  | TRUE
141 | bus_LV_2022-7_0_3_node_138 | 0.4 | n |  | TRUE
142 | bus_LV_2022-7_0_3_node_139 | 0.4 | n |  | TRUE
143 | bus_LV_2022-7_0_3_node_142 | 0.4 | n |  | TRUE
144 | bus_LV_2022-7_0_3_node_234 | 0.4 | n |  | TRUE
145 | bus_LV_2022-7_0_3_node_143 | 0.4 | n |  | TRUE
146 | bus_LV_2022-7_0_3_node_235 | 0.4 | n |  | TRUE
147 | bus_LV_2022-7_0_3_node_145 | 0.4 | n |  | TRUE
148 | bus_LV_2022-7_0_3_node_146 | 0.4 | n |  | TRUE
149 | bus_LV_2022-7_0_3_node_147 | 0.4 | n |  | TRUE
150 | bus_LV_2022-7_0_3_node_148 | 0.4 | n |  | TRUE
151 | bus_LV_2022-7_0_3_node_149 | 0.4 | n |  | TRUE
152 | bus_LV_2022-7_0_3_node_150 | 0.4 | n |  | TRUE
153 | bus_LV_2022-7_0_3_node_175 | 0.4 | n |  | TRUE
154 | bus_LV_2022-7_0_3_node_173 | 0.4 | n |  | TRUE
155 | bus_LV_2022-7_0_3_node_244 | 0.4 | n |  | TRUE
156 | bus_LV_2022-7_0_3_node_174 | 0.4 | n |  | TRUE
157 | bus_LV_2022-7_0_3_node_172 | 0.4 | n |  | TRUE
158 | bus_LV_2022-7_0_3_node_159 | 0.4 | n |  | TRUE
159 | bus_LV_2022-7_0_3_node_155 | 0.4 | n |  | TRUE
160 | bus_LV_2022-7_0_3_node_161 | 0.4 | n |  | TRUE
161 | bus_LV_2022-7_0_3_node_163 | 0.4 | n |  | TRUE
162 | bus_LV_2022-7_0_3_node_160 | 0.4 | n |  | TRUE
163 | bus_LV_2022-7_0_3_node_153 | 0.4 | n |  | TRUE
164 | bus_LV_2022-7_0_3_node_162 | 0.4 | n |  | TRUE
165 | bus_LV_2022-7_0_3_node_164 | 0.4 | n |  | TRUE
166 | bus_LV_2022-7_0_3_node_151 | 0.4 | n |  | TRUE
167 | bus_LV_2022-7_0_3_node_166 | 0.4 | n |  | TRUE
168 | bus_LV_2022-7_0_3_node_171 | 0.4 | n |  | TRUE
169 | bus_LV_2022-7_0_3_node_165 | 0.4 | n |  | TRUE
170 | bus_LV_2022-7_0_3_node_167 | 0.4 | n |  | TRUE
171 | bus_LV_2022-7_0_3_node_168 | 0.4 | n |  | TRUE
172 | bus_LV_2022-7_0_3_node_169 | 0.4 | n |  | TRUE
173 | bus_LV_2022-7_0_3_node_170 | 0.4 | n |  | TRUE
174 | bus_LV_2022-7_0_3_node_179 | 0.4 | n |  | TRUE
175 | bus_LV_2022-7_0_3_node_180 | 0.4 | n |  | TRUE
176 | bus_LV_2022-7_0_3_node_176 | 0.4 | n |  | TRUE
177 | bus_LV_2022-7_0_3_node_177 | 0.4 | n |  | TRUE
178 | bus_LV_2022-7_0_3_node_242 | 0.4 | n |  | TRUE
179 | bus_LV_2022-7_0_3_node_178 | 0.4 | n |  | TRUE
180 | bus_LV_2022-7_0_3_node_247 | 0.4 | n |  | TRUE
181 | bus_LV_2022-7_0_3_node_248 | 0.4 | n |  | TRUE
182 | bus_LV_2022-7_0_3_node_181 | 0.4 | n |  | TRUE
183 | bus_LV_2022-7_0_3_node_182 | 0.4 | n |  | TRUE
184 | bus_LV_2022-7_0_3_node_183 | 0.4 | n |  | TRUE
185 | bus_LV_2022-7_0_3_node_184 | 0.4 | n |  | TRUE
186 | bus_LV_2022-7_0_3_node_185 | 0.4 | n |  | TRUE
187 | bus_LV_2022-7_0_3_node_186 | 0.4 | n |  | TRUE
188 | bus_LV_2022-7_0_3_node_187 | 0.4 | n |  | TRUE
189 | bus_LV_2022-7_0_3_node_188 | 0.4 | n |  | TRUE
190 | bus_LV_2022-7_0_3_node_189 | 0.4 | n |  | TRUE
191 | bus_LV_2022-7_0_3_node_261 | 0.4 | n |  | TRUE
192 | bus_LV_2022-7_0_3_node_190 | 0.4 | n |  | TRUE
193 | bus_LV_2022-7_0_3_node_191 | 0.4 | n |  | TRUE
194 | bus_LV_2022-7_0_3_node_262 | 0.4 | n |  | TRUE
195 | bus_LV_2022-7_0_3_node_259 | 0.4 | n |  | TRUE
196 | bus_LV_2022-7_0_3_node_258 | 0.4 | n |  | TRUE
197 | bus_LV_2022-7_0_3_node_260 | 0.4 | n |  | TRUE
198 | bus_LV_2022-7_0_3_node_257 | 0.4 | n |  | TRUE
199 | bus_LV_2022-7_0_3_node_192 | 0.4 | n |  | TRUE
200 | bus_LV_2022-7_0_3_node_193 | 0.4 | n |  | TRUE
201 | bus_LV_2022-7_0_3_node_194 | 0.4 | n |  | TRUE
202 | bus_LV_2022-7_0_3_node_195 | 0.4 | n |  | TRUE
203 | bus_LV_2022-7_0_3_node_196 | 0.4 | n |  | TRUE
204 | bus_LV_2022-7_0_3_node_197 | 0.4 | n |  | TRUE
205 | bus_LV_2022-7_0_3_node_198 | 0.4 | n |  | TRUE
206 | bus_LV_2022-7_0_3_node_199 | 0.4 | n |  | TRUE
207 | bus_LV_2022-7_0_3_node_200 | 0.4 | n |  | TRUE
208 | bus_LV_2022-7_0_3_node_201 | 0.4 | n |  | TRUE
209 | bus_LV_2022-7_0_3_node_203 | 0.4 | n |  | TRUE
210 | bus_LV_2022-7_0_3_node_204 | 0.4 | n |  | TRUE
211 | bus_LV_2022-7_0_3_node_205 | 0.4 | n |  | TRUE
212 | bus_LV_2022-7_0_3_node_206 | 0.4 | n |  | TRUE
213 | bus_LV_2022-7_0_3_node_207 | 0.4 | n |  | TRUE
214 | bus_LV_2022-7_0_3_node_208 | 0.4 | n |  | TRUE
215 | bus_LV_2022-7_0_3_node_209 | 0.4 | n |  | TRUE
216 | bus_LV_2022-7_0_3_node_211 | 0.4 | n |  | TRUE
217 | bus_LV_2022-7_0_3_node_212 | 0.4 | n |  | TRUE
218 | bus_LV_2022-7_0_3_node_213 | 0.4 | n |  | TRUE
219 | bus_LV_2022-7_0_3_node_210 | 0.4 | n |  | TRUE
220 | bus_LV_2022-7_0_3_node_214 | 0.4 | n |  | TRUE
221 | bus_LV_2022-7_0_3_node_215 | 0.4 | n |  | TRUE
222 | bus_LV_2022-7_0_3_node_227 | 0.4 | n |  | TRUE
223 | bus_LV_2022-7_0_3_node_236 | 0.4 | n |  | TRUE
224 | bus_LV_2022-7_0_3_node_222 | 0.4 | n |  | TRUE
225 | bus_LV_2022-7_0_3_node_230 | 0.4 | n |  | TRUE
226 | bus_LV_2022-7_0_3_node_233 | 0.4 | n |  | TRUE
227 | bus_LV_2022-7_0_3_node_225 | 0.4 | n |  | TRUE
228 | bus_LV_2022-7_0_3_node_240 | 0.4 | n |  | TRUE
229 | bus_LV_2022-7_0_3_node_237 | 0.4 | n |  | TRUE
230 | bus_LV_2022-7_0_3_node_220 | 0.4 | n |  | TRUE
231 | bus_LV_2022-7_0_3_node_229 | 0.4 | n |  | TRUE
232 | bus_LV_2022-7_0_3_node_232 | 0.4 | n |  | TRUE
233 | bus_LV_2022-7_0_3_node_216 | 0.4 | n |  | TRUE
234 | bus_LV_2022-7_0_3_node_217 | 0.4 | n |  | TRUE
235 | bus_LV_2022-7_0_3_node_218 | 0.4 | n |  | TRUE
236 | bus_LV_2022-7_0_3_node_219 | 0.4 | n |  | TRUE
237 | bus_LV_2022-7_0_3_node_221 | 0.4 | n |  | TRUE
238 | bus_LV_2022-7_0_3_node_231 | 0.4 | n |  | TRUE
239 | bus_LV_2022-7_0_3_node_223 | 0.4 | n |  | TRUE
240 | bus_LV_2022-7_0_3_node_224 | 0.4 | n |  | TRUE
241 | bus_LV_2022-7_0_3_node_226 | 0.4 | n |  | TRUE
242 | bus_LV_2022-7_0_3_node_228 | 0.4 | n |  | TRUE
243 | bus_LV_2022-7_0_3_node_241 | 0.4 | n |  | TRUE
244 | bus_LV_2022-7_0_3_node_238 | 0.4 | n |  | TRUE
245 | bus_LV_2022-7_0_3_node_239 | 0.4 | n |  | TRUE
246 | bus_LV_2022-7_0_3_node_263 | 0.4 | n |  | TRUE
247 | bus_LV_2022-7_0_3_node_264 | 0.4 | n |  | TRUE
248 | bus_LV_2022-7_0_3_node_243 | 0.4 | n |  | TRUE
249 | bus_LV_2022-7_0_3_node_245 | 0.4 | n |  | TRUE
250 | bus_LV_2022-7_0_3_node_246 | 0.4 | n |  | TRUE
251 | bus_LV_2022-7_0_3_node_266 | 0.4 | n |  | TRUE
252 | bus_LV_2022-7_0_3_node_265 | 0.4 | n |  | TRUE
253 | bus_LV_2022-7_0_3_node_249 | 0.4 | n |  | TRUE
254 | bus_LV_2022-7_0_3_node_250 | 0.4 | n |  | TRUE
255 | bus_LV_2022-7_0_3_node_251 | 0.4 | n |  | TRUE
256 | bus_LV_2022-7_0_3_node_252 | 0.4 | n |  | TRUE
257 | bus_LV_2022-7_0_3_node_253 | 0.4 | n |  | TRUE
258 | bus_LV_2022-7_0_3_node_254 | 0.4 | n |  | TRUE
259 | bus_LV_2022-7_0_3_node_255 | 0.4 | n |  | TRUE
260 | bus_LV_2022-7_0_3_node_256 | 0.4 | n |  | TRUE
261 | bus_MV_377_0_node_10 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2022-7_0_3_load_0 | 0 | 0.00011366 | 2.8485e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2022-7_0_3_load_1 | 1 | 0.00010329 | 2.5886e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2022-7_0_3_load_2 | 2 | 9.4031e-05 | 2.3566e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2022-7_0_3_load_3 | 3 | 0.00016795 | 4.2093e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2022-7_0_3_load_5 | 4 | 0.00010018 | 2.5107e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2022-7_0_3_load_8 | 5 | 0.00011053 | 2.7701e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2022-7_0_3_load_7 | 6 | 0.00010409 | 2.6088e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2022-7_0_3_load_11 | 7 | 0.00011407 | 2.8588e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2022-7_0_3_load_14 | 8 | 8.7651e-05 | 2.1967e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2022-7_0_3_load_75 | 9 | 8.9536e-05 | 2.244e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2022-7_0_3_load_77 | 10 | 0.00015822 | 3.9653e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2022-7_0_3_load_102 | 12 | 0.00034619 | 8.6764e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2022-7_0_3_load_101 | 13 | 0.00016483 | 4.1309e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2022-7_0_3_load_9 | 14 | 8.5614e-05 | 2.1457e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2022-7_0_3_load_15 | 15 | 9.459e-05 | 2.3707e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2022-7_0_3_load_10 | 16 | 8.2478e-05 | 2.0671e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2022-7_0_3_load_12 | 17 | 9.5291e-05 | 2.3882e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2022-7_0_3_load_13 | 18 | 9.5709e-05 | 2.3987e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2022-7_0_3_load_16 | 19 | 8.3183e-05 | 2.0848e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2022-7_0_3_load_30 | 20 | 0.00010495 | 2.6303e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2022-7_0_3_load_48 | 21 | 8.8641e-05 | 2.2216e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2022-7_0_3_load_49 | 22 | 8.3416e-05 | 2.0906e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2022-7_0_3_load_28 | 23 | 9.4107e-05 | 2.3585e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2022-7_0_3_load_17 | 24 | 0.00011041 | 2.7671e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2022-7_0_3_load_18 | 25 | 0.00012344 | 3.0938e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2022-7_0_3_load_19 | 26 | 0.00011051 | 2.7695e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2022-7_0_3_load_21 | 28 | 0.00010824 | 2.7126e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2022-7_0_3_load_22 | 29 | 9.9529e-05 | 2.4944e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2022-7_0_3_load_23 | 30 | 8.6139e-05 | 2.1588e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2022-7_0_3_load_24 | 31 | 0.0001774 | 4.4461e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2022-7_0_3_load_25 | 32 | 9.7978e-05 | 2.4556e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2022-7_0_3_load_38 | 33 | 0.00027034 | 6.7754e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2022-7_0_3_load_39 | 34 | 0.00010313 | 2.5847e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2022-7_0_3_load_26 | 35 | 8.8929e-05 | 2.2288e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2022-7_0_3_load_27 | 36 | 0.0001122 | 2.812e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2022-7_0_3_load_29 | 37 | 0.00012663 | 3.1736e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2022-7_0_3_load_47 | 39 | 0.00019803 | 4.9631e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2022-7_0_3_load_46 | 40 | 0.00023897 | 5.9891e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2022-7_0_3_load_45 | 42 | 0.00015914 | 3.9883e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2022-7_0_3_load_32 | 43 | 8.64e-05 | 2.1654e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2022-7_0_3_load_33 | 44 | 0.00011696 | 2.9314e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2022-7_0_3_load_35 | 45 | 0.0001345 | 3.3708e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2022-7_0_3_load_36 | 46 | 0.00010773 | 2.7e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2022-7_0_3_load_37 | 47 | 0.00011023 | 2.7627e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2022-7_0_3_load_40 | 49 | 9.8768e-05 | 2.4754e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2022-7_0_3_load_44 | 51 | 0.00010256 | 2.5705e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2022-7_0_3_load_41 | 52 | 9.9778e-05 | 2.5007e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2022-7_0_3_load_53 | 53 | 0.00011577 | 2.9014e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2022-7_0_3_load_51 | 54 | 8.9472e-05 | 2.2424e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2022-7_0_3_load_50 | 55 | 9.7725e-05 | 2.4492e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2022-7_0_3_load_54 | 56 | 0.00024946 | 6.252e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2022-7_0_3_load_72 | 57 | 9.4779e-05 | 2.3754e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2022-7_0_3_load_70 | 58 | 0.00017802 | 4.4616e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2022-7_0_3_load_55 | 59 | 0.00010318 | 2.5858e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2022-7_0_3_load_56 | 60 | 0.00010614 | 2.66e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2022-7_0_3_load_57 | 61 | 0.0001362 | 3.4134e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2022-7_0_3_load_58 | 62 | 0.00010593 | 2.6549e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2022-7_0_3_load_61 | 65 | 0.00010647 | 2.6684e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2022-7_0_3_load_62 | 66 | 8.7326e-05 | 2.1886e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2022-7_0_3_load_64 | 67 | 8.2668e-05 | 2.0719e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2022-7_0_3_load_79 | 68 | 0.00067913 | 0.00017021 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2022-7_0_3_load_63 | 69 | 0.00041757 | 0.00010465 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2022-7_0_3_load_73 | 70 | 0.00044897 | 0.00011252 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2022-7_0_3_load_69 | 71 | 0.00011304 | 2.833e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2022-7_0_3_load_80 | 72 | 0.0003673 | 9.2055e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2022-7_0_3_load_118 | 73 | 0.00040174 | 0.00010069 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2022-7_0_3_load_65 | 75 | 0.00036188 | 9.0695e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2022-7_0_3_load_66 | 76 | 0.00062632 | 0.00015697 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2022-7_0_3_load_68 | 77 | 0.00040652 | 0.00010188 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2022-7_0_3_load_71 | 78 | 0.00048257 | 0.00012094 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2022-7_0_3_load_126 | 79 | 0.00068895 | 0.00017267 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2022-7_0_3_load_127 | 80 | 0.0010681 | 0.0002677 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2022-7_0_3_load_78 | 82 | 8.2218e-05 | 2.0606e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2022-7_0_3_load_82 | 83 | 0.00044752 | 0.00011216 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2022-7_0_3_load_92 | 84 | 0.00013017 | 3.2623e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2022-7_0_3_load_83 | 85 | 0.00018419 | 4.6163e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2022-7_0_3_load_81 | 86 | 0.00015017 | 3.7636e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2022-7_0_3_load_100 | 87 | 0.00059217 | 0.00014841 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2022-7_0_3_load_84 | 88 | 0.00016038 | 4.0196e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2022-7_0_3_load_85 | 89 | 0.00013428 | 3.3654e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2022-7_0_3_load_88 | 92 | 0.00011738 | 2.9417e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2022-7_0_3_load_89 | 93 | 0.00011249 | 2.8194e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2022-7_0_3_load_91 | 95 | 0.00041593 | 0.00010424 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2022-7_0_3_load_93 | 96 | 0.00013407 | 3.3601e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2022-7_0_3_load_94 | 97 | 0.00014053 | 3.5219e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2022-7_0_3_load_96 | 99 | 0.00018656 | 4.6758e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2022-7_0_3_load_97 | 100 | 0.00014727 | 3.691e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2022-7_0_3_load_107 | 101 | 0.00014519 | 3.6388e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2022-7_0_3_load_104 | 102 | 0.0001725 | 4.3233e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2022-7_0_3_load_98 | 103 | 0.00014054 | 3.5223e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2022-7_0_3_load_105 | 105 | 0.00014958 | 3.7488e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2022-7_0_3_load_99 | 106 | 0.00014735 | 3.6929e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2022-7_0_3_load_114 | 108 | 0.00037334 | 9.3567e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2022-7_0_3_load_111 | 109 | 0.00038018 | 9.5283e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2022-7_0_3_load_106 | 110 | 0.00019497 | 4.8863e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2022-7_0_3_load_108 | 111 | 0.00014071 | 3.5265e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2022-7_0_3_load_109 | 112 | 0.00014641 | 3.6694e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2022-7_0_3_load_156 | 113 | 0.00052541 | 0.00013168 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2022-7_0_3_load_152 | 114 | 0.00025766 | 6.4575e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2022-7_0_3_load_116 | 115 | 0.00050092 | 0.00012554 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2022-7_0_3_load_112 | 116 | 0.00039546 | 9.9113e-05 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2022-7_0_3_load_113 | 117 | 0.00039987 | 0.00010022 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2022-7_0_3_load_117 | 118 | 0.00039523 | 9.9054e-05 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2022-7_0_3_load_120 | 119 | 0.0001402 | 3.5136e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2022-7_0_3_load_119 | 120 | 0.00047444 | 0.0001189 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2022-7_0_3_load_125 | 122 | 0.00044444 | 0.00011139 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2022-7_0_3_load_122 | 123 | 0.00017289 | 4.333e-05 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2022-7_0_3_load_123 | 124 | 0.00018402 | 4.612e-05 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2022-7_0_3_load_124 | 125 | 0.00033994 | 8.5196e-05 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2022-7_0_3_load_157 | 126 | 0.00014718 | 3.6888e-05 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2022-7_0_3_load_144 | 127 | 0.00012934 | 3.2415e-05 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2022-7_0_3_load_130 | 128 | 0.00037474 | 9.3919e-05 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2022-7_0_3_load_158 | 129 | 0.00016064 | 4.0261e-05 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2022-7_0_3_load_129 | 130 | 0.00041144 | 0.00010312 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2022-7_0_3_load_131 | 132 | 0.00069702 | 0.00017469 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2022-7_0_3_load_132 | 133 | 0.0010135 | 0.000254 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2022-7_0_3_load_140 | 134 | 0.00061175 | 0.00015332 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2022-7_0_3_load_133 | 136 | 0.00078139 | 0.00019583 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2022-7_0_3_load_134 | 137 | 0.0006495 | 0.00016278 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2022-7_0_3_load_135 | 138 | 0.0006167 | 0.00015456 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2022-7_0_3_load_137 | 139 | 0.00071156 | 0.00017833 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2022-7_0_3_load_136 | 140 | 0.00074052 | 0.00018559 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2022-7_0_3_load_138 | 141 | 0.0017118 | 0.00042901 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2022-7_0_3_load_139 | 142 | 0.0014097 | 0.00035331 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2022-7_0_3_load_142 | 143 | 0.0013351 | 0.0003346 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2022-7_0_3_load_234 | 144 | 0.0012764 | 0.00031991 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_2022-7_0_3_load_235 | 146 | 0.0011187 | 0.00028037 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_2022-7_0_3_load_145 | 147 | 0.00010755 | 2.6955e-05 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_2022-7_0_3_load_146 | 148 | 0.00024825 | 6.2218e-05 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_2022-7_0_3_load_147 | 149 | 0.00143 | 0.00035839 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_2022-7_0_3_load_149 | 151 | 0.0033124 | 0.00083017 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_2022-7_0_3_load_150 | 152 | 0.0032984 | 0.00082666 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_2022-7_0_3_load_175 | 153 | 0.00095794 | 0.00024008 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_2022-7_0_3_load_244 | 155 | 0.00095901 | 0.00024035 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_2022-7_0_3_load_174 | 156 | 0.0027173 | 0.00068103 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_2022-7_0_3_load_172 | 157 | 0.0016313 | 0.00040884 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_2022-7_0_3_load_159 | 158 | 0.00048176 | 0.00012074 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_2022-7_0_3_load_155 | 159 | 0.00016988 | 4.2575e-05 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_2022-7_0_3_load_161 | 160 | 0.0016312 | 0.00040882 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_2022-7_0_3_load_160 | 162 | 0.00048294 | 0.00012104 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_2022-7_0_3_load_162 | 164 | 0.0030757 | 0.00077085 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_2022-7_0_3_load_151 | 166 | 0.00011643 | 2.9179e-05 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_2022-7_0_3_load_166 | 167 | 0.0016305 | 0.00040864 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_2022-7_0_3_load_171 | 168 | 0.0023919 | 0.00059948 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_2022-7_0_3_load_165 | 169 | 0.0024136 | 0.00060491 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_2022-7_0_3_load_167 | 170 | 0.0017171 | 0.00043033 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_2022-7_0_3_load_169 | 172 | 0.0019442 | 0.00048727 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_2022-7_0_3_load_170 | 173 | 0.0023524 | 0.00058956 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_2022-7_0_3_load_179 | 174 | 0.0025317 | 0.00063449 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_2022-7_0_3_load_180 | 175 | 0.0027247 | 0.00068287 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_2022-7_0_3_load_176 | 176 | 0.00096584 | 0.00024206 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_2022-7_0_3_load_177 | 177 | 0.00098711 | 0.00024739 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_2022-7_0_3_load_242 | 178 | 0.0021045 | 0.00052745 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_2022-7_0_3_load_178 | 179 | 0.00097605 | 0.00024462 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_2022-7_0_3_load_247 | 180 | 0.0018005 | 0.00045125 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_2022-7_0_3_load_248 | 181 | 0.00098952 | 0.000248 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_2022-7_0_3_load_181 | 182 | 0.0016489 | 0.00041326 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_2022-7_0_3_load_182 | 183 | 0.0024932 | 0.00062486 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_2022-7_0_3_load_183 | 184 | 0.0034024 | 0.00085272 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_2022-7_0_3_load_184 | 185 | 0.0028173 | 0.00070608 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_2022-7_0_3_load_185 | 186 | 0.0037182 | 0.00093186 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_2022-7_0_3_load_186 | 187 | 0.002354 | 0.00058997 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_2022-7_0_3_load_187 | 188 | 0.0027649 | 0.00069294 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_2022-7_0_3_load_188 | 189 | 0.0045782 | 0.0011474 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_2022-7_0_3_load_261 | 191 | 0.0018982 | 0.00047573 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_2022-7_0_3_load_190 | 192 | 0.0036777 | 0.00092172 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_2022-7_0_3_load_262 | 194 | 0.0017764 | 0.00044521 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_2022-7_0_3_load_259 | 195 | 0.0035204 | 0.00088229 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_2022-7_0_3_load_258 | 196 | 0.0031564 | 0.00079108 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_2022-7_0_3_load_260 | 197 | 0.0039545 | 0.0009911 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_2022-7_0_3_load_257 | 198 | 0.0012886 | 0.00032295 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_2022-7_0_3_load_192 | 199 | 0.0021838 | 0.00054732 | 0 | 0 |  | 1 | TRUE | wye
172 | LV_2022-7_0_3_load_193 | 200 | 0.001635 | 0.00040977 | 0 | 0 |  | 1 | TRUE | wye
173 | LV_2022-7_0_3_load_194 | 201 | 0.0022873 | 0.00057325 | 0 | 0 |  | 1 | TRUE | wye
174 | LV_2022-7_0_3_load_195 | 202 | 0.0017218 | 0.00043153 | 0 | 0 |  | 1 | TRUE | wye
175 | LV_2022-7_0_3_load_196 | 203 | 0.0017422 | 0.00043663 | 0 | 0 |  | 1 | TRUE | wye
176 | LV_2022-7_0_3_load_197 | 204 | 0.0037432 | 0.00093814 | 0 | 0 |  | 1 | TRUE | wye
177 | LV_2022-7_0_3_load_198 | 205 | 0.0016107 | 0.00040369 | 0 | 0 |  | 1 | TRUE | wye
178 | LV_2022-7_0_3_load_199 | 206 | 0.0019977 | 0.00050068 | 0 | 0 |  | 1 | TRUE | wye
179 | LV_2022-7_0_3_load_200 | 207 | 0.0022873 | 0.00057326 | 0 | 0 |  | 1 | TRUE | wye
180 | LV_2022-7_0_3_load_201 | 208 | 0.0028269 | 0.00070848 | 0 | 0 |  | 1 | TRUE | wye
181 | LV_2022-7_0_3_load_203 | 209 | 0.0022858 | 0.00057289 | 0 | 0 |  | 1 | TRUE | wye
182 | LV_2022-7_0_3_load_204 | 210 | 0.0022854 | 0.00057277 | 0 | 0 |  | 1 | TRUE | wye
183 | LV_2022-7_0_3_load_205 | 211 | 0.0015306 | 0.0003836 | 0 | 0 |  | 1 | TRUE | wye
184 | LV_2022-7_0_3_load_206 | 212 | 0.0012247 | 0.00030694 | 0 | 0 |  | 1 | TRUE | wye
185 | LV_2022-7_0_3_load_208 | 214 | 0.001023 | 0.00025639 | 0 | 0 |  | 1 | TRUE | wye
186 | LV_2022-7_0_3_load_211 | 216 | 0.0010356 | 0.00025954 | 0 | 0 |  | 1 | TRUE | wye
187 | LV_2022-7_0_3_load_212 | 217 | 0.0010879 | 0.00027265 | 0 | 0 |  | 1 | TRUE | wye
188 | LV_2022-7_0_3_load_213 | 218 | 0.001616 | 0.00040502 | 0 | 0 |  | 1 | TRUE | wye
189 | LV_2022-7_0_3_load_215 | 221 | 0.001438 | 0.00036039 | 0 | 0 |  | 1 | TRUE | wye
190 | LV_2022-7_0_3_load_227 | 222 | 0.0042778 | 0.0010721 | 0 | 0 |  | 1 | TRUE | wye
191 | LV_2022-7_0_3_load_222 | 224 | 0.0025479 | 0.00063856 | 0 | 0 |  | 1 | TRUE | wye
192 | LV_2022-7_0_3_load_230 | 225 | 0.0016467 | 0.00041269 | 0 | 0 |  | 1 | TRUE | wye
193 | LV_2022-7_0_3_load_233 | 226 | 0.001239 | 0.00031052 | 0 | 0 |  | 1 | TRUE | wye
194 | LV_2022-7_0_3_load_225 | 227 | 0.0016705 | 0.00041867 | 0 | 0 |  | 1 | TRUE | wye
195 | LV_2022-7_0_3_load_240 | 228 | 0.0010833 | 0.00027149 | 0 | 0 |  | 1 | TRUE | wye
196 | LV_2022-7_0_3_load_237 | 229 | 0.002372 | 0.00059449 | 0 | 0 |  | 1 | TRUE | wye
197 | LV_2022-7_0_3_load_220 | 230 | 0.0014945 | 0.00037455 | 0 | 0 |  | 1 | TRUE | wye
198 | LV_2022-7_0_3_load_229 | 231 | 0.0016822 | 0.0004216 | 0 | 0 |  | 1 | TRUE | wye
199 | LV_2022-7_0_3_load_232 | 232 | 0.00018625 | 4.6679e-05 | 0 | 0 |  | 1 | TRUE | wye
200 | LV_2022-7_0_3_load_216 | 233 | 0.000207 | 5.1879e-05 | 0 | 0 |  | 1 | TRUE | wye
201 | LV_2022-7_0_3_load_218 | 235 | 0.00025172 | 6.3086e-05 | 0 | 0 |  | 1 | TRUE | wye
202 | LV_2022-7_0_3_load_219 | 236 | 0.00025555 | 6.4048e-05 | 0 | 0 |  | 1 | TRUE | wye
203 | LV_2022-7_0_3_load_221 | 237 | 0.00018473 | 4.6297e-05 | 0 | 0 |  | 1 | TRUE | wye
204 | LV_2022-7_0_3_load_231 | 238 | 0.0012393 | 0.00031061 | 0 | 0 |  | 1 | TRUE | wye
205 | LV_2022-7_0_3_load_223 | 239 | 0.0017967 | 0.0004503 | 0 | 0 |  | 1 | TRUE | wye
206 | LV_2022-7_0_3_load_224 | 240 | 0.0022154 | 0.00055523 | 0 | 0 |  | 1 | TRUE | wye
207 | LV_2022-7_0_3_load_226 | 241 | 0.0017901 | 0.00044864 | 0 | 0 |  | 1 | TRUE | wye
208 | LV_2022-7_0_3_load_228 | 242 | 0.0016511 | 0.00041381 | 0 | 0 |  | 1 | TRUE | wye
209 | LV_2022-7_0_3_load_241 | 243 | 0.0010634 | 0.0002665 | 0 | 0 |  | 1 | TRUE | wye
210 | LV_2022-7_0_3_load_238 | 244 | 0.0007069 | 0.00017717 | 0 | 0 |  | 1 | TRUE | wye
211 | LV_2022-7_0_3_load_239 | 245 | 0.0011532 | 0.00028902 | 0 | 0 |  | 1 | TRUE | wye
212 | LV_2022-7_0_3_load_263 | 246 | 0.0010573 | 0.00026499 | 0 | 0 |  | 1 | TRUE | wye
213 | LV_2022-7_0_3_load_264 | 247 | 0.0020341 | 0.00050979 | 0 | 0 |  | 1 | TRUE | wye
214 | LV_2022-7_0_3_load_243 | 248 | 0.00098939 | 0.00024796 | 0 | 0 |  | 1 | TRUE | wye
215 | LV_2022-7_0_3_load_245 | 249 | 0.0010594 | 0.0002655 | 0 | 0 |  | 1 | TRUE | wye
216 | LV_2022-7_0_3_load_246 | 250 | 0.0010447 | 0.00026182 | 0 | 0 |  | 1 | TRUE | wye
217 | LV_2022-7_0_3_load_266 | 251 | 0.0010212 | 0.00025594 | 0 | 0 |  | 1 | TRUE | wye
218 | LV_2022-7_0_3_load_265 | 252 | 0.0010192 | 0.00025545 | 0 | 0 |  | 1 | TRUE | wye
219 | LV_2022-7_0_3_load_249 | 253 | 0.001075 | 0.00026942 | 0 | 0 |  | 1 | TRUE | wye
220 | LV_2022-7_0_3_load_250 | 254 | 0.00104 | 0.00026065 | 0 | 0 |  | 1 | TRUE | wye
221 | LV_2022-7_0_3_load_251 | 255 | 0.0028197 | 0.00070669 | 0 | 0 |  | 1 | TRUE | wye
222 | LV_2022-7_0_3_load_252 | 256 | 0.0029089 | 0.00072905 | 0 | 0 |  | 1 | TRUE | wye
223 | LV_2022-7_0_3_load_253 | 257 | 0.0037901 | 0.00094989 | 0 | 0 |  | 1 | TRUE | wye
224 | LV_2022-7_0_3_load_254 | 258 | 0.0029801 | 0.00074688 | 0 | 0 |  | 1 | TRUE | wye
225 | LV_2022-7_0_3_load_255 | 259 | 0.0012886 | 0.00032295 | 0 | 0 |  | 1 | TRUE | wye
226 | LV_2022-7_0_3_load_256 | 260 | 0.003056 | 0.00076591 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 251 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2022-7_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.022844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2022-7_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0050972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2022-7_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.003053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2022-7_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.0077745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2022-7_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.014026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2022-7_0_3_line_5 | NAYY 4x150 SE | 5 | 8 | 0.017772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2022-7_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.0011621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2022-7_0_3_line_7 | NAYY 4x150 SE | 7 | 14 | 0.0059765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2022-7_0_3_line_8 | NAYY 4x150 SE | 8 | 15 | 0.0014874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2022-7_0_3_line_9 | NAYY 4x150 SE | 9 | 10 | 0.010816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2022-7_0_3_line_10 | NAYY 4x150 SE | 10 | 66 | 0.010984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2022-7_0_3_line_11 | NAYY 4x150 SE | 11 | 12 | 0.036686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2022-7_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.019512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2022-7_0_3_line_13 | NAYY 4x150 SE | 13 | 84 | 0.0038183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2022-7_0_3_line_14 | NAYY 4x150 SE | 14 | 16 | 0.01012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2022-7_0_3_line_15 | NAYY 4x150 SE | 15 | 21 | 0.010218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2022-7_0_3_line_16 | NAYY 4x150 SE | 16 | 17 | 0.014505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2022-7_0_3_line_17 | NAYY 4x150 SE | 17 | 18 | 0.010066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2022-7_0_3_line_18 | NAYY 4x150 SE | 18 | 19 | 1.2223e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2022-7_0_3_line_19 | NAYY 4x150 SE | 19 | 20 | 0.0034646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2022-7_0_3_line_20 | NAYY 4x150 SE | 20 | 23 | 0.0069028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2022-7_0_3_line_21 | NAYY 4x150 SE | 21 | 22 | 0.00026023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2022-7_0_3_line_22 | NAYY 4x150 SE | 22 | 55 | 0.010287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2022-7_0_3_line_23 | NAYY 4x150 SE | 23 | 35 | 0.0062644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2022-7_0_3_line_24 | NAYY 4x150 SE | 24 | 25 | 0.014163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2022-7_0_3_line_25 | NAYY 4x150 SE | 24 | 26 | 0.000417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2022-7_0_3_line_26 | NAYY 4x150 SE | 25 | 27 | 0.0070646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2022-7_0_3_line_27 | NAYY 4x150 SE | 26 | 28 | 0.013535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2022-7_0_3_line_28 | NAYY 4x150 SE | 27 | 29 | 0.0072491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2022-7_0_3_line_29 | NAYY 4x150 SE | 27 | 30 | 0.0066822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2022-7_0_3_line_30 | NAYY 4x150 SE | 28 | 31 | 0.001678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2022-7_0_3_line_31 | NAYY 4x150 SE | 30 | 32 | 0.013414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2022-7_0_3_line_32 | NAYY 4x150 SE | 31 | 33 | 0.0013081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2022-7_0_3_line_33 | NAYY 4x150 SE | 33 | 34 | 0.014451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2022-7_0_3_line_34 | NAYY 4x150 SE | 34 | 50 | 0.0096343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2022-7_0_3_line_35 | NAYY 4x150 SE | 35 | 36 | 0.018243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2022-7_0_3_line_36 | NAYY 4x150 SE | 36 | 37 | 0.00031211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2022-7_0_3_line_37 | NAYY 4x150 SE | 37 | 38 | 0.016635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2022-7_0_3_line_38 | NAYY 4x150 SE | 38 | 39 | 0.0011024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2022-7_0_3_line_39 | NAYY 4x150 SE | 38 | 40 | 0.022793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2022-7_0_3_line_40 | NAYY 4x150 SE | 39 | 41 | 0.011248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_2022-7_0_3_line_41 | NAYY 4x150 SE | 40 | 42 | 0.01834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_2022-7_0_3_line_42 | NAYY 4x150 SE | 41 | 53 | 0.007452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_2022-7_0_3_line_43 | NAYY 4x150 SE | 41 | 54 | 0.0095402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2022-7_0_3_line_44 | NAYY 4x150 SE | 42 | 51 | 0.0025227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_2022-7_0_3_line_45 | NAYY 4x150 SE | 43 | 44 | 0.0019336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2022-7_0_3_line_46 | NAYY 4x150 SE | 44 | 45 | 0.015637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_2022-7_0_3_line_47 | NAYY 4x150 SE | 45 | 46 | 0.014666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2022-7_0_3_line_48 | NAYY 4x150 SE | 46 | 47 | 0.013386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2022-7_0_3_line_49 | NAYY 4x150 SE | 47 | 48 | 0.010571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2022-7_0_3_line_50 | NAYY 4x150 SE | 48 | 49 | 0.019362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_2022-7_0_3_line_51 | NAYY 4x150 SE | 49 | 52 | 0.011933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2022-7_0_3_line_52 | NAYY 4x150 SE | 50 | 51 | 0.017107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2022-7_0_3_line_53 | NAYY 4x150 SE | 50 | 52 | 0.009537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_2022-7_0_3_line_54 | NAYY 4x150 SE | 53 | 56 | 0.0063818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_2022-7_0_3_line_55 | NAYY 4x150 SE | 54 | 55 | 0.0076324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_2022-7_0_3_line_56 | NAYY 4x150 SE | 56 | 57 | 0.01949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2022-7_0_3_line_57 | NAYY 4x150 SE | 57 | 58 | 0.0053597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2022-7_0_3_line_58 | NAYY 4x150 SE | 58 | 74 | 0.0035405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2022-7_0_3_line_59 | NAYY 4x150 SE | 59 | 60 | 0.0084446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2022-7_0_3_line_60 | NAYY 4x150 SE | 59 | 61 | 0.0035064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2022-7_0_3_line_61 | NAYY 4x150 SE | 60 | 62 | 0.009286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2022-7_0_3_line_62 | NAYY 4x150 SE | 61 | 63 | 0.012216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2022-7_0_3_line_63 | NAYY 4x150 SE | 62 | 64 | 0.0081615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2022-7_0_3_line_64 | NAYY 4x150 SE | 63 | 65 | 0.012236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2022-7_0_3_line_65 | NAYY 4x150 SE | 63 | 66 | 0.0069559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2022-7_0_3_line_66 | NAYY 4x150 SE | 64 | 67 | 0.0063989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2022-7_0_3_line_67 | NAYY 4x150 SE | 65 | 68 | 0.0086175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2022-7_0_3_line_68 | NAYY 4x150 SE | 67 | 71 | 1.6361e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2022-7_0_3_line_69 | NAYY 4x150 SE | 68 | 72 | 0.01971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2022-7_0_3_line_70 | NAYY 4x150 SE | 69 | 70 | 0.010936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2022-7_0_3_line_71 | NAYY 4x150 SE | 70 | 73 | 0.00082584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2022-7_0_3_line_72 | NAYY 4x150 SE | 71 | 74 | 0.019085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2022-7_0_3_line_73 | NAYY 4x150 SE | 72 | 86 | 0.010838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_2022-7_0_3_line_74 | NAYY 4x150 SE | 73 | 81 | 0.0095168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2022-7_0_3_line_75 | NAYY 4x150 SE | 74 | 75 | 0.010475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2022-7_0_3_line_76 | NAYY 4x150 SE | 75 | 76 | 0.0092267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2022-7_0_3_line_77 | NAYY 4x150 SE | 76 | 77 | 0.0026653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2022-7_0_3_line_78 | NAYY 4x150 SE | 77 | 78 | 0.013151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2022-7_0_3_line_79 | NAYY 4x150 SE | 78 | 79 | 0.0039572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2022-7_0_3_line_80 | NAYY 4x150 SE | 79 | 80 | 0.023291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2022-7_0_3_line_81 | NAYY 4x150 SE | 80 | 131 | 0.012012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2022-7_0_3_line_82 | NAYY 4x150 SE | 81 | 118 | 0.018005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2022-7_0_3_line_83 | NAYY 4x150 SE | 81 | 117 | 0.0070043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2022-7_0_3_line_84 | NAYY 4x150 SE | 82 | 83 | 0.0042133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2022-7_0_3_line_85 | NAYY 4x150 SE | 83 | 85 | 0.012096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2022-7_0_3_line_86 | NAYY 4x150 SE | 84 | 91 | 0.017526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2022-7_0_3_line_87 | NAYY 4x150 SE | 85 | 86 | 0.010499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2022-7_0_3_line_88 | NAYY 4x150 SE | 86 | 87 | 0.010686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2022-7_0_3_line_89 | NAYY 4x150 SE | 88 | 89 | 0.0082746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2022-7_0_3_line_90 | NAYY 4x150 SE | 88 | 90 | 0.011536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2022-7_0_3_line_91 | NAYY 4x150 SE | 89 | 91 | 0.010438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2022-7_0_3_line_92 | NAYY 4x150 SE | 90 | 92 | 0.0099846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2022-7_0_3_line_93 | NAYY 4x150 SE | 90 | 93 | 0.0084497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2022-7_0_3_line_94 | NAYY 4x150 SE | 90 | 94 | 0.026624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2022-7_0_3_line_95 | NAYY 4x150 SE | 91 | 95 | 0.013942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2022-7_0_3_line_96 | NAYY 4x150 SE | 92 | 96 | 0.015923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2022-7_0_3_line_97 | NAYY 4x150 SE | 93 | 97 | 0.013751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2022-7_0_3_line_98 | NAYY 4x150 SE | 94 | 98 | 0.027936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2022-7_0_3_line_99 | NAYY 4x150 SE | 94 | 99 | 0.010931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2022-7_0_3_line_100 | NAYY 4x150 SE | 96 | 100 | 0.0088582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2022-7_0_3_line_101 | NAYY 4x150 SE | 98 | 101 | 0.038034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2022-7_0_3_line_102 | NAYY 4x150 SE | 99 | 102 | 0.010341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2022-7_0_3_line_103 | NAYY 4x150 SE | 100 | 103 | 0.0099348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2022-7_0_3_line_104 | NAYY 4x150 SE | 101 | 104 | 0.012566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2022-7_0_3_line_105 | NAYY 4x150 SE | 102 | 105 | 0.0038262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2022-7_0_3_line_106 | NAYY 4x150 SE | 103 | 106 | 0.0017924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2022-7_0_3_line_107 | NAYY 4x150 SE | 104 | 113 | 0.020962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2022-7_0_3_line_108 | NAYY 4x150 SE | 104 | 114 | 0.0036298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2022-7_0_3_line_109 | NAYY 4x150 SE | 105 | 110 | 0.012242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2022-7_0_3_line_110 | NAYY 4x150 SE | 107 | 108 | 0.018507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2022-7_0_3_line_111 | NAYY 4x150 SE | 107 | 109 | 0.009375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2022-7_0_3_line_112 | NAYY 4x150 SE | 108 | 115 | 0.013372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2022-7_0_3_line_113 | NAYY 4x150 SE | 109 | 116 | 0.0022766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2022-7_0_3_line_114 | NAYY 4x150 SE | 110 | 111 | 0.0069569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2022-7_0_3_line_115 | NAYY 4x150 SE | 111 | 112 | 0.0071959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2022-7_0_3_line_116 | NAYY 4x150 SE | 114 | 166 | 0.020204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2022-7_0_3_line_117 | NAYY 4x150 SE | 115 | 119 | 0.0012378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2022-7_0_3_line_118 | NAYY 4x150 SE | 116 | 117 | 0.012783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_2022-7_0_3_line_119 | NAYY 4x150 SE | 118 | 120 | 0.0052055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_2022-7_0_3_line_120 | NAYY 4x150 SE | 119 | 121 | 0.021176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_2022-7_0_3_line_121 | NAYY 4x150 SE | 120 | 122 | 0.0080418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_2022-7_0_3_line_122 | NAYY 4x150 SE | 121 | 123 | 0.010487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_2022-7_0_3_line_123 | NAYY 4x150 SE | 121 | 124 | 0.019864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_2022-7_0_3_line_124 | NAYY 4x150 SE | 121 | 125 | 0.014414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_2022-7_0_3_line_125 | NAYY 4x150 SE | 123 | 126 | 0.0017361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_2022-7_0_3_line_126 | NAYY 4x150 SE | 124 | 127 | 0.0018488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_2022-7_0_3_line_127 | NAYY 4x150 SE | 125 | 128 | 0.0018446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_2022-7_0_3_line_128 | NAYY 4x150 SE | 126 | 129 | 0.0026364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_2022-7_0_3_line_129 | NAYY 4x150 SE | 128 | 130 | 0.021143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_2022-7_0_3_line_130 | NAYY 4x150 SE | 130 | 131 | 0.0087327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_2022-7_0_3_line_131 | NAYY 4x150 SE | 131 | 132 | 0.0070215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_2022-7_0_3_line_132 | NAYY 4x150 SE | 132 | 133 | 0.021486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_2022-7_0_3_line_133 | NAYY 4x150 SE | 133 | 134 | 0.022575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_2022-7_0_3_line_134 | NAYY 4x150 SE | 134 | 135 | 0.02875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_2022-7_0_3_line_135 | NAYY 4x150 SE | 135 | 147 | 0.014776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_2022-7_0_3_line_136 | NAYY 4x150 SE | 135 | 148 | 0.020275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_2022-7_0_3_line_137 | NAYY 4x150 SE | 135 | 149 | 0.034857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_2022-7_0_3_line_138 | NAYY 4x150 SE | 136 | 137 | 0.021495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_2022-7_0_3_line_139 | NAYY 4x150 SE | 136 | 138 | 0.021259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_2022-7_0_3_line_140 | NAYY 4x150 SE | 138 | 139 | 0.022083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_2022-7_0_3_line_141 | NAYY 4x150 SE | 139 | 142 | 0.021688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_2022-7_0_3_line_142 | NAYY 4x150 SE | 140 | 141 | 0.023734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_2022-7_0_3_line_143 | NAYY 4x150 SE | 141 | 143 | 0.023693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_2022-7_0_3_line_144 | NAYY 4x150 SE | 142 | 144 | 0.019408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_2022-7_0_3_line_145 | NAYY 4x150 SE | 143 | 145 | 0.018682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_2022-7_0_3_line_146 | NAYY 4x150 SE | 144 | 146 | 0.0067629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_2022-7_0_3_line_147 | NAYY 4x150 SE | 145 | 153 | 0.017101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
148 | LV_2022-7_0_3_line_148 | NAYY 4x150 SE | 145 | 154 | 0.029938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
149 | LV_2022-7_0_3_line_149 | NAYY 4x150 SE | 146 | 218 | 0.018952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_2022-7_0_3_line_150 | NAYY 4x150 SE | 147 | 150 | 0.027463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
151 | LV_2022-7_0_3_line_151 | NAYY 4x150 SE | 148 | 151 | 0.013237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
152 | LV_2022-7_0_3_line_152 | NAYY 4x150 SE | 149 | 152 | 0.017297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
153 | LV_2022-7_0_3_line_153 | NAYY 4x150 SE | 150 | 158 | 0.019385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
154 | LV_2022-7_0_3_line_154 | NAYY 4x150 SE | 150 | 159 | 0.021983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
155 | LV_2022-7_0_3_line_155 | NAYY 4x150 SE | 151 | 160 | 0.01252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
156 | LV_2022-7_0_3_line_156 | NAYY 4x150 SE | 152 | 161 | 0.019543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
157 | LV_2022-7_0_3_line_157 | NAYY 4x150 SE | 153 | 155 | 0.0069092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
158 | LV_2022-7_0_3_line_158 | NAYY 4x150 SE | 154 | 156 | 0.013855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
159 | LV_2022-7_0_3_line_159 | NAYY 4x150 SE | 154 | 157 | 0.015226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
160 | LV_2022-7_0_3_line_160 | NAYY 4x150 SE | 155 | 178 | 0.0048681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
161 | LV_2022-7_0_3_line_161 | NAYY 4x150 SE | 156 | 176 | 0.015371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
162 | LV_2022-7_0_3_line_162 | NAYY 4x150 SE | 157 | 168 | 7.0652e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
163 | LV_2022-7_0_3_line_163 | NAYY 4x150 SE | 158 | 162 | 0.016426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
164 | LV_2022-7_0_3_line_164 | NAYY 4x150 SE | 159 | 163 | 0.0083285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
165 | LV_2022-7_0_3_line_165 | NAYY 4x150 SE | 160 | 164 | 0.016898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
166 | LV_2022-7_0_3_line_166 | NAYY 4x150 SE | 161 | 165 | 0.026336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
167 | LV_2022-7_0_3_line_167 | NAYY 4x150 SE | 163 | 166 | 0.0042268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
168 | LV_2022-7_0_3_line_168 | NAYY 4x150 SE | 164 | 167 | 0.0070348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
169 | LV_2022-7_0_3_line_169 | NAYY 4x150 SE | 165 | 169 | 0.021504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
170 | LV_2022-7_0_3_line_170 | NAYY 4x150 SE | 167 | 168 | 0.024136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
171 | LV_2022-7_0_3_line_171 | NAYY 4x150 SE | 169 | 170 | 0.029772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
172 | LV_2022-7_0_3_line_172 | NAYY 4x150 SE | 170 | 171 | 0.016717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
173 | LV_2022-7_0_3_line_173 | NAYY 4x150 SE | 171 | 172 | 0.045063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
174 | LV_2022-7_0_3_line_174 | NAYY 4x150 SE | 172 | 173 | 0.031152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
175 | LV_2022-7_0_3_line_175 | NAYY 4x150 SE | 173 | 174 | 0.024049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
176 | LV_2022-7_0_3_line_176 | NAYY 4x150 SE | 174 | 175 | 0.03751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
177 | LV_2022-7_0_3_line_177 | NAYY 4x150 SE | 175 | 182 | 0.021103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
178 | LV_2022-7_0_3_line_178 | NAYY 4x150 SE | 176 | 177 | 0.0067251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
179 | LV_2022-7_0_3_line_179 | NAYY 4x150 SE | 177 | 179 | 0.0067824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
180 | LV_2022-7_0_3_line_180 | NAYY 4x150 SE | 178 | 248 | 0.0021835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
181 | LV_2022-7_0_3_line_181 | NAYY 4x150 SE | 179 | 180 | 0.00017429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
182 | LV_2022-7_0_3_line_182 | NAYY 4x150 SE | 180 | 181 | 0.0065994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
183 | LV_2022-7_0_3_line_183 | NAYY 4x150 SE | 181 | 253 | 0.0067605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
184 | LV_2022-7_0_3_line_184 | NAYY 4x150 SE | 183 | 184 | 0.019834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
185 | LV_2022-7_0_3_line_185 | NAYY 4x150 SE | 183 | 185 | 0.0079121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
186 | LV_2022-7_0_3_line_186 | NAYY 4x150 SE | 184 | 186 | 0.018556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
187 | LV_2022-7_0_3_line_187 | NAYY 4x150 SE | 185 | 187 | 0.013458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
188 | LV_2022-7_0_3_line_188 | NAYY 4x150 SE | 186 | 188 | 0.025578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
189 | LV_2022-7_0_3_line_189 | NAYY 4x150 SE | 187 | 189 | 0.010231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
190 | LV_2022-7_0_3_line_190 | NAYY 4x150 SE | 188 | 190 | 0.020011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
191 | LV_2022-7_0_3_line_191 | NAYY 4x150 SE | 189 | 191 | 0.012705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
192 | LV_2022-7_0_3_line_192 | NAYY 4x150 SE | 190 | 192 | 0.033987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
193 | LV_2022-7_0_3_line_193 | NAYY 4x150 SE | 190 | 193 | 0.031888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
194 | LV_2022-7_0_3_line_194 | NAYY 4x150 SE | 191 | 194 | 0.020758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
195 | LV_2022-7_0_3_line_195 | NAYY 4x150 SE | 192 | 195 | 0.027163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
196 | LV_2022-7_0_3_line_196 | NAYY 4x150 SE | 193 | 196 | 0.014035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
197 | LV_2022-7_0_3_line_197 | NAYY 4x150 SE | 194 | 205 | 0.011023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
198 | LV_2022-7_0_3_line_198 | NAYY 4x150 SE | 195 | 197 | 0.022016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
199 | LV_2022-7_0_3_line_199 | NAYY 4x150 SE | 196 | 198 | 0.021945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
200 | LV_2022-7_0_3_line_200 | NAYY 4x150 SE | 197 | 210 | 0.021772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
201 | LV_2022-7_0_3_line_201 | NAYY 4x150 SE | 198 | 260 | 0.00024931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
202 | LV_2022-7_0_3_line_202 | NAYY 4x150 SE | 199 | 200 | 0.015882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
203 | LV_2022-7_0_3_line_203 | NAYY 4x150 SE | 199 | 201 | 0.0052644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
204 | LV_2022-7_0_3_line_204 | NAYY 4x150 SE | 200 | 202 | 0.0070495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
205 | LV_2022-7_0_3_line_205 | NAYY 4x150 SE | 201 | 203 | 0.014434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
206 | LV_2022-7_0_3_line_206 | NAYY 4x150 SE | 202 | 204 | 0.0092204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
207 | LV_2022-7_0_3_line_207 | NAYY 4x150 SE | 203 | 205 | 0.010535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
208 | LV_2022-7_0_3_line_208 | NAYY 4x150 SE | 204 | 206 | 0.019686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
209 | LV_2022-7_0_3_line_209 | NAYY 4x150 SE | 206 | 207 | 0.018446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
210 | LV_2022-7_0_3_line_210 | NAYY 4x150 SE | 207 | 208 | 0.0023193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
211 | LV_2022-7_0_3_line_211 | NAYY 4x150 SE | 209 | 210 | 0.02202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
212 | LV_2022-7_0_3_line_212 | NAYY 4x150 SE | 211 | 212 | 0.020735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
213 | LV_2022-7_0_3_line_213 | NAYY 4x150 SE | 211 | 213 | 0.013597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
214 | LV_2022-7_0_3_line_214 | NAYY 4x150 SE | 212 | 214 | 0.0097629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
215 | LV_2022-7_0_3_line_215 | NAYY 4x150 SE | 213 | 215 | 0.021605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
216 | LV_2022-7_0_3_line_216 | NAYY 4x150 SE | 214 | 216 | 0.0065872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
217 | LV_2022-7_0_3_line_217 | NAYY 4x150 SE | 215 | 217 | 0.021927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
218 | LV_2022-7_0_3_line_218 | NAYY 4x150 SE | 215 | 218 | 0.023033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
219 | LV_2022-7_0_3_line_219 | NAYY 4x150 SE | 216 | 222 | 0.0040151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
220 | LV_2022-7_0_3_line_220 | NAYY 4x150 SE | 217 | 223 | 0.0092833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
221 | LV_2022-7_0_3_line_221 | NAYY 4x150 SE | 219 | 220 | 0.025482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
222 | LV_2022-7_0_3_line_222 | NAYY 4x150 SE | 219 | 221 | 0.019163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
223 | LV_2022-7_0_3_line_223 | NAYY 4x150 SE | 220 | 224 | 0.016504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
224 | LV_2022-7_0_3_line_224 | NAYY 4x150 SE | 220 | 225 | 0.015384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
225 | LV_2022-7_0_3_line_225 | NAYY 4x150 SE | 221 | 226 | 0.00019321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
226 | LV_2022-7_0_3_line_226 | NAYY 4x150 SE | 222 | 227 | 0.015746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
227 | LV_2022-7_0_3_line_227 | NAYY 4x150 SE | 223 | 228 | 0.0083037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
228 | LV_2022-7_0_3_line_228 | NAYY 4x150 SE | 223 | 229 | 0.011277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
229 | LV_2022-7_0_3_line_229 | NAYY 4x150 SE | 224 | 230 | 0.0061105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
230 | LV_2022-7_0_3_line_230 | NAYY 4x150 SE | 225 | 231 | 0.014289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
231 | LV_2022-7_0_3_line_231 | NAYY 4x150 SE | 226 | 232 | 0.02067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
232 | LV_2022-7_0_3_line_232 | NAYY 4x150 SE | 227 | 239 | 0.023403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
233 | LV_2022-7_0_3_line_233 | NAYY 4x150 SE | 228 | 243 | 0.0078906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
234 | LV_2022-7_0_3_line_234 | NAYY 4x150 SE | 229 | 244 | 0.016399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
235 | LV_2022-7_0_3_line_235 | NAYY 4x150 SE | 230 | 234 | 0.019594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
236 | LV_2022-7_0_3_line_236 | NAYY 4x150 SE | 231 | 242 | 0.010757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
237 | LV_2022-7_0_3_line_237 | NAYY 4x150 SE | 232 | 238 | 0.0065103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
238 | LV_2022-7_0_3_line_238 | NAYY 4x150 SE | 233 | 234 | 0.043412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
239 | LV_2022-7_0_3_line_239 | NAYY 4x150 SE | 235 | 236 | 0.029894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
240 | LV_2022-7_0_3_line_240 | NAYY 4x150 SE | 236 | 237 | 0.027853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
241 | LV_2022-7_0_3_line_241 | NAYY 4x150 SE | 237 | 238 | 0.022916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
242 | LV_2022-7_0_3_line_242 | NAYY 4x150 SE | 239 | 240 | 0.014797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
243 | LV_2022-7_0_3_line_243 | NAYY 4x150 SE | 240 | 241 | 0.012396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
244 | LV_2022-7_0_3_line_244 | NAYY 4x150 SE | 241 | 242 | 0.0086399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
245 | LV_2022-7_0_3_line_245 | NAYY 4x150 SE | 243 | 246 | 0.0067558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
246 | LV_2022-7_0_3_line_246 | NAYY 4x150 SE | 244 | 245 | 0.020419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
247 | LV_2022-7_0_3_line_247 | NAYY 4x150 SE | 246 | 247 | 0.0066647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
248 | LV_2022-7_0_3_line_248 | NAYY 4x150 SE | 247 | 252 | 0.0028202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
249 | LV_2022-7_0_3_line_249 | NAYY 4x150 SE | 248 | 249 | 0.007047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
250 | LV_2022-7_0_3_line_250 | NAYY 4x150 SE | 249 | 250 | 0.0069712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
251 | LV_2022-7_0_3_line_251 | NAYY 4x150 SE | 250 | 251 | 0.006848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
252 | LV_2022-7_0_3_line_252 | NAYY 4x150 SE | 251 | 252 | 0.006761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
253 | LV_2022-7_0_3_line_253 | NAYY 4x150 SE | 253 | 254 | 0.0065598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
254 | LV_2022-7_0_3_line_254 | NAYY 4x150 SE | 254 | 255 | 0.010766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
255 | LV_2022-7_0_3_line_255 | NAYY 4x150 SE | 255 | 256 | 0.01265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
256 | LV_2022-7_0_3_line_256 | NAYY 4x150 SE | 256 | 257 | 0.016596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
257 | LV_2022-7_0_3_line_257 | NAYY 4x150 SE | 257 | 258 | 0.0062818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
258 | LV_2022-7_0_3_line_258 | NAYY 4x150 SE | 258 | 259 | 0.019316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
259 | LV_2022-7_0_3_line_259 | NAYY 4x150 SE | 259 | 260 | 8.0039e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2022-7_0_3_trafo_266 | 0.25 MVA 20/0.4 kV | 261 | 251 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2561738.2096 | 1195037.1625 | 2561719.2182 | 1195024.4674
1 | 2561738.2096 | 1195037.1625 | 2561742.4472 | 1195039.9952
2 | 2561719.2182 | 1195024.4674 | 2561716.68 | 1195022.7707
3 | 2561710.2166 | 1195018.4501 | 2561716.68 | 1195022.7707
4 | 2561710.2166 | 1195018.4501 | 2561698.5557 | 1195010.6552
5 | 2561683.7811 | 1195000.7789 | 2561698.5557 | 1195010.6552
6 | 2561740.7082 | 1195008.4091 | 2561740.4212 | 1195008.0107 | 2561739.941 | 1195007.5419
7 | 2561735.6647 | 1195003.3668 | 2561739.941 | 1195007.5419
8 | 2561683.7811 | 1195000.7789 | 2561682.5445 | 1194999.9523
9 | 2561704.3358 | 1195062.2209 | 2561695.2047 | 1195056.4238
10 | 2561685.9316 | 1195050.5366 | 2561695.2047 | 1195056.4238
11 | 2561719.7708 | 1195114.4684 | 2561721.7795 | 1195130.6644 | 2561729.381 | 1195149.558
12 | 2561719.7708 | 1195114.4684 | 2561708.1072 | 1195130.1103
13 | 2561708.1072 | 1195130.1103 | 2561705.8248 | 1195133.1712
14 | 2561735.6647 | 1195003.3668 | 2561728.4232 | 1194996.2968
15 | 2561674.0495 | 1194994.2737 | 2561682.5445 | 1194999.9523
16 | 2561717.6655 | 1194986.7094 | 2561719.4817 | 1194987.5671 | 2561728.4232 | 1194996.2968
17 | 2561717.6655 | 1194986.7094 | 2561708.564 | 1194982.4109
18 | 2561708.5529 | 1194982.4057 | 2561708.564 | 1194982.4109
19 | 2561708.5529 | 1194982.4057 | 2561705.4201 | 1194980.9261
20 | 2561699.1784 | 1194977.9782 | 2561705.4201 | 1194980.9261
21 | 2561673.8331 | 1194994.129 | 2561674.0495 | 1194994.2737
22 | 2561665.281 | 1194988.4123 | 2561673.8331 | 1194994.129
23 | 2561699.1784 | 1194977.9782 | 2561693.5139 | 1194975.303
24 | 2561744.7156 | 1194955.6581 | 2561733.0956 | 1194947.5602
25 | 2561732.7535 | 1194947.3218 | 2561733.0956 | 1194947.5602
26 | 2561750.5116 | 1194959.6972 | 2561744.7156 | 1194955.6581
27 | 2561732.7535 | 1194947.3218 | 2561721.6491 | 1194939.5832
28 | 2561750.5116 | 1194959.6972 | 2561756.4389 | 1194963.8705
29 | 2561750.5116 | 1194959.6972 | 2561746.4387 | 1194964.9948
30 | 2561721.6491 | 1194939.5832 | 2561720.2724 | 1194938.6238
31 | 2561738.2629 | 1194975.629 | 2561746.4387 | 1194964.9948
32 | 2561720.2724 | 1194938.6238 | 2561719.1992 | 1194937.876
33 | 2561707.3434 | 1194929.6138 | 2561719.1992 | 1194937.876
34 | 2561699.4391 | 1194924.1054 | 2561707.3434 | 1194929.6138
35 | 2561675.7658 | 1194971.7314 | 2561690.104 | 1194973.6926 | 2561693.5139 | 1194975.303
36 | 2561675.4565 | 1194971.6891 | 2561675.7658 | 1194971.7314
37 | 2561658.9745 | 1194969.4347 | 2561675.4565 | 1194971.6891
38 | 2561658.9745 | 1194969.4347 | 2561658.2631 | 1194970.2767
39 | 2561658.9745 | 1194969.4347 | 2561674.1532 | 1194952.4311
40 | 2561651.0044 | 1194978.8688 | 2561658.2631 | 1194970.2767
41 | 2561686.3669 | 1194938.7492 | 2561674.1532 | 1194952.4311
42 | 2561651.0044 | 1194978.8688 | 2561646.1393 | 1194984.5135
43 | 2561651.0044 | 1194978.8688 | 2561658.9358 | 1194984.1707
44 | 2561686.3669 | 1194938.7492 | 2561688.0469 | 1194936.8672
45 | 2561772.7548 | 1194925.288 | 2561771.3581 | 1194923.9509
46 | 2561771.3581 | 1194923.9509 | 2561760.0623 | 1194913.1373
47 | 2561760.0623 | 1194913.1373 | 2561756.2393 | 1194909.4774 | 2561747.9654 | 1194905.0721
48 | 2561747.9654 | 1194905.0721 | 2561736.1497 | 1194898.7809
49 | 2561726.8192 | 1194893.813 | 2561736.1497 | 1194898.7809
50 | 2561726.8192 | 1194893.813 | 2561713.836 | 1194908.1772
51 | 2561713.836 | 1194908.1772 | 2561705.8341 | 1194917.0302
52 | 2561699.4391 | 1194924.1054 | 2561688.0469 | 1194936.8672
53 | 2561699.4391 | 1194924.1054 | 2561705.8341 | 1194917.0302
54 | 2561641.9729 | 1194989.3476 | 2561646.1393 | 1194984.5135
55 | 2561665.281 | 1194988.4123 | 2561658.9358 | 1194984.1707
56 | 2561641.9729 | 1194989.3476 | 2561629.2485 | 1195004.1108
57 | 2561629.2485 | 1195004.1108 | 2561625.7494 | 1195008.1707
58 | 2561623.4379 | 1195010.8526 | 2561625.7494 | 1195008.1707
59 | 2561666.5585 | 1195038.751 | 2561659.3072 | 1195034.4234
60 | 2561666.5585 | 1195038.751 | 2561669.5695 | 1195040.548
61 | 2561659.3072 | 1195034.4234 | 2561651.3333 | 1195029.6645
62 | 2561680.0592 | 1195046.8084 | 2561669.5695 | 1195040.548
63 | 2561644.325 | 1195025.4818 | 2561651.3333 | 1195029.6645
64 | 2561680.0592 | 1195046.8084 | 2561675.1151 | 1195058.0013
65 | 2561680.0592 | 1195046.8084 | 2561685.9316 | 1195050.5366
66 | 2561644.325 | 1195025.4818 | 2561639.0838 | 1195021.8109
67 | 2561675.1151 | 1195058.0013 | 2561671.6331 | 1195065.8841 | 2561671.6331 | 1195065.8841
68 | 2561639.0838 | 1195021.8109 | 2561639.0704 | 1195021.8015
69 | 2561670.2047 | 1195085.5182 | 2561670.285 | 1195077.8104 | 2561671.6331 | 1195065.8841
70 | 2561633.3502 | 1195051.2574 | 2561632.5502 | 1195053.4285 | 2561630.9975 | 1195061.9094
71 | 2561630.9975 | 1195061.9094 | 2561630.8488 | 1195062.7217
72 | 2561623.4379 | 1195010.8526 | 2561639.0704 | 1195021.8015
73 | 2561670.0918 | 1195096.3552 | 2561670.2047 | 1195085.5182
74 | 2561629.1349 | 1195072.0829 | 2561630.8488 | 1195062.7217
75 | 2561623.4379 | 1195010.8526 | 2561616.448 | 1195018.6547
76 | 2561616.448 | 1195018.6547 | 2561610.2912 | 1195025.5269
77 | 2561608.5128 | 1195027.5121 | 2561610.2912 | 1195025.5269
78 | 2561599.7376 | 1195037.307 | 2561608.5128 | 1195027.5121
79 | 2561599.7376 | 1195037.307 | 2561597.0971 | 1195040.2544
80 | 2561581.5554 | 1195057.6021 | 2561597.0971 | 1195040.2544
81 | 2561573.5401 | 1195066.5488 | 2561581.5554 | 1195057.6021
82 | 2561629.1349 | 1195072.0829 | 2561611.1742 | 1195070.8178
83 | 2561629.1349 | 1195072.0829 | 2561628.7953 | 1195079.079
84 | 2561696.4405 | 1195091.4119 | 2561692.2995 | 1195092.1888
85 | 2561692.2995 | 1195092.1888 | 2561680.411 | 1195094.4192
86 | 2561695.3485 | 1195147.2209 | 2561705.8248 | 1195133.1712
87 | 2561670.0918 | 1195096.3552 | 2561680.411 | 1195094.4192
88 | 2561670.0918 | 1195096.3552 | 2561659.5697 | 1195098.2179
89 | 2561684.5113 | 1195162.4762 | 2561689.3034 | 1195155.7305
90 | 2561677.8307 | 1195171.8803 | 2561684.5113 | 1195162.4762
91 | 2561695.3485 | 1195147.2209 | 2561689.3034 | 1195155.7305
92 | 2561677.8307 | 1195171.8803 | 2561670.4007 | 1195166.9253 | 2561669.6475 | 1195166.1882
93 | 2561677.8307 | 1195171.8803 | 2561684.598 | 1195176.9399
94 | 2561662.3358 | 1195193.5584 | 2561677.8307 | 1195171.8803
95 | 2561695.3485 | 1195147.2209 | 2561688.0188 | 1195135.3503
96 | 2561658.3613 | 1195154.9626 | 2561659.3061 | 1195156.0684 | 2561669.6475 | 1195166.1882
97 | 2561695.6113 | 1195185.174 | 2561684.598 | 1195176.9399
98 | 2561645.42 | 1195215.8239 | 2561662.3358 | 1195193.5584
99 | 2561662.3358 | 1195193.5584 | 2561653.9436 | 1195186.5539
100 | 2561658.3613 | 1195154.9626 | 2561652.6073 | 1195148.2277
101 | 2561645.42 | 1195215.8239 | 2561614.1376 | 1195194.19
102 | 2561653.9436 | 1195186.5539 | 2561646.0042 | 1195179.9273
103 | 2561652.6073 | 1195148.2277 | 2561649.2647 | 1195144.3154 | 2561646.9295 | 1195140.1343
104 | 2561603.8024 | 1195187.0424 | 2561614.1376 | 1195194.19
105 | 2561646.0042 | 1195179.9273 | 2561644.5182 | 1195178.687 | 2561643.1668 | 1195177.3649
106 | 2561646.0555 | 1195138.5694 | 2561646.9295 | 1195140.1343
107 | 2561603.8024 | 1195187.0424 | 2561592.1595 | 1195204.4742
108 | 2561603.8024 | 1195187.0424 | 2561600.8567 | 1195184.9216
109 | 2561634.4159 | 1195168.8036 | 2561643.1668 | 1195177.3649
110 | 2561630.0149 | 1195103.4501 | 2561611.7717 | 1195106.5651
111 | 2561630.0149 | 1195103.4501 | 2561629.2888 | 1195094.1033
112 | 2561598.5901 | 1195108.8158 | 2561611.7717 | 1195106.5651
113 | 2561629.2888 | 1195094.1033 | 2561629.1125 | 1195091.8335
114 | 2561634.4159 | 1195168.8036 | 2561629.4431 | 1195163.9384
115 | 2561624.2994 | 1195158.9062 | 2561629.4431 | 1195163.9384
116 | 2561584.4603 | 1195173.1164 | 2561600.8567 | 1195184.9216
117 | 2561597.37 | 1195109.0242 | 2561598.5901 | 1195108.8158
118 | 2561628.7953 | 1195079.079 | 2561628.5362 | 1195084.4158 | 2561629.1125 | 1195091.8335
119 | 2561611.1742 | 1195070.8178 | 2561605.9816 | 1195070.452
120 | 2561576.4959 | 1195112.5884 | 2561597.37 | 1195109.0242
121 | 2561605.9816 | 1195070.452 | 2561597.9597 | 1195069.8869
122 | 2561576.4959 | 1195112.5884 | 2561578.831 | 1195122.8124
123 | 2561576.4959 | 1195112.5884 | 2561557.0143 | 1195116.4651
124 | 2561576.4959 | 1195112.5884 | 2561575.5724 | 1195098.2044
125 | 2561579.2175 | 1195124.5049 | 2561578.831 | 1195122.8124
126 | 2561557.0143 | 1195116.4651 | 2561555.201 | 1195116.8259
127 | 2561575.5724 | 1195098.2044 | 2561575.4542 | 1195096.3635
128 | 2561579.8045 | 1195127.0751 | 2561579.2175 | 1195124.5049
129 | 2561574.0996 | 1195075.2636 | 2561575.4542 | 1195096.3635
130 | 2561573.5401 | 1195066.5488 | 2561574.0996 | 1195075.2636
131 | 2561573.5401 | 1195066.5488 | 2561568.9355 | 1195071.8497
132 | 2561568.9355 | 1195071.8497 | 2561554.8453 | 1195088.0707
133 | 2561540.0409 | 1195105.1138 | 2561554.8453 | 1195088.0707
134 | 2561522.5509 | 1195127.7111 | 2561525.1292 | 1195122.2804 | 2561540.0409 | 1195105.1138
135 | 2561522.5509 | 1195127.7111 | 2561534.4046 | 1195136.5328
136 | 2561522.5509 | 1195127.7111 | 2561506.0266 | 1195115.9621
137 | 2561522.5509 | 1195127.7111 | 2561501.7873 | 1195155.7084
138 | 2561550.6322 | 1195046.821 | 2561536.6812 | 1195063.1737
139 | 2561564.4298 | 1195030.6479 | 2561550.6322 | 1195046.821
140 | 2561578.7626 | 1195013.8477 | 2561564.4298 | 1195030.6479
141 | 2561577.9664 | 1194995.6972 | 2561584.1846 | 1195007.4923 | 2561578.7626 | 1195013.8477
142 | 2561483.9771 | 1195063.688 | 2561503.2895 | 1195077.4843
143 | 2561483.9771 | 1195063.688 | 2561464.6981 | 1195049.9156
144 | 2561577.9664 | 1194995.6972 | 2561575.4991 | 1194991.0169 | 2561564.8092 | 1194981.7964
145 | 2561449.4969 | 1195039.0562 | 2561464.6981 | 1195049.9156
146 | 2561564.8092 | 1194981.7964 | 2561559.6881 | 1194977.3793
147 | 2561449.4969 | 1195039.0562 | 2561458.3756 | 1195024.4412
148 | 2561433.3932 | 1195064.3187 | 2561449.4969 | 1195039.0562
149 | 2561545.3369 | 1194965.0008 | 2561559.6881 | 1194977.3793
150 | 2561556.4357 | 1195152.9287 | 2561534.4046 | 1195136.5328
151 | 2561506.0266 | 1195115.9621 | 2561495.2384 | 1195108.2916
152 | 2561491.5141 | 1195169.6245 | 2561500.2987 | 1195157.7156 | 2561501.7873 | 1195155.7084
153 | 2561556.4357 | 1195152.9287 | 2561545.0923 | 1195168.6483
154 | 2561556.4357 | 1195152.9287 | 2561574.2725 | 1195165.7785
155 | 2561495.2384 | 1195108.2916 | 2561485.0351 | 1195101.0368
156 | 2561479.9133 | 1195185.3513 | 2561491.5141 | 1195169.6245
157 | 2561461.9628 | 1195018.5362 | 2561458.3756 | 1195024.4412
158 | 2561433.3932 | 1195064.3187 | 2561422.1503 | 1195056.2219
159 | 2561433.3932 | 1195064.3187 | 2561445.8023 | 1195073.1417
160 | 2561464.4904 | 1195014.3757 | 2561461.9628 | 1195018.5362
161 | 2561422.1503 | 1195056.2219 | 2561409.6775 | 1195047.2395
162 | 2561445.8023 | 1195073.1417 | 2561445.8598 | 1195073.1827
163 | 2561535.4801 | 1195181.9687 | 2561545.0923 | 1195168.6483
164 | 2561581.0301 | 1195170.6467 | 2561574.2725 | 1195165.7785
165 | 2561471.2636 | 1195091.2451 | 2561485.0351 | 1195101.0368
166 | 2561453.7344 | 1195181.8518 | 2561479.9133 | 1195185.3513
167 | 2561581.0301 | 1195170.6467 | 2561584.4603 | 1195173.1164
168 | 2561471.2636 | 1195091.2451 | 2561465.5303 | 1195087.1686
169 | 2561453.7344 | 1195181.8518 | 2561436.2456 | 1195169.3387
170 | 2561465.5303 | 1195087.1686 | 2561445.8598 | 1195073.1827
171 | 2561412.0332 | 1195152.0148 | 2561436.2456 | 1195169.3387
172 | 2561398.4382 | 1195142.2876 | 2561412.0332 | 1195152.0148
173 | 2561398.4382 | 1195142.2876 | 2561398.9596 | 1195141.6283 | 2561379.8425 | 1195128.5782 | 2561362.3748 | 1195116.7864
174 | 2561362.3748 | 1195116.7864 | 2561336.5556 | 1195099.3568
175 | 2561336.5556 | 1195099.3568 | 2561321.6748 | 1195089.3113 | 2561320.8536 | 1195088.3939 | 2561320.5154 | 1195086.7729 | 2561319.3254 | 1195085.3799 | 2561318.2985 | 1195084.4638 | 2561318.2985 | 1195084.4638
176 | 2561318.2985 | 1195084.4638 | 2561316.7112 | 1195084.0739 | 2561315.2555 | 1195084.0055 | 2561288.2167 | 1195062.7099
177 | 2561288.2167 | 1195062.7099 | 2561276.2514 | 1195053.2861 | 2561275.9696 | 1195052.1206 | 2561275.3182 | 1195050.3684 | 2561274.3127 | 1195049.2298 | 2561273.4607 | 1195048.2681
178 | 2561404.2202 | 1195043.3094 | 2561409.6775 | 1195047.2395
179 | 2561404.2202 | 1195043.3094 | 2561398.7165 | 1195039.3459
180 | 2561464.4904 | 1195014.3757 | 2561465.624 | 1195012.5096
181 | 2561398.5751 | 1195039.244 | 2561398.7165 | 1195039.3459
182 | 2561398.5751 | 1195039.244 | 2561393.2198 | 1195035.3874
183 | 2561393.2198 | 1195035.3874 | 2561387.7339 | 1195031.4366
184 | 2561382.7108 | 1194950.7734 | 2561370.9168 | 1194966.7195
185 | 2561382.7108 | 1194950.7734 | 2561387.4158 | 1194944.4122
186 | 2561370.9168 | 1194966.7195 | 2561367.1618 | 1194971.7963 | 2561356.6998 | 1194965.4397
187 | 2561387.4158 | 1194944.4122 | 2561395.4183 | 1194933.5924 | 2561395.4183 | 1194933.5924
188 | 2561356.6998 | 1194965.4397 | 2561334.8403 | 1194952.1578
189 | 2561401.097 | 1194925.082 | 2561395.4183 | 1194933.5924
190 | 2561317.7385 | 1194941.7668 | 2561334.8403 | 1194952.1578
191 | 2561401.097 | 1194925.082 | 2561408.1487 | 1194914.5139
192 | 2561317.7385 | 1194941.7668 | 2561336.5091 | 1194913.4331
193 | 2561299.7063 | 1194968.0426 | 2561310.456 | 1194951.4082 | 2561317.7385 | 1194941.7668
194 | 2561408.1487 | 1194914.5139 | 2561419.6702 | 1194897.2471
195 | 2561336.5091 | 1194913.4331 | 2561351.5108 | 1194890.7887
196 | 2561299.7063 | 1194968.0426 | 2561311.0954 | 1194976.2446
197 | 2561425.7884 | 1194888.0781 | 2561419.6702 | 1194897.2471
198 | 2561351.5108 | 1194890.7887 | 2561358.2581 | 1194880.6039 | 2561363.8365 | 1194872.5479
199 | 2561328.9035 | 1194989.0692 | 2561311.0954 | 1194976.2446
200 | 2561376.2311 | 1194854.6484 | 2561363.8365 | 1194872.5479
201 | 2561328.9035 | 1194989.0692 | 2561329.1058 | 1194989.2149
202 | 2561442.569 | 1194862.9296 | 2561451.384 | 1194849.719
203 | 2561442.569 | 1194862.9296 | 2561439.647 | 1194867.3086
204 | 2561455.2967 | 1194843.8551 | 2561451.384 | 1194849.719
205 | 2561439.647 | 1194867.3086 | 2561431.6355 | 1194879.3152
206 | 2561460.4145 | 1194836.1853 | 2561460.4145 | 1194836.1853 | 2561455.2967 | 1194843.8551
207 | 2561425.7884 | 1194888.0781 | 2561431.6355 | 1194879.3152
208 | 2561460.4145 | 1194836.1853 | 2561443.2574 | 1194826.5334
209 | 2561443.2574 | 1194826.5334 | 2561427.1805 | 1194817.4891
210 | 2561425.1591 | 1194816.3519 | 2561427.1805 | 1194817.4891
211 | 2561388.7671 | 1194836.5446 | 2561376.2311 | 1194854.6484
212 | 2561529.9775 | 1194925.3235 | 2561512.8003 | 1194913.71
213 | 2561541.2414 | 1194932.9391 | 2561529.9775 | 1194925.3235
214 | 2561512.8003 | 1194913.71 | 2561504.7125 | 1194908.2418
215 | 2561541.2414 | 1194932.9391 | 2561527.8954 | 1194949.9567
216 | 2561504.7125 | 1194908.2418 | 2561499.2554 | 1194904.5523
217 | 2561527.8954 | 1194949.9567 | 2561514.2382 | 1194967.1107
218 | 2561527.8954 | 1194949.9567 | 2561545.3369 | 1194965.0008
219 | 2561499.2554 | 1194904.5523 | 2561495.9292 | 1194902.3034
220 | 2561508.456 | 1194974.3733 | 2561514.2382 | 1194967.1107
221 | 2561576.5757 | 1194893.2452 | 2561561.1325 | 1194913.5447
222 | 2561561.1325 | 1194913.5447 | 2561576.5501 | 1194924.9248
223 | 2561576.5757 | 1194893.2452 | 2561588.0139 | 1194881.3479
224 | 2561576.5757 | 1194893.2452 | 2561564.0119 | 1194884.3664
225 | 2561576.7056 | 1194925.0395 | 2561576.5501 | 1194924.9248
226 | 2561504.8169 | 1194889.3053 | 2561495.9292 | 1194902.3034 | 2561495.9292 | 1194902.3034
227 | 2561508.456 | 1194974.3733 | 2561500.8789 | 1194977.7701
228 | 2561508.456 | 1194974.3733 | 2561511.457 | 1194985.2439
229 | 2561588.0139 | 1194881.3479 | 2561592.2489 | 1194876.943
230 | 2561552.3424 | 1194876.1197 | 2561564.0119 | 1194884.3664
231 | 2561593.3361 | 1194937.3149 | 2561576.7056 | 1194925.0395
232 | 2561518.0266 | 1194869.9862 | 2561504.8169 | 1194889.3053
233 | 2561500.8789 | 1194977.7701 | 2561493.6786 | 1194980.9979
234 | 2561511.457 | 1194985.2439 | 2561515.8209 | 1195001.0516
235 | 2561605.8289 | 1194862.8179 | 2561592.2489 | 1194876.943
236 | 2561552.3424 | 1194876.1197 | 2561543.5577 | 1194869.9117
237 | 2561593.3361 | 1194937.3149 | 2561598.574 | 1194941.1812
238 | 2561605.8289 | 1194862.8179 | 2561623.2067 | 1194866.0301 | 2561643.8975 | 1194881.3403
239 | 2561656.7782 | 1194925.1701 | 2561636.9273 | 1194947.5221
240 | 2561636.9273 | 1194947.5221 | 2561625.1424 | 1194960.7919 | 2561617.0116 | 1194954.7903
241 | 2561617.0116 | 1194954.7903 | 2561598.574 | 1194941.1812
242 | 2561518.0266 | 1194869.9862 | 2561526.3786 | 1194857.7714
243 | 2561526.3786 | 1194857.7714 | 2561526.3786 | 1194857.7714 | 2561536.5019 | 1194864.9254
244 | 2561536.5019 | 1194864.9254 | 2561543.5577 | 1194869.9117
245 | 2561493.6786 | 1194980.9979 | 2561487.5139 | 1194983.7614
246 | 2561506.7883 | 1195019.3644 | 2561515.8209 | 1195001.0516
247 | 2561487.5139 | 1194983.7614 | 2561481.4324 | 1194986.4877
248 | 2561481.4324 | 1194986.4877 | 2561481.4324 | 1194986.4877 | 2561479.9681 | 1194988.898
249 | 2561469.2829 | 1195006.4868 | 2561465.624 | 1195012.5096
250 | 2561472.9023 | 1195000.5289 | 2561469.2829 | 1195006.4868
251 | 2561476.4578 | 1194994.6763 | 2561472.9023 | 1195000.5289
252 | 2561479.9681 | 1194988.898 | 2561476.4578 | 1194994.6763
253 | 2561387.7339 | 1195031.4366 | 2561382.4108 | 1195027.6031
254 | 2561373.6747 | 1195021.3118 | 2561382.4108 | 1195027.6031
255 | 2561373.6747 | 1195021.3118 | 2561363.4095 | 1195013.9191
256 | 2561349.9426 | 1195004.2208 | 2561363.4095 | 1195013.9191
257 | 2561349.9426 | 1195004.2208 | 2561344.8451 | 1195000.5498
258 | 2561329.1707 | 1194989.2617 | 2561344.8451 | 1195000.5498
259 | 2561329.1058 | 1194989.2149 | 2561329.1707 | 1194989.2617

## bus_geodata
| x | y | coords
0 | 2561738.2096 | 1195037.1625
1 | 2561719.2182 | 1195024.4674
2 | 2561742.4472 | 1195039.9952
3 | 2561716.68 | 1195022.7707
4 | 2561710.2166 | 1195018.4501
5 | 2561698.5557 | 1195010.6552
6 | 2561740.7082 | 1195008.4091
7 | 2561739.941 | 1195007.5419
8 | 2561683.7811 | 1195000.7789
9 | 2561704.3358 | 1195062.2209
10 | 2561695.2047 | 1195056.4238
11 | 2561719.7708 | 1195114.4684
12 | 2561729.381 | 1195149.558
13 | 2561708.1072 | 1195130.1103
14 | 2561735.6647 | 1195003.3668
15 | 2561682.5445 | 1194999.9523
16 | 2561728.4232 | 1194996.2968
17 | 2561717.6655 | 1194986.7094
18 | 2561708.564 | 1194982.4109
19 | 2561708.5529 | 1194982.4057
20 | 2561705.4201 | 1194980.9261
21 | 2561674.0495 | 1194994.2737
22 | 2561673.8331 | 1194994.129
23 | 2561699.1784 | 1194977.9782
24 | 2561733.0956 | 1194947.5602
25 | 2561744.7156 | 1194955.6581
26 | 2561732.7535 | 1194947.3218
27 | 2561750.5116 | 1194959.6972
28 | 2561721.6491 | 1194939.5832
29 | 2561756.4389 | 1194963.8705
30 | 2561746.4387 | 1194964.9948
31 | 2561720.2724 | 1194938.6238
32 | 2561738.2629 | 1194975.629
33 | 2561719.1992 | 1194937.876
34 | 2561707.3434 | 1194929.6138
35 | 2561693.5139 | 1194975.303
36 | 2561675.7658 | 1194971.7314
37 | 2561675.4565 | 1194971.6891
38 | 2561658.9745 | 1194969.4347
39 | 2561658.2631 | 1194970.2767
40 | 2561674.1532 | 1194952.4311
41 | 2561651.0044 | 1194978.8688
42 | 2561686.3669 | 1194938.7492
43 | 2561772.7548 | 1194925.288
44 | 2561771.3581 | 1194923.9509
45 | 2561760.0623 | 1194913.1373
46 | 2561747.9654 | 1194905.0721
47 | 2561736.1497 | 1194898.7809
48 | 2561726.8192 | 1194893.813
49 | 2561713.836 | 1194908.1772
50 | 2561699.4391 | 1194924.1054
51 | 2561688.0469 | 1194936.8672
52 | 2561705.8341 | 1194917.0302
53 | 2561646.1393 | 1194984.5135
54 | 2561658.9358 | 1194984.1707
55 | 2561665.281 | 1194988.4123
56 | 2561641.9729 | 1194989.3476
57 | 2561629.2485 | 1195004.1108
58 | 2561625.7494 | 1195008.1707
59 | 2561666.5585 | 1195038.751
60 | 2561659.3072 | 1195034.4234
61 | 2561669.5695 | 1195040.548
62 | 2561651.3333 | 1195029.6645
63 | 2561680.0592 | 1195046.8084
64 | 2561644.325 | 1195025.4818
65 | 2561675.1151 | 1195058.0013
66 | 2561685.9316 | 1195050.5366
67 | 2561639.0838 | 1195021.8109
68 | 2561671.6331 | 1195065.8841
69 | 2561633.3502 | 1195051.2574
70 | 2561630.9975 | 1195061.9094
71 | 2561639.0704 | 1195021.8015
72 | 2561670.2047 | 1195085.5182
73 | 2561630.8488 | 1195062.7217
74 | 2561623.4379 | 1195010.8526
75 | 2561616.448 | 1195018.6547
76 | 2561610.2912 | 1195025.5269
77 | 2561608.5128 | 1195027.5121
78 | 2561599.7376 | 1195037.307
79 | 2561597.0971 | 1195040.2544
80 | 2561581.5554 | 1195057.6021
81 | 2561629.1349 | 1195072.0829
82 | 2561696.4405 | 1195091.4119
83 | 2561692.2995 | 1195092.1888
84 | 2561705.8248 | 1195133.1712
85 | 2561680.411 | 1195094.4192
86 | 2561670.0918 | 1195096.3552
87 | 2561659.5697 | 1195098.2179
88 | 2561684.5113 | 1195162.4762
89 | 2561689.3034 | 1195155.7305
90 | 2561677.8307 | 1195171.8803
91 | 2561695.3485 | 1195147.2209
92 | 2561669.6475 | 1195166.1882
93 | 2561684.598 | 1195176.9399
94 | 2561662.3358 | 1195193.5584
95 | 2561688.0188 | 1195135.3503
96 | 2561658.3613 | 1195154.9626
97 | 2561695.6113 | 1195185.174
98 | 2561645.42 | 1195215.8239
99 | 2561653.9436 | 1195186.5539
100 | 2561652.6073 | 1195148.2277
101 | 2561614.1376 | 1195194.19
102 | 2561646.0042 | 1195179.9273
103 | 2561646.9295 | 1195140.1343
104 | 2561603.8024 | 1195187.0424
105 | 2561643.1668 | 1195177.3649
106 | 2561646.0555 | 1195138.5694
107 | 2561630.0149 | 1195103.4501
108 | 2561611.7717 | 1195106.5651
109 | 2561629.2888 | 1195094.1033
110 | 2561634.4159 | 1195168.8036
111 | 2561629.4431 | 1195163.9384
112 | 2561624.2994 | 1195158.9062
113 | 2561592.1595 | 1195204.4742
114 | 2561600.8567 | 1195184.9216
115 | 2561598.5901 | 1195108.8158
116 | 2561629.1125 | 1195091.8335
117 | 2561628.7953 | 1195079.079
118 | 2561611.1742 | 1195070.8178
119 | 2561597.37 | 1195109.0242
120 | 2561605.9816 | 1195070.452
121 | 2561576.4959 | 1195112.5884
122 | 2561597.9597 | 1195069.8869
123 | 2561578.831 | 1195122.8124
124 | 2561557.0143 | 1195116.4651
125 | 2561575.5724 | 1195098.2044
126 | 2561579.2175 | 1195124.5049
127 | 2561555.201 | 1195116.8259
128 | 2561575.4542 | 1195096.3635
129 | 2561579.8045 | 1195127.0751
130 | 2561574.0996 | 1195075.2636
131 | 2561573.5401 | 1195066.5488
132 | 2561568.9355 | 1195071.8497
133 | 2561554.8453 | 1195088.0707
134 | 2561540.0409 | 1195105.1138
135 | 2561522.5509 | 1195127.7111
136 | 2561550.6322 | 1195046.821
137 | 2561536.6812 | 1195063.1737
138 | 2561564.4298 | 1195030.6479
139 | 2561578.7626 | 1195013.8477
140 | 2561503.2895 | 1195077.4843
141 | 2561483.9771 | 1195063.688
142 | 2561577.9664 | 1194995.6972
143 | 2561464.6981 | 1195049.9156
144 | 2561564.8092 | 1194981.7964
145 | 2561449.4969 | 1195039.0562
146 | 2561559.6881 | 1194977.3793
147 | 2561534.4046 | 1195136.5328
148 | 2561506.0266 | 1195115.9621
149 | 2561501.7872 | 1195155.7084
150 | 2561556.4357 | 1195152.9287
151 | 2561495.2384 | 1195108.2916
152 | 2561491.5141 | 1195169.6245
153 | 2561458.3756 | 1195024.4412
154 | 2561433.3932 | 1195064.3187
155 | 2561461.9628 | 1195018.5362
156 | 2561422.1503 | 1195056.2219
157 | 2561445.8023 | 1195073.1417
158 | 2561545.0923 | 1195168.6483
159 | 2561574.2725 | 1195165.7785
160 | 2561485.0351 | 1195101.0368
161 | 2561479.9133 | 1195185.3513
162 | 2561535.4801 | 1195181.9687
163 | 2561581.0301 | 1195170.6467
164 | 2561471.2636 | 1195091.2451
165 | 2561453.7344 | 1195181.8518
166 | 2561584.4603 | 1195173.1164
167 | 2561465.5303 | 1195087.1686
168 | 2561445.8598 | 1195073.1827
169 | 2561436.2456 | 1195169.3387
170 | 2561412.0332 | 1195152.0148
171 | 2561398.4382 | 1195142.2876
172 | 2561362.3748 | 1195116.7864
173 | 2561336.5556 | 1195099.3567
174 | 2561318.2985 | 1195084.4638
175 | 2561288.2167 | 1195062.7099
176 | 2561409.6775 | 1195047.2395
177 | 2561404.2202 | 1195043.3094
178 | 2561464.4904 | 1195014.3757
179 | 2561398.7165 | 1195039.3459
180 | 2561398.5751 | 1195039.244
181 | 2561393.2198 | 1195035.3874
182 | 2561273.4607 | 1195048.2681
183 | 2561382.7108 | 1194950.7734
184 | 2561370.9168 | 1194966.7195
185 | 2561387.4158 | 1194944.4122
186 | 2561356.6998 | 1194965.4397
187 | 2561395.4183 | 1194933.5924
188 | 2561334.8403 | 1194952.1578
189 | 2561401.097 | 1194925.082
190 | 2561317.7385 | 1194941.7668
191 | 2561408.1487 | 1194914.5139
192 | 2561336.5091 | 1194913.4331
193 | 2561299.7063 | 1194968.0426
194 | 2561419.6702 | 1194897.2471
195 | 2561351.5108 | 1194890.7887
196 | 2561311.0954 | 1194976.2446
197 | 2561363.8365 | 1194872.5479
198 | 2561328.9035 | 1194989.0692
199 | 2561442.569 | 1194862.9296
200 | 2561451.384 | 1194849.719
201 | 2561439.647 | 1194867.3086
202 | 2561455.2967 | 1194843.8551
203 | 2561431.6355 | 1194879.3152
204 | 2561460.4145 | 1194836.1853
205 | 2561425.7884 | 1194888.0781
206 | 2561443.2574 | 1194826.5334
207 | 2561427.1805 | 1194817.4891
208 | 2561425.1591 | 1194816.3519
209 | 2561388.7671 | 1194836.5446
210 | 2561376.2311 | 1194854.6484
211 | 2561529.9775 | 1194925.3235
212 | 2561512.8003 | 1194913.71
213 | 2561541.2414 | 1194932.9391
214 | 2561504.7125 | 1194908.2418
215 | 2561527.8954 | 1194949.9567
216 | 2561499.2554 | 1194904.5523
217 | 2561514.2382 | 1194967.1107
218 | 2561545.3369 | 1194965.0008
219 | 2561561.1325 | 1194913.5447
220 | 2561576.5757 | 1194893.2452
221 | 2561576.5501 | 1194924.9248
222 | 2561495.9292 | 1194902.3034
223 | 2561508.456 | 1194974.3733
224 | 2561588.0139 | 1194881.3479
225 | 2561564.0119 | 1194884.3664
226 | 2561576.7056 | 1194925.0395
227 | 2561504.8169 | 1194889.3053
228 | 2561500.8789 | 1194977.7701
229 | 2561511.457 | 1194985.2439
230 | 2561592.2489 | 1194876.943
231 | 2561552.3424 | 1194876.1197
232 | 2561593.3361 | 1194937.3149
233 | 2561643.8975 | 1194881.3403
234 | 2561605.8289 | 1194862.8179
235 | 2561656.7782 | 1194925.1701
236 | 2561636.9273 | 1194947.5221
237 | 2561617.0116 | 1194954.7903
238 | 2561598.574 | 1194941.1812
239 | 2561518.0266 | 1194869.9862
240 | 2561526.3786 | 1194857.7714
241 | 2561536.5019 | 1194864.9254
242 | 2561543.5577 | 1194869.9117
243 | 2561493.6786 | 1194980.9979
244 | 2561515.8209 | 1195001.0516
245 | 2561506.7883 | 1195019.3644
246 | 2561487.5139 | 1194983.7614
247 | 2561481.4324 | 1194986.4877
248 | 2561465.624 | 1195012.5096
249 | 2561469.2829 | 1195006.4868
250 | 2561472.9023 | 1195000.5289
251 | 2561476.4578 | 1194994.6763
252 | 2561479.9681 | 1194988.898
253 | 2561387.7339 | 1195031.4366
254 | 2561382.4108 | 1195027.6031
255 | 2561373.6747 | 1195021.3118
256 | 2561363.4095 | 1195013.9191
257 | 2561349.9426 | 1195004.2208
258 | 2561344.8451 | 1195000.5498
259 | 2561329.1707 | 1194989.2617
260 | 2561329.1058 | 1194989.2149
261 | 2561508.456 | 1194974.3733

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97774 | -0.15658 | 0.00011366 | 2.8485e-05
1 | 0.97774 | -0.15653 | 0.00010329 | 2.5886e-05
2 | 0.97774 | -0.15659 | 9.4031e-05 | 2.3566e-05
3 | 0.97775 | -0.15652 | 0.00016795 | 4.2093e-05
4 | 0.97775 | -0.15649 | 0.00010018 | 2.5107e-05
5 | 0.97776 | -0.1564 | 0.00011053 | 2.7701e-05
6 | 0.97768 | -0.15703 | 0.00010409 | 2.6088e-05
7 | 0.97768 | -0.15703 | 0.00011407 | 2.8588e-05
8 | 0.97778 | -0.15627 | 8.7651e-05 | 2.1967e-05
9 | 0.97784 | -0.1558 | 8.9536e-05 | 2.244e-05
10 | 0.97785 | -0.15579 | 0.00015822 | 3.9653e-05
11 | 0.98061 | -0.13598 | 0 | 0
12 | 0.98059 | -0.13612 | 0.00034619 | 8.6764e-05
13 | 0.98062 | -0.13591 | 0.00016483 | 4.1309e-05
14 | 0.97768 | -0.15701 | 8.5614e-05 | 2.1457e-05
15 | 0.97778 | -0.15626 | 9.459e-05 | 2.3707e-05
16 | 0.97768 | -0.15698 | 8.2478e-05 | 2.0671e-05
17 | 0.97769 | -0.15692 | 9.5291e-05 | 2.3882e-05
18 | 0.9777 | -0.15687 | 9.5709e-05 | 2.3987e-05
19 | 0.9777 | -0.15687 | 8.3183e-05 | 2.0848e-05
20 | 0.9777 | -0.15685 | 0.00010495 | 2.6303e-05
21 | 0.9778 | -0.15617 | 8.8641e-05 | 2.2216e-05
22 | 0.9778 | -0.15616 | 8.3416e-05 | 2.0906e-05
23 | 0.97771 | -0.15679 | 9.4107e-05 | 2.3585e-05
24 | 0.97751 | -0.15825 | 0.00011041 | 2.7671e-05
25 | 0.9775 | -0.15831 | 0.00012344 | 3.0938e-05
26 | 0.97751 | -0.15825 | 0.00011051 | 2.7695e-05
27 | 0.9775 | -0.15833 | 0 | 0
28 | 0.97752 | -0.15816 | 0.00010824 | 2.7126e-05
29 | 0.97749 | -0.15834 | 9.9529e-05 | 2.4944e-05
30 | 0.97749 | -0.15835 | 8.6139e-05 | 2.1588e-05
31 | 0.97752 | -0.15815 | 0.0001774 | 4.4461e-05
32 | 0.97749 | -0.15836 | 9.7978e-05 | 2.4556e-05
33 | 0.97752 | -0.15813 | 0.00027034 | 6.7754e-05
34 | 0.97755 | -0.15795 | 0.00010313 | 2.5847e-05
35 | 0.97772 | -0.15674 | 8.8929e-05 | 2.2288e-05
36 | 0.97774 | -0.15655 | 0.0001122 | 2.812e-05
37 | 0.97774 | -0.15655 | 0.00012663 | 3.1736e-05
38 | 0.97777 | -0.15634 | 0 | 0
39 | 0.97778 | -0.1563 | 0.00019803 | 4.9631e-05
40 | 0.97769 | -0.15695 | 0.00023897 | 5.9891e-05
41 | 0.97784 | -0.15583 | 0 | 0
42 | 0.97762 | -0.1574 | 0.00015914 | 3.9883e-05
43 | 0.9775 | -0.15831 | 8.64e-05 | 2.1654e-05
44 | 0.9775 | -0.15831 | 0.00011696 | 2.9314e-05
45 | 0.9775 | -0.15827 | 0.0001345 | 3.3708e-05
46 | 0.97751 | -0.15822 | 0.00010773 | 2.7e-05
47 | 0.97752 | -0.15816 | 0.00011023 | 2.7627e-05
48 | 0.97753 | -0.15809 | 0 | 0
49 | 0.97754 | -0.15798 | 9.8768e-05 | 2.4754e-05
50 | 0.97757 | -0.15782 | 0 | 0
51 | 0.97762 | -0.15745 | 0.00010256 | 2.5705e-05
52 | 0.97756 | -0.1579 | 9.9778e-05 | 2.5007e-05
53 | 0.9779 | -0.15543 | 0.00011577 | 2.9014e-05
54 | 0.97782 | -0.15596 | 8.9472e-05 | 2.2424e-05
55 | 0.97781 | -0.15605 | 9.7725e-05 | 2.4492e-05
56 | 0.97795 | -0.15508 | 0.00024946 | 6.252e-05
57 | 0.9781 | -0.15394 | 9.4779e-05 | 2.3754e-05
58 | 0.97815 | -0.15363 | 0.00017802 | 4.4616e-05
59 | 0.97792 | -0.15525 | 0.00010318 | 2.5858e-05
60 | 0.97796 | -0.15497 | 0.00010614 | 2.66e-05
61 | 0.97791 | -0.15536 | 0.0001362 | 3.4134e-05
62 | 0.978 | -0.15465 | 0.00010593 | 2.6549e-05
63 | 0.97785 | -0.15574 | 0 | 0
64 | 0.97805 | -0.15436 | 0 | 0
65 | 0.97781 | -0.15607 | 0.00010647 | 2.6684e-05
66 | 0.97785 | -0.15576 | 8.7326e-05 | 2.1886e-05
67 | 0.97808 | -0.15413 | 8.2668e-05 | 2.0719e-05
68 | 0.97778 | -0.1563 | 0.00067913 | 0.00017021
69 | 0.97848 | -0.15122 | 0.00041757 | 0.00010465
70 | 0.97849 | -0.15117 | 0.00044897 | 0.00011252
71 | 0.97808 | -0.15413 | 0.00011304 | 2.833e-05
72 | 0.97772 | -0.15668 | 0.0003673 | 9.2055e-05
73 | 0.97849 | -0.15116 | 0.00040174 | 0.00010069
74 | 0.97818 | -0.15341 | 0 | 0
75 | 0.97832 | -0.15238 | 0.00036188 | 9.0695e-05
76 | 0.97845 | -0.15143 | 0.00062632 | 0.00015697
77 | 0.97849 | -0.15114 | 0.00040652 | 0.00010188
78 | 0.9787 | -0.14966 | 0.00048257 | 0.00012094
79 | 0.97876 | -0.14919 | 0.00068895 | 0.00017267
80 | 0.97917 | -0.14627 | 0.0010681 | 0.0002677
81 | 0.9785 | -0.15104 | 0 | 0
82 | 0.97768 | -0.15699 | 8.2218e-05 | 2.0606e-05
83 | 0.97768 | -0.15699 | 0.00044752 | 0.00011216
84 | 0.98063 | -0.13589 | 0.00013017 | 3.2623e-05
85 | 0.97769 | -0.15692 | 0.00018419 | 4.6163e-05
86 | 0.9777 | -0.15684 | 0.00015017 | 3.7636e-05
87 | 0.97769 | -0.15691 | 0.00059217 | 0.00014841
88 | 0.98067 | -0.13556 | 0.00016038 | 4.0196e-05
89 | 0.98066 | -0.13566 | 0.00013428 | 3.3654e-05
90 | 0.98069 | -0.13539 | 0 | 0
91 | 0.98064 | -0.13577 | 0 | 0
92 | 0.98068 | -0.13546 | 0.00011738 | 2.9417e-05
93 | 0.98069 | -0.13541 | 0.00011249 | 2.8194e-05
94 | 0.98078 | -0.13475 | 0 | 0
95 | 0.98063 | -0.13583 | 0.00041593 | 0.00010424
96 | 0.98067 | -0.13556 | 0.00013407 | 3.3601e-05
97 | 0.98069 | -0.13543 | 0.00014053 | 3.5219e-05
98 | 0.98092 | -0.1338 | 0 | 0
99 | 0.98077 | -0.13487 | 0.00018656 | 4.6758e-05
100 | 0.98067 | -0.1356 | 0.00014727 | 3.691e-05
101 | 0.9811 | -0.13249 | 0.00014519 | 3.6388e-05
102 | 0.98076 | -0.13495 | 0.0001725 | 4.3233e-05
103 | 0.98066 | -0.13563 | 0.00014054 | 3.5223e-05
104 | 0.98116 | -0.13204 | 0 | 0
105 | 0.98075 | -0.13498 | 0.00014958 | 3.7488e-05
106 | 0.98066 | -0.13563 | 0.00014735 | 3.6929e-05
107 | 0.97865 | -0.15 | 0 | 0
108 | 0.97875 | -0.14928 | 0.00037334 | 9.3567e-05
109 | 0.9786 | -0.15037 | 0.00038018 | 9.5283e-05
110 | 0.98074 | -0.13504 | 0.00019497 | 4.8863e-05
111 | 0.98074 | -0.13506 | 0.00014071 | 3.5265e-05
112 | 0.98074 | -0.13507 | 0.00014641 | 3.6694e-05
113 | 0.98114 | -0.13215 | 0.00052541 | 0.00013168
114 | 0.98118 | -0.13189 | 0.00025766 | 6.4575e-05
115 | 0.97883 | -0.1487 | 0.00050092 | 0.00012554
116 | 0.97859 | -0.15045 | 0.00039546 | 9.9113e-05
117 | 0.97853 | -0.15085 | 0.00039987 | 0.00010022
118 | 0.97847 | -0.15128 | 0.00039523 | 9.9054e-05
119 | 0.97884 | -0.14864 | 0.0001402 | 3.5136e-05
120 | 0.97846 | -0.15133 | 0.00047444 | 0.0001189
121 | 0.97899 | -0.14758 | 0 | 0
122 | 0.97846 | -0.15137 | 0.00044444 | 0.00011139
123 | 0.97898 | -0.14764 | 0.00017289 | 4.333e-05
124 | 0.97898 | -0.14765 | 0.00018402 | 4.612e-05
125 | 0.9791 | -0.14675 | 0.00033994 | 8.5196e-05
126 | 0.97898 | -0.14764 | 0.00014718 | 3.6888e-05
127 | 0.97898 | -0.14765 | 0.00012934 | 3.2415e-05
128 | 0.97912 | -0.14663 | 0.00037474 | 9.3919e-05
129 | 0.97898 | -0.14765 | 0.00016064 | 4.0261e-05
130 | 0.97931 | -0.14525 | 0.00041144 | 0.00010312
131 | 0.9794 | -0.14464 | 0 | 0
132 | 0.9796 | -0.14319 | 0.00069702 | 0.00017469
133 | 0.98024 | -0.13861 | 0.0010135 | 0.000254
134 | 0.98094 | -0.13357 | 0.00061175 | 0.00015332
135 | 0.98186 | -0.12697 | 0 | 0
136 | 0.99481 | -0.036329 | 0.00078139 | 0.00019583
137 | 0.99479 | -0.03647 | 0.0006495 | 0.00016278
138 | 0.99485 | -0.036022 | 0.0006167 | 0.00015456
139 | 0.99492 | -0.035565 | 0.00071156 | 0.00017833
140 | 0.99361 | -0.044236 | 0.00074052 | 0.00018559
141 | 0.99363 | -0.044058 | 0.0017118 | 0.00042901
142 | 0.995 | -0.03496 | 0.0014097 | 0.00035331
143 | 0.99371 | -0.04347 | 0.0013351 | 0.0003346
144 | 0.99512 | -0.034142 | 0.0012764 | 0.00031991
145 | 0.99382 | -0.042754 | 0 | 0
146 | 0.99517 | -0.03377 | 0.0011187 | 0.00028037
147 | 0.98175 | -0.12783 | 0.00010755 | 2.6955e-05
148 | 0.98327 | -0.11694 | 0.00024825 | 6.2218e-05
149 | 0.98085 | -0.13423 | 0.00143 | 0.00035839
150 | 0.98153 | -0.1294 | 0 | 0
151 | 0.9842 | -0.11038 | 0.0033124 | 0.00083017
152 | 0.98038 | -0.13758 | 0.0032984 | 0.00082666
153 | 0.99582 | -0.028866 | 0.00095794 | 0.00024008
154 | 0.99039 | -0.066623 | 0 | 0
155 | 0.99663 | -0.023238 | 0.00095901 | 0.00024035
156 | 0.98943 | -0.07336 | 0.0027173 | 0.00068103
157 | 0.98903 | -0.076207 | 0.0016313 | 0.00040884
158 | 0.9815 | -0.12959 | 0.00048176 | 0.00012074
159 | 0.98138 | -0.13043 | 0.00016988 | 4.2575e-05
160 | 0.98513 | -0.10375 | 0.0016312 | 0.00040882
161 | 0.97994 | -0.1407 | 0 | 0
162 | 0.98149 | -0.12967 | 0.00048294 | 0.00012104
163 | 0.98133 | -0.13081 | 0 | 0
164 | 0.98643 | -0.094548 | 0.0030757 | 0.00077085
165 | 0.97935 | -0.1449 | 0 | 0
166 | 0.9813 | -0.131 | 0.00011643 | 2.9179e-05
167 | 0.987 | -0.090501 | 0.0016305 | 0.00040864
168 | 0.98902 | -0.07625 | 0.0023919 | 0.00059948
169 | 0.97887 | -0.14834 | 0.0024136 | 0.00060491
170 | 0.97831 | -0.15235 | 0.0017171 | 0.00043033
171 | 0.97803 | -0.15431 | 0 | 0
172 | 0.9773 | -0.15959 | 0.0019442 | 0.00048727
173 | 0.97688 | -0.1626 | 0.0023524 | 0.00058956
174 | 0.97663 | -0.16434 | 0.0025317 | 0.00063449
175 | 0.9764 | -0.16606 | 0.0027247 | 0.00068287
176 | 0.98839 | -0.080635 | 0.00096584 | 0.00024206
177 | 0.98794 | -0.083789 | 0.00098711 | 0.00024739
178 | 0.99721 | -0.019254 | 0.0021045 | 0.00052745
179 | 0.98749 | -0.08694 | 0.00097605 | 0.00024462
180 | 0.98748 | -0.08702 | 0.0018005 | 0.00045125
181 | 0.98706 | -0.089994 | 0.00098952 | 0.000248
182 | 0.97634 | -0.16643 | 0.0016489 | 0.00041326
183 | 0.97547 | -0.17216 | 0.0024932 | 0.00062486
184 | 0.97658 | -0.16427 | 0.0034024 | 0.00085272
185 | 0.97506 | -0.1751 | 0.0028173 | 0.00070608
186 | 0.9777 | -0.15624 | 0.0037182 | 0.00093186
187 | 0.97442 | -0.17972 | 0.002354 | 0.00058997
188 | 0.97855 | -0.15022 | 0.0027649 | 0.00069294
189 | 0.97396 | -0.18298 | 0.0045782 | 0.0011474
190 | 0.97925 | -0.14524 | 0 | 0
191 | 0.97349 | -0.18642 | 0.0018982 | 0.00047573
192 | 0.97847 | -0.15081 | 0.0036777 | 0.00092172
193 | 0.98073 | -0.1347 | 0 | 0
194 | 0.97276 | -0.19163 | 0.0017764 | 0.00044521
195 | 0.97799 | -0.15422 | 0.0035204 | 0.00088229
196 | 0.98138 | -0.13007 | 0.0031564 | 0.00079108
197 | 0.97772 | -0.15618 | 0.0039545 | 0.0009911
198 | 0.98245 | -0.12248 | 0.0012886 | 0.00032295
199 | 0.97157 | -0.20023 | 0.0021838 | 0.00054732
200 | 0.97123 | -0.20262 | 0.001635 | 0.00040977
201 | 0.97169 | -0.19932 | 0.0022873 | 0.00057325
202 | 0.9711 | -0.20356 | 0.0017218 | 0.00043153
203 | 0.97209 | -0.19647 | 0.0017422 | 0.00043663
204 | 0.97096 | -0.20462 | 0.0037432 | 0.00093814
205 | 0.9724 | -0.19419 | 0.0016107 | 0.00040369
206 | 0.97075 | -0.2061 | 0.0019977 | 0.00050068
207 | 0.97061 | -0.2071 | 0.0022873 | 0.00057326
208 | 0.9706 | -0.20717 | 0.0028269 | 0.00070848
209 | 0.9775 | -0.15775 | 0.0022858 | 0.00057289
210 | 0.97757 | -0.15722 | 0.0022854 | 0.00057277
211 | 0.99407 | -0.041486 | 0.0015306 | 0.0003836
212 | 0.99321 | -0.047584 | 0.0012247 | 0.00030694
213 | 0.99467 | -0.037283 | 0 | 0
214 | 0.99281 | -0.050338 | 0.001023 | 0.00025639
215 | 0.99562 | -0.030614 | 0 | 0
216 | 0.99256 | -0.052129 | 0.0010356 | 0.00025954
217 | 0.99684 | -0.022053 | 0.0010879 | 0.00027265
218 | 0.99535 | -0.032515 | 0.001616 | 0.00040502
219 | 0.98963 | -0.072865 | 0 | 0
220 | 0.9898 | -0.071617 | 0 | 0
221 | 0.9895 | -0.073804 | 0.001438 | 0.00036039
222 | 0.99241 | -0.053179 | 0.0042778 | 0.0010721
223 | 0.99737 | -0.018334 | 0 | 0
224 | 0.9897 | -0.072333 | 0.0025479 | 0.00063856
225 | 0.99 | -0.070196 | 0.0016467 | 0.00041269
226 | 0.98949 | -0.073811 | 0.001239 | 0.00031052
227 | 0.99192 | -0.056616 | 0.0016705 | 0.00041867
228 | 0.9979 | -0.014657 | 0.0010833 | 0.00027149
229 | 0.99731 | -0.018813 | 0.002372 | 0.00059449
230 | 0.98969 | -0.072439 | 0.0014945 | 0.00037455
231 | 0.99022 | -0.068637 | 0.0016822 | 0.0004216
232 | 0.98943 | -0.074259 | 0.00018625 | 4.6679e-05
233 | 0.98967 | -0.072574 | 0.000207 | 5.1879e-05
234 | 0.98968 | -0.072481 | 0 | 0
235 | 0.98936 | -0.074773 | 0.00025172 | 6.3086e-05
236 | 0.98937 | -0.074696 | 0.00025555 | 6.4048e-05
237 | 0.98939 | -0.074551 | 0.00018473 | 4.6297e-05
238 | 0.98941 | -0.074387 | 0.0012393 | 0.00031061
239 | 0.99126 | -0.061333 | 0.0017967 | 0.0004503
240 | 0.99087 | -0.064048 | 0.0022154 | 0.00055523
241 | 0.99059 | -0.066045 | 0.0017901 | 0.00044864
242 | 0.99042 | -0.06728 | 0.0016511 | 0.00041381
243 | 0.99841 | -0.011081 | 0.0010634 | 0.0002665
244 | 0.99726 | -0.019119 | 0.0007069 | 0.00017717
245 | 0.99723 | -0.019356 | 0.0011532 | 0.00028902
246 | 0.99886 | -0.0079511 | 0.0010573 | 0.00026499
247 | 0.99931 | -0.0047953 | 0.0020341 | 0.00050979
248 | 0.99747 | -0.017446 | 0.00098939 | 0.00024796
249 | 0.99832 | -0.011581 | 0.0010594 | 0.0002655
250 | 0.99916 | -0.005752 | 0.0010447 | 0.00026182
251 | 1 | 0 | -0.22268 | -0.05605
252 | 0.99951 | -0.0034034 | 0.0010192 | 0.00025545
253 | 0.98663 | -0.093009 | 0.001075 | 0.00026942
254 | 0.98622 | -0.095901 | 0.00104 | 0.00026065
255 | 0.98555 | -0.10059 | 0.0028197 | 0.00070669
256 | 0.98479 | -0.10593 | 0.0029089 | 0.00072905
257 | 0.98384 | -0.1127 | 0.0037901 | 0.00094989
258 | 0.98349 | -0.11514 | 0.0029801 | 0.00074688
259 | 0.98247 | -0.12237 | 0.0012886 | 0.00032295
260 | 0.98246 | -0.1224 | 0.003056 | 0.00076591
261 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00020769 | -5.1988e-05 | 0.00020769 | 5.1702e-05 | 1.4235e-09 | -2.8595e-07 | 0.00031606 | 0.00031595 | 0.00031606 | 0.97774 | -0.15658 | 0.97774 | -0.15653 | 0.11706
1 | 9.4031e-05 | 2.3502e-05 | -9.4031e-05 | -2.3566e-05 | 6.5097e-11 | -6.3902e-08 | 0.00014308 | 0.0001431 | 0.0001431 | 0.97774 | -0.15658 | 0.97774 | -0.15659 | 0.053002
2 | -0.00031098 | -7.7588e-05 | 0.00031098 | 7.7549e-05 | 4.2646e-10 | -3.8126e-08 | 0.00047314 | 0.00047313 | 0.00047314 | 0.97774 | -0.15653 | 0.97775 | -0.15652 | 0.17524
3 | -0.00047893 | -0.00011964 | 0.00047893 | 0.00011955 | 2.5762e-09 | -9.6516e-08 | 0.00072874 | 0.0007287 | 0.00072874 | 0.97775 | -0.15652 | 0.97775 | -0.15649 | 0.2699
4 | -0.00057911 | -0.00014465 | 0.00057912 | 0.00014448 | 6.7953e-09 | -1.7331e-07 | 0.00088116 | 0.0008811 | 0.00088116 | 0.97775 | -0.15649 | 0.97776 | -0.1564 | 0.32635
5 | -0.00068964 | -0.00017218 | 0.00068966 | 0.00017196 | 1.2209e-08 | -2.182e-07 | 0.0010493 | 0.0010492 | 0.0010493 | 0.97776 | -0.1564 | 0.97778 | -0.15627 | 0.38863
6 | -0.00010409 | -2.6088e-05 | 0.00010409 | 2.6073e-05 | 1.8275e-11 | -1.4566e-08 | 0.00015843 | 0.00015842 | 0.00015843 | 0.97768 | -0.15703 | 0.97768 | -0.15703 | 0.058677
7 | -0.00021816 | -5.4661e-05 | 0.00021816 | 5.4586e-05 | 4.111e-10 | -7.4787e-08 | 0.00033203 | 0.000332 | 0.00033203 | 0.97768 | -0.15703 | 0.97768 | -0.15701 | 0.12297
8 | -0.00077731 | -0.00019393 | 0.00077731 | 0.00019391 | 1.2981e-09 | -1.8157e-08 | 0.0011826 | 0.0011826 | 0.0011826 | 0.97778 | -0.15627 | 0.97778 | -0.15626 | 0.43801
9 | -8.9536e-05 | -2.244e-05 | 8.9536e-05 | 2.2304e-05 | 1.2524e-10 | -1.3563e-07 | 0.00013625 | 0.0001362 | 0.00013625 | 0.97784 | -0.1558 | 0.97785 | -0.15579 | 0.050463
10 | -0.00024775 | -6.1957e-05 | 0.00024775 | 6.1819e-05 | 9.7383e-10 | -1.3741e-07 | 0.00037696 | 0.00037691 | 0.00037696 | 0.97785 | -0.15579 | 0.97785 | -0.15576 | 0.13962
11 | 0.0003462 | 8.6303e-05 | -0.00034619 | -8.6764e-05 | 6.3155e-09 | -4.6037e-07 | 0.00052517 | 0.00052533 | 0.00052533 | 0.98061 | -0.13598 | 0.98059 | -0.13612 | 0.19457
12 | -0.0003462 | -8.6303e-05 | 0.0003462 | 8.6058e-05 | 3.3574e-09 | -2.4486e-07 | 0.00052517 | 0.00052508 | 0.00052517 | 0.98061 | -0.13598 | 0.98062 | -0.13591 | 0.19451
13 | -0.00051103 | -0.00012737 | 0.00051103 | 0.00012732 | 1.4317e-09 | -4.762e-08 | 0.00077519 | 0.00077517 | 0.00077519 | 0.98062 | -0.13591 | 0.98063 | -0.13589 | 0.28711
14 | -0.00030377 | -7.6043e-05 | 0.00030377 | 7.5917e-05 | 1.3496e-09 | -1.2639e-07 | 0.00046231 | 0.00046226 | 0.00046231 | 0.97768 | -0.15701 | 0.97768 | -0.15698 | 0.17122
15 | -0.0008719 | -0.00021762 | 0.00087191 | 0.00021749 | 1.122e-08 | -1.2385e-07 | 0.0013266 | 0.0013265 | 0.0013266 | 0.97778 | -0.15626 | 0.9778 | -0.15617 | 0.49132
16 | -0.00038625 | -9.6587e-05 | 0.00038625 | 9.6407e-05 | 3.1268e-09 | -1.8069e-07 | 0.00058779 | 0.00058773 | 0.00058779 | 0.97768 | -0.15698 | 0.97769 | -0.15692 | 0.2177
17 | -0.00048155 | -0.00012029 | 0.00048155 | 0.00012016 | 3.3722e-09 | -1.2493e-07 | 0.00073275 | 0.00073271 | 0.00073275 | 0.97769 | -0.15692 | 0.9777 | -0.15687 | 0.27139
18 | -0.00057726 | -0.00014415 | 0.00057726 | 0.00014415 | 5.4661e-12 | -1.5068e-10 | 0.00087837 | 0.00087837 | 0.00087837 | 0.9777 | -0.15687 | 0.9777 | -0.15687 | 0.32532
19 | -0.00066044 | -0.000165 | 0.00066044 | 0.00016496 | 2.1835e-09 | -4.2609e-08 | 0.001005 | 0.001005 | 0.001005 | 0.9777 | -0.15687 | 0.9777 | -0.15685 | 0.37221
20 | -0.00076539 | -0.00019126 | 0.0007654 | 0.00019117 | 5.8428e-09 | -8.432e-08 | 0.0011647 | 0.0011647 | 0.0011647 | 0.9777 | -0.15685 | 0.97771 | -0.15679 | 0.43137
21 | -0.00096055 | -0.00023971 | 0.00096055 | 0.00023971 | 3.468e-10 | -3.1307e-09 | 0.0014614 | 0.0014614 | 0.0014614 | 0.9778 | -0.15617 | 0.9778 | -0.15616 | 0.54126
22 | -0.001044 | -0.00026061 | 0.001044 | 0.00026049 | 1.6194e-08 | -1.228e-07 | 0.0015883 | 0.0015883 | 0.0015883 | 0.9778 | -0.15616 | 0.97781 | -0.15605 | 0.58828
23 | -0.0008595 | -0.00021476 | 0.00085951 | 0.00021468 | 6.6864e-09 | -7.599e-08 | 0.0013079 | 0.0013079 | 0.0013079 | 0.97771 | -0.15679 | 0.97772 | -0.15674 | 0.4844
24 | 0.00040709 | 0.00010142 | -0.00040709 | -0.0001016 | 3.392e-09 | -1.7624e-07 | 0.00061948 | 0.00061955 | 0.00061955 | 0.97751 | -0.15825 | 0.9775 | -0.15831 | 0.22946
25 | -0.0005175 | -0.00012909 | 0.0005175 | 0.00012909 | 1.614e-10 | -5.1655e-09 | 0.00078755 | 0.00078755 | 0.00078755 | 0.97751 | -0.15825 | 0.97751 | -0.15825 | 0.29169
26 | 0.00028365 | 7.0658e-05 | -0.00028365 | -7.0746e-05 | 8.2136e-10 | -8.8242e-08 | 0.00043163 | 0.00043167 | 0.00043167 | 0.9775 | -0.15831 | 0.9775 | -0.15833 | 0.15988
27 | -0.00062801 | -0.00015678 | 0.00062802 | 0.00015661 | 7.7147e-09 | -1.6671e-07 | 0.00095577 | 0.00095571 | 0.00095577 | 0.97751 | -0.15825 | 0.97752 | -0.15816 | 0.35399
28 | 9.9529e-05 | 2.4854e-05 | -9.9529e-05 | -2.4944e-05 | 1.0382e-10 | -9.083e-08 | 0.00015148 | 0.00015151 | 0.00015151 | 0.9775 | -0.15833 | 0.97749 | -0.15834 | 0.056115
29 | 0.00018412 | 4.5892e-05 | -0.00018412 | -4.5976e-05 | 3.2739e-10 | -8.3639e-08 | 0.00028019 | 0.00028022 | 0.00028022 | 0.9775 | -0.15833 | 0.97749 | -0.15835 | 0.10378
30 | -0.00073625 | -0.00018374 | 0.00073625 | 0.00018372 | 1.3145e-09 | -2.053e-08 | 0.0011205 | 0.0011205 | 0.0011205 | 0.97752 | -0.15816 | 0.97752 | -0.15815 | 0.41499
31 | 9.7978e-05 | 2.4388e-05 | -9.7978e-05 | -2.4556e-05 | 1.8613e-10 | -1.6808e-07 | 0.00014909 | 0.00014915 | 0.00014915 | 0.97749 | -0.15835 | 0.97749 | -0.15836 | 0.055241
32 | -0.00091366 | -0.00022818 | 0.00091366 | 0.00022816 | 1.5782e-09 | -1.5791e-08 | 0.0013905 | 0.0013905 | 0.0013905 | 0.97752 | -0.15815 | 0.97752 | -0.15813 | 0.515
33 | -0.001184 | -0.00029592 | 0.001184 | 0.00029575 | 2.9281e-08 | -1.699e-07 | 0.001802 | 0.001802 | 0.001802 | 0.97752 | -0.15813 | 0.97755 | -0.15795 | 0.66742
34 | -0.0012872 | -0.0003216 | 0.0012872 | 0.00032148 | 2.307e-08 | -1.1191e-07 | 0.0019589 | 0.0019589 | 0.0019589 | 0.97755 | -0.15795 | 0.97757 | -0.15782 | 0.72554
35 | -0.00094844 | -0.00023697 | 0.00094846 | 0.00023675 | 2.3708e-08 | -2.1967e-07 | 0.0014432 | 0.0014431 | 0.0014432 | 0.97772 | -0.15674 | 0.97774 | -0.15655 | 0.53452
36 | -0.0010607 | -0.00026487 | 0.0010607 | 0.00026487 | 5.0724e-10 | -3.7194e-09 | 0.0016139 | 0.0016139 | 0.0016139 | 0.97774 | -0.15655 | 0.97774 | -0.15655 | 0.59773
37 | -0.0011873 | -0.0002966 | 0.0011873 | 0.00029641 | 3.3878e-08 | -1.9561e-07 | 0.0018066 | 0.0018065 | 0.0018066 | 0.97774 | -0.15655 | 0.97777 | -0.15634 | 0.66911
38 | -0.0037301 | -0.00093065 | 0.0037301 | 0.00093065 | 2.2154e-08 | -5.3057e-09 | 0.0056751 | 0.0056751 | 0.0056751 | 0.97777 | -0.15634 | 0.97778 | -0.1563 | 2.1019
39 | 0.0025427 | 0.00063424 | -0.0025425 | -0.00063445 | 2.1286e-07 | -2.0399e-07 | 0.0038686 | 0.0038687 | 0.0038687 | 0.97777 | -0.15634 | 0.97769 | -0.15695 | 1.4328
40 | -0.0039281 | -0.00098028 | 0.0039284 | 0.00098023 | 2.5069e-07 | -4.4668e-08 | 0.0059764 | 0.0059764 | 0.0059764 | 0.97778 | -0.1563 | 0.97784 | -0.15583 | 2.2135
41 | 0.0023036 | 0.00057456 | -0.0023034 | -0.00057473 | 1.4059e-07 | -1.7591e-07 | 0.003505 | 0.003505 | 0.003505 | 0.97769 | -0.15695 | 0.97762 | -0.1574 | 1.2982
42 | -0.0051596 | -0.0012874 | 0.0051599 | 0.0012875 | 2.8651e-07 | 1.671e-08 | 0.0078495 | 0.0078494 | 0.0078495 | 0.97784 | -0.15583 | 0.9779 | -0.15543 | 2.9072
43 | 0.0012312 | 0.0003072 | -0.0012312 | -0.00030732 | 2.0887e-08 | -1.1164e-07 | 0.0018731 | 0.0018731 | 0.0018731 | 0.97784 | -0.15583 | 0.97782 | -0.15596 | 0.69376
44 | 0.0021443 | 0.00053485 | -0.0021443 | -0.00053488 | 1.6759e-08 | -2.5186e-08 | 0.0032628 | 0.0032628 | 0.0032628 | 0.97762 | -0.1574 | 0.97762 | -0.15745 | 1.2085
45 | -8.64e-05 | -2.1654e-05 | 8.64e-05 | 2.163e-05 | 2.091e-11 | -2.4231e-08 | 0.00013152 | 0.00013152 | 0.00013152 | 0.9775 | -0.15831 | 0.9775 | -0.15831 | 0.048713
46 | -0.00020337 | -5.0944e-05 | 0.00020337 | 5.0748e-05 | 9.3488e-10 | -1.9566e-07 | 0.00030957 | 0.0003095 | 0.00030957 | 0.9775 | -0.15831 | 0.9775 | -0.15827 | 0.11465
47 | -0.00033786 | -8.4456e-05 | 0.00033787 | 8.4273e-05 | 2.4197e-09 | -1.8292e-07 | 0.00051424 | 0.00051417 | 0.00051424 | 0.9775 | -0.15827 | 0.97751 | -0.15822 | 0.19046
48 | -0.0004456 | -0.00011127 | 0.0004456 | 0.00011111 | 3.8413e-09 | -1.6633e-07 | 0.00067817 | 0.00067811 | 0.00067817 | 0.97751 | -0.15822 | 0.97752 | -0.15816 | 0.25117
49 | -0.00055583 | -0.00013873 | 0.00055584 | 0.0001386 | 4.7196e-09 | -1.307e-07 | 0.00084591 | 0.00084586 | 0.00084591 | 0.97752 | -0.15816 | 0.97753 | -0.15809 | 0.3133
50 | -0.00055584 | -0.0001386 | 0.00055585 | 0.00013836 | 8.6435e-09 | -2.3941e-07 | 0.00084586 | 0.00084577 | 0.00084586 | 0.97753 | -0.15809 | 0.97754 | -0.15798 | 0.31328
51 | -0.00065462 | -0.00016312 | 0.00065462 | 0.00016297 | 7.3883e-09 | -1.4677e-07 | 0.00099612 | 0.00099606 | 0.00099612 | 0.97754 | -0.15798 | 0.97756 | -0.1579 | 0.36893
52 | -0.0020416 | -0.00050935 | 0.0020417 | 0.00050917 | 1.0303e-07 | -1.7486e-07 | 0.0031068 | 0.0031067 | 0.0031068 | 0.97757 | -0.15782 | 0.97762 | -0.15745 | 1.1507
53 | 0.00075441 | 0.00018786 | -0.0007544 | -0.00018798 | 7.8419e-09 | -1.1655e-07 | 0.0011479 | 0.0011479 | 0.0011479 | 0.97757 | -0.15782 | 0.97756 | -0.1579 | 0.42516
54 | -0.0052756 | -0.0013165 | 0.0052759 | 0.0013165 | 2.565e-07 | 1.8584e-08 | 0.0080256 | 0.0080256 | 0.0080256 | 0.9779 | -0.15543 | 0.97795 | -0.15508 | 2.9724
55 | 0.0011417 | 0.00028489 | -0.0011417 | -0.00028498 | 1.437e-08 | -9.0212e-08 | 0.001737 | 0.001737 | 0.001737 | 0.97782 | -0.15596 | 0.97781 | -0.15605 | 0.64334
56 | -0.0055253 | -0.001379 | 0.0055262 | 0.0013791 | 8.5918e-07 | 8.5872e-08 | 0.0084051 | 0.0084051 | 0.0084051 | 0.97795 | -0.15508 | 0.9781 | -0.15394 | 3.113
57 | -0.005621 | -0.0014028 | 0.0056212 | 0.0014029 | 2.4445e-07 | 2.6744e-08 | 0.0085492 | 0.0085492 | 0.0085492 | 0.9781 | -0.15394 | 0.97815 | -0.15363 | 3.1664
58 | -0.0057992 | -0.0014475 | 0.0057994 | 0.0014475 | 1.7187e-07 | 2.166e-08 | 0.00882 | 0.00882 | 0.00882 | 0.97815 | -0.15363 | 0.97818 | -0.15341 | 3.2667
59 | -0.0031842 | -0.00079643 | 0.0031843 | 0.00079637 | 1.2367e-07 | -5.8388e-08 | 0.0048445 | 0.0048445 | 0.0048445 | 0.97792 | -0.15525 | 0.97796 | -0.15497 | 1.7943
60 | 0.003081 | 0.00077057 | -0.0030809 | -0.0007706 | 4.8077e-08 | -2.5501e-08 | 0.0046875 | 0.0046875 | 0.0046875 | 0.97792 | -0.15525 | 0.97791 | -0.15536 | 1.7361
61 | -0.0032904 | -0.00082297 | 0.0032906 | 0.00082291 | 1.4521e-07 | -6.0672e-08 | 0.005006 | 0.0050059 | 0.005006 | 0.97796 | -0.15497 | 0.978 | -0.15465 | 1.8541
62 | 0.0029447 | 0.00073646 | -0.0029446 | -0.00073656 | 1.5301e-07 | -9.4401e-08 | 0.0044803 | 0.0044803 | 0.0044803 | 0.97791 | -0.15536 | 0.97785 | -0.15574 | 1.6594
63 | -0.0033965 | -0.00084946 | 0.0033966 | 0.00084941 | 1.3597e-07 | -5.0123e-08 | 0.0051671 | 0.005167 | 0.0051671 | 0.978 | -0.15465 | 0.97805 | -0.15436 | 1.9137
64 | 0.0026095 | 0.00065294 | -0.0026094 | -0.00065305 | 1.2038e-07 | -1.0719e-07 | 0.0039706 | 0.0039706 | 0.0039706 | 0.97785 | -0.15574 | 0.97781 | -0.15607 | 1.4706
65 | 0.00033508 | 8.3618e-05 | -0.00033508 | -8.3705e-05 | 1.128e-09 | -8.6825e-08 | 0.00050977 | 0.0005098 | 0.0005098 | 0.97785 | -0.15574 | 0.97785 | -0.15576 | 0.18881
66 | -0.0033966 | -0.00084941 | 0.0033968 | 0.00084937 | 1.066e-07 | -3.9304e-08 | 0.005167 | 0.005167 | 0.005167 | 0.97805 | -0.15436 | 0.97808 | -0.15413 | 1.9137
67 | 0.0025029 | 0.00062636 | -0.0025028 | -0.00062644 | 7.8001e-08 | -7.809e-08 | 0.0038086 | 0.0038086 | 0.0038086 | 0.97781 | -0.15607 | 0.97778 | -0.1563 | 1.4106
68 | -0.0034794 | -0.00087009 | 0.0034794 | 0.00087009 | 2.8544e-10 | -9.46e-11 | 0.0052928 | 0.0052928 | 0.0052928 | 0.97808 | -0.15413 | 0.97808 | -0.15413 | 1.9603
69 | 0.0018237 | 0.00045623 | -0.0018236 | -0.00045644 | 9.4723e-08 | -2.1078e-07 | 0.0027751 | 0.0027752 | 0.0027752 | 0.97778 | -0.1563 | 0.97772 | -0.15668 | 1.0279
70 | -0.00041757 | -0.00010465 | 0.00041757 | 0.00010452 | 2.7514e-09 | -1.363e-07 | 0.00063501 | 0.00063496 | 0.00063501 | 0.97848 | -0.15122 | 0.97849 | -0.15117 | 0.23519
71 | -0.00086654 | -0.00021704 | 0.00086654 | 0.00021703 | 8.948e-10 | -1.0029e-08 | 0.0013177 | 0.0013177 | 0.0013177 | 0.97849 | -0.15117 | 0.97849 | -0.15116 | 0.48805
72 | -0.0035925 | -0.00089842 | 0.0035928 | 0.00089832 | 3.5565e-07 | -1.0277e-07 | 0.0054648 | 0.0054647 | 0.0054648 | 0.97808 | -0.15413 | 0.97818 | -0.15341 | 2.024
73 | 0.0014563 | 0.00036439 | -0.0014563 | -0.00036451 | 3.3216e-08 | -1.2314e-07 | 0.0022162 | 0.0022162 | 0.0022162 | 0.97772 | -0.15668 | 0.9777 | -0.15684 | 0.82083
74 | -0.0012683 | -0.00031771 | 0.0012683 | 0.0003176 | 2.2089e-08 | -1.1105e-07 | 0.0019287 | 0.0019286 | 0.0019287 | 0.97849 | -0.15116 | 0.9785 | -0.15104 | 0.71432
75 | -0.0093922 | -0.0023458 | 0.0093936 | 0.0023462 | 1.3338e-06 | 3.8149e-07 | 0.014285 | 0.014285 | 0.014285 | 0.97818 | -0.15341 | 0.97832 | -0.15238 | 5.2906
76 | -0.0097554 | -0.0024369 | 0.0097567 | 0.0024373 | 1.2671e-06 | 3.7147e-07 | 0.014835 | 0.014835 | 0.014835 | 0.97832 | -0.15238 | 0.97845 | -0.15143 | 5.4945
77 | -0.010383 | -0.0025942 | 0.010383 | 0.0025944 | 4.1453e-07 | 1.2596e-07 | 0.015788 | 0.015788 | 0.015788 | 0.97845 | -0.15143 | 0.97849 | -0.15114 | 5.8472
78 | -0.01079 | -0.0026963 | 0.010792 | 0.0026969 | 2.2086e-06 | 6.8426e-07 | 0.016406 | 0.016406 | 0.016406 | 0.97849 | -0.15114 | 0.9787 | -0.14966 | 6.0762
79 | -0.011275 | -0.0028179 | 0.011275 | 0.0028181 | 7.2537e-07 | 2.2926e-07 | 0.017139 | 0.017139 | 0.017139 | 0.9787 | -0.14966 | 0.97876 | -0.14919 | 6.3479
80 | -0.011964 | -0.0029908 | 0.011969 | 0.0029923 | 4.8071e-06 | 1.5561e-06 | 0.018187 | 0.018187 | 0.018187 | 0.97876 | -0.14919 | 0.97917 | -0.14627 | 6.7358
81 | -0.013037 | -0.00326 | 0.01304 | 0.003261 | 2.9415e-06 | 9.802e-07 | 0.01981 | 0.01981 | 0.01981 | 0.97917 | -0.14627 | 0.9794 | -0.14464 | 7.337
82 | 0.0013142 | 0.00032897 | -0.0013141 | -0.00032918 | 4.4867e-08 | -2.089e-07 | 0.0019983 | 0.0019984 | 0.0019984 | 0.9785 | -0.15104 | 0.97847 | -0.15128 | 0.74014
83 | -0.0025825 | -0.00064657 | 0.0025825 | 0.00064651 | 6.7399e-08 | -6.2063e-08 | 0.0039269 | 0.0039269 | 0.0039269 | 0.9785 | -0.15104 | 0.97853 | -0.15085 | 1.4544
84 | -8.2218e-05 | -2.0606e-05 | 8.2218e-05 | 2.0553e-05 | 4.114e-11 | -5.2819e-08 | 0.00012513 | 0.00012512 | 0.00012513 | 0.97768 | -0.15699 | 0.97768 | -0.15699 | 0.046346
85 | -0.00052974 | -0.00013271 | 0.00052975 | 0.00013256 | 4.906e-09 | -1.498e-07 | 0.00080624 | 0.00080619 | 0.00080624 | 0.97768 | -0.15699 | 0.97769 | -0.15692 | 0.29861
86 | -0.00064119 | -0.00015994 | 0.0006412 | 0.00015973 | 1.0346e-08 | -2.1712e-07 | 0.00097269 | 0.00097261 | 0.00097269 | 0.98063 | -0.13589 | 0.98064 | -0.13577 | 0.36025
87 | -0.00071394 | -0.00017873 | 0.00071395 | 0.0001786 | 7.7339e-09 | -1.2869e-07 | 0.0010865 | 0.0010865 | 0.0010865 | 0.97769 | -0.15692 | 0.9777 | -0.15684 | 0.40242
88 | 0.00059217 | 0.00014828 | -0.00059217 | -0.00014841 | 5.4159e-09 | -1.3192e-07 | 0.00090121 | 0.00090126 | 0.00090126 | 0.9777 | -0.15684 | 0.97769 | -0.15691 | 0.3338
89 | 0.0011915 | 0.00029722 | -0.0011914 | -0.00029732 | 1.6866e-08 | -9.7912e-08 | 0.0018074 | 0.0018074 | 0.0018074 | 0.98067 | -0.13556 | 0.98066 | -0.13566 | 0.6694
90 | -0.0013518 | -0.00033742 | 0.0013519 | 0.00033729 | 3.027e-08 | -1.3391e-07 | 0.0020507 | 0.0020507 | 0.0020507 | 0.98067 | -0.13556 | 0.98069 | -0.13539 | 0.75952
91 | 0.0010572 | 0.00026367 | -0.0010571 | -0.00026379 | 1.6751e-08 | -1.2525e-07 | 0.0016036 | 0.0016037 | 0.0016037 | 0.98066 | -0.13566 | 0.98064 | -0.13577 | 0.59396
92 | 0.00068663 | 0.0001715 | -0.00068662 | -0.00017162 | 6.7601e-09 | -1.2338e-07 | 0.0010416 | 0.0010417 | 0.0010417 | 0.98069 | -0.13539 | 0.98068 | -0.13546 | 0.3858
93 | 0.00025302 | 6.3134e-05 | -0.00025302 | -6.324e-05 | 7.7679e-10 | -1.0632e-07 | 0.00038381 | 0.00038385 | 0.00038385 | 0.98069 | -0.13539 | 0.98069 | -0.13541 | 0.14217
94 | -0.0022915 | -0.00057192 | 0.0022917 | 0.00057166 | 2.0074e-07 | -2.5876e-07 | 0.0034761 | 0.003476 | 0.0034761 | 0.98069 | -0.13539 | 0.98078 | -0.13475 | 1.2874
95 | 0.00041593 | 0.00010407 | -0.00041593 | -0.00010424 | 3.4651e-09 | -1.7456e-07 | 0.00063107 | 0.00063114 | 0.00063114 | 0.98064 | -0.13577 | 0.98063 | -0.13583 | 0.23375
96 | 0.00056925 | 0.00014221 | -0.00056924 | -0.00014241 | 7.4105e-09 | -1.9806e-07 | 0.00086357 | 0.00086364 | 0.00086364 | 0.98068 | -0.13546 | 0.98067 | -0.13556 | 0.31987
97 | 0.00014053 | 3.5046e-05 | -0.00014053 | -3.5219e-05 | 3.9e-10 | -1.7335e-07 | 0.00021316 | 0.00021322 | 0.00021322 | 0.98069 | -0.13541 | 0.98069 | -0.13543 | 0.078972
98 | -0.0032825 | -0.00081932 | 0.0032829 | 0.00081914 | 4.3212e-07 | -1.864e-07 | 0.0049789 | 0.0049788 | 0.0049789 | 0.98078 | -0.13475 | 0.98092 | -0.1338 | 1.844
99 | 0.00099076 | 0.00024766 | -0.00099075 | -0.0002478 | 1.5408e-08 | -1.3202e-07 | 0.0015029 | 0.001503 | 0.001503 | 0.98078 | -0.13475 | 0.98077 | -0.13487 | 0.55666
100 | 0.00043517 | 0.0001088 | -0.00043516 | -0.00010891 | 2.4094e-09 | -1.1084e-07 | 0.00066021 | 0.00066025 | 0.00066025 | 0.98067 | -0.13556 | 0.98067 | -0.1356 | 0.24454
101 | -0.0032829 | -0.00081914 | 0.0032835 | 0.00081888 | 5.8829e-07 | -2.5394e-07 | 0.0049788 | 0.0049786 | 0.0049788 | 0.98092 | -0.1338 | 0.9811 | -0.13249 | 1.844
102 | 0.00080418 | 0.00020104 | -0.00080417 | -0.00020116 | 9.6038e-09 | -1.2681e-07 | 0.0012199 | 0.00122 | 0.00122 | 0.98077 | -0.13487 | 0.98076 | -0.13495 | 0.45184
103 | 0.00028789 | 7.2005e-05 | -0.00028789 | -7.213e-05 | 1.1828e-09 | -1.2489e-07 | 0.00043678 | 0.00043683 | 0.00043683 | 0.98067 | -0.1356 | 0.98066 | -0.13563 | 0.16179
104 | -0.0034287 | -0.00085527 | 0.0034289 | 0.0008552 | 2.1193e-07 | -7.7184e-08 | 0.0051988 | 0.0051987 | 0.0051988 | 0.9811 | -0.13249 | 0.98116 | -0.13204 | 1.9255
105 | 0.00063167 | 0.00015793 | -0.00063167 | -0.00015798 | 2.1923e-09 | -4.744e-08 | 0.00095824 | 0.00095826 | 0.00095826 | 0.98076 | -0.13495 | 0.98075 | -0.13498 | 0.35491
106 | 0.00014735 | 3.6907e-05 | -0.00014735 | -3.6929e-05 | 5.5947e-11 | -2.2593e-08 | 0.00022357 | 0.00022358 | 0.00022358 | 0.98066 | -0.13563 | 0.98066 | -0.13563 | 0.082808
107 | 0.00052542 | 0.00013142 | -0.00052541 | -0.00013168 | 8.3046e-09 | -2.6155e-07 | 0.00079675 | 0.00079684 | 0.00079684 | 0.98116 | -0.13204 | 0.98114 | -0.13215 | 0.29513
108 | -0.0039543 | -0.00098661 | 0.0039544 | 0.0009866 | 8.1418e-08 | -1.453e-08 | 0.0059955 | 0.0059955 | 0.0059955 | 0.98116 | -0.13204 | 0.98118 | -0.13189 | 2.2206
109 | 0.00048209 | 0.00012049 | -0.00048208 | -0.00012064 | 4.0859e-09 | -1.5292e-07 | 0.00073132 | 0.00073137 | 0.00073137 | 0.98075 | -0.13498 | 0.98074 | -0.13504 | 0.27088
110 | -0.0037584 | -0.00094097 | 0.0037588 | 0.00094088 | 3.7709e-07 | -8.7535e-08 | 0.0057143 | 0.0057142 | 0.0057143 | 0.97865 | -0.15 | 0.97875 | -0.14928 | 2.1164
111 | 0.0037584 | 0.00094097 | -0.0037582 | -0.00094101 | 1.9102e-07 | -4.4321e-08 | 0.0057143 | 0.0057143 | 0.0057143 | 0.97865 | -0.15 | 0.9786 | -0.15037 | 2.1164
112 | -0.0041321 | -0.0010344 | 0.0041325 | 0.0010344 | 3.2927e-07 | -4.143e-08 | 0.0062818 | 0.0062817 | 0.0062818 | 0.97875 | -0.14928 | 0.97883 | -0.1487 | 2.3266
113 | 0.0033781 | 0.00084573 | -0.003378 | -0.00084574 | 3.7477e-08 | -1.4188e-08 | 0.0051362 | 0.0051362 | 0.0051362 | 0.9786 | -0.15037 | 0.97859 | -0.15045 | 1.9023
114 | 0.00028712 | 7.178e-05 | -0.00028712 | -7.1868e-05 | 8.2364e-10 | -8.7472e-08 | 0.00043556 | 0.00043559 | 0.00043559 | 0.98074 | -0.13504 | 0.98074 | -0.13506 | 0.16133
115 | 0.00014641 | 3.6603e-05 | -0.00014641 | -3.6694e-05 | 2.2154e-10 | -9.0718e-08 | 0.00022211 | 0.00022214 | 0.00022214 | 0.98074 | -0.13506 | 0.98074 | -0.13507 | 0.082274
116 | -0.0042121 | -0.0010512 | 0.0042126 | 0.0010511 | 5.1417e-07 | -5.7455e-08 | 0.0063862 | 0.0063861 | 0.0063862 | 0.98118 | -0.13189 | 0.9813 | -0.131 | 2.3653
117 | -0.0046334 | -0.0011599 | 0.0046334 | 0.0011599 | 3.8316e-08 | -8.2217e-10 | 0.0070432 | 0.0070432 | 0.0070432 | 0.97883 | -0.1487 | 0.97884 | -0.14864 | 2.6086
118 | 0.0029826 | 0.00074663 | -0.0029824 | -0.00074673 | 1.6404e-07 | -9.7497e-08 | 0.0045349 | 0.004535 | 0.004535 | 0.97859 | -0.15045 | 0.97853 | -0.15085 | 1.6796
119 | 0.00091888 | 0.00023013 | -0.00091888 | -0.00023019 | 6.3425e-09 | -6.2944e-08 | 0.0013973 | 0.0013974 | 0.0013974 | 0.97847 | -0.15128 | 0.97846 | -0.15133 | 0.51754
120 | -0.0047736 | -0.0011951 | 0.0047743 | 0.0011951 | 6.9576e-07 | 1.3772e-09 | 0.0072563 | 0.0072562 | 0.0072563 | 0.97884 | -0.14864 | 0.97899 | -0.14758 | 2.6875
121 | 0.00044444 | 0.00011129 | -0.00044444 | -0.00011139 | 2.2923e-09 | -1.0012e-07 | 0.00067585 | 0.00067589 | 0.00067589 | 0.97846 | -0.15133 | 0.97846 | -0.15137 | 0.25033
122 | 0.00048072 | 0.00012029 | -0.00048072 | -0.00012042 | 3.4934e-09 | -1.3052e-07 | 0.00073061 | 0.00073066 | 0.00073066 | 0.97899 | -0.14758 | 0.97898 | -0.14764 | 0.27061
123 | 0.00031336 | 7.8263e-05 | -0.00031336 | -7.8511e-05 | 2.8112e-09 | -2.4867e-07 | 0.0004762 | 0.00047629 | 0.00047629 | 0.97899 | -0.14758 | 0.97898 | -0.14765 | 0.1764
124 | -0.0055684 | -0.0013936 | 0.005569 | 0.0013937 | 6.4418e-07 | 6.6507e-08 | 0.008463 | 0.008463 | 0.008463 | 0.97899 | -0.14758 | 0.9791 | -0.14675 | 3.1345
125 | 0.00030783 | 7.7094e-05 | -0.00030783 | -7.7116e-05 | 2.371e-10 | -2.1737e-08 | 0.00046787 | 0.00046788 | 0.00046788 | 0.97898 | -0.14764 | 0.97898 | -0.14764 | 0.17329
126 | 0.00012934 | 3.2392e-05 | -0.00012934 | -3.2415e-05 | 4.4669e-11 | -2.3229e-08 | 0.00019658 | 0.00019659 | 0.00019659 | 0.97898 | -0.14765 | 0.97898 | -0.14765 | 0.072811
127 | -0.005909 | -0.0014789 | 0.0059091 | 0.0014789 | 9.2813e-08 | 1.2497e-08 | 0.0089796 | 0.0089796 | 0.0089796 | 0.9791 | -0.14675 | 0.97912 | -0.14663 | 3.3258
128 | 0.00016064 | 4.0228e-05 | -0.00016064 | -4.0261e-05 | 9.8079e-11 | -3.3111e-08 | 0.00024416 | 0.00024417 | 0.00024417 | 0.97898 | -0.14764 | 0.97898 | -0.14765 | 0.090435
129 | -0.0062838 | -0.0015728 | 0.006285 | 0.001573 | 1.203e-06 | 1.9673e-07 | 0.0095491 | 0.009549 | 0.0095491 | 0.97912 | -0.14663 | 0.97931 | -0.14525 | 3.5367
130 | -0.0066965 | -0.0016761 | 0.006697 | 0.0016763 | 5.6406e-07 | 1.0706e-07 | 0.010174 | 0.010174 | 0.010174 | 0.97931 | -0.14525 | 0.9794 | -0.14464 | 3.7682
131 | -0.019737 | -0.0049373 | 0.019741 | 0.0049387 | 3.939e-06 | 1.4266e-06 | 0.029984 | 0.029984 | 0.029984 | 0.9794 | -0.14464 | 0.9796 | -0.14319 | 11.1052
132 | -0.020438 | -0.0051134 | 0.020451 | 0.0051181 | 1.292e-05 | 4.6985e-06 | 0.031043 | 0.031043 | 0.031043 | 0.9796 | -0.14319 | 0.98024 | -0.13861 | 11.4973
133 | -0.021465 | -0.0053721 | 0.02148 | 0.0053776 | 1.4954e-05 | 5.4666e-06 | 0.032581 | 0.032581 | 0.032581 | 0.98024 | -0.13861 | 0.98094 | -0.13357 | 12.0671
134 | -0.022091 | -0.0055309 | 0.022112 | 0.0055383 | 2.0144e-05 | 7.3845e-06 | 0.033509 | 0.033509 | 0.033509 | 0.98094 | -0.13357 | 0.98186 | -0.12697 | 12.4107
135 | 0.005574 | 0.0013913 | -0.0055733 | -0.0013912 | 6.5763e-07 | 6.6072e-08 | 0.0084453 | 0.0084454 | 0.0084454 | 0.98186 | -0.12697 | 0.98175 | -0.12783 | 3.1279
136 | -0.047823 | -0.011983 | 0.04789 | 0.012008 | 6.6456e-05 | 2.5303e-05 | 0.072475 | 0.072475 | 0.072475 | 0.98186 | -0.12697 | 0.98327 | -0.11694 | 26.8427
137 | 0.020138 | 0.0050533 | -0.020118 | -0.0050459 | 2.0262e-05 | 7.3525e-06 | 0.030521 | 0.030521 | 0.030521 | 0.98186 | -0.12697 | 0.98085 | -0.13423 | 11.3042
138 | 0.00064951 | 0.0001625 | -0.0006495 | -0.00016278 | 1.2659e-08 | -2.7421e-07 | 0.00097142 | 0.00097152 | 0.00097152 | 0.99481 | -0.036329 | 0.99479 | -0.03647 | 0.35982
139 | -0.0014309 | -0.00035834 | 0.001431 | 0.00035809 | 6.076e-08 | -2.5266e-07 | 0.0021402 | 0.0021401 | 0.0021402 | 0.99481 | -0.036329 | 0.99485 | -0.036022 | 0.79267
140 | -0.0020477 | -0.00051265 | 0.0020478 | 0.00051241 | 1.2924e-07 | -2.3706e-07 | 0.0030625 | 0.0030624 | 0.0030625 | 0.99485 | -0.036022 | 0.99492 | -0.035565 | 1.1343
141 | -0.0027593 | -0.00069074 | 0.0027596 | 0.00069055 | 2.3045e-07 | -1.9303e-07 | 0.0041266 | 0.0041265 | 0.0041266 | 0.99492 | -0.035565 | 0.995 | -0.03496 | 1.5284
142 | -0.00074052 | -0.00018559 | 0.00074053 | 0.00018529 | 1.8213e-08 | -3.0041e-07 | 0.001109 | 0.0011089 | 0.001109 | 0.99361 | -0.044236 | 0.99363 | -0.044058 | 0.41074
143 | -0.0024523 | -0.0006143 | 0.0024525 | 0.00061407 | 1.9938e-07 | -2.3023e-07 | 0.0036724 | 0.0036722 | 0.0036724 | 0.99363 | -0.044058 | 0.99371 | -0.04347 | 1.3601
144 | -0.0041693 | -0.0010439 | 0.0041698 | 0.0010438 | 4.7076e-07 | -7.1048e-08 | 0.0062348 | 0.0062347 | 0.0062348 | 0.995 | -0.03496 | 0.99512 | -0.034142 | 2.3092
145 | -0.0037876 | -0.00094867 | 0.003788 | 0.00094858 | 3.7496e-07 | -9.7829e-08 | 0.0056714 | 0.0056714 | 0.0056714 | 0.99371 | -0.04347 | 0.99382 | -0.042754 | 2.1005
146 | -0.0054462 | -0.0013637 | 0.0054465 | 0.0013637 | 2.7985e-07 | 1.9769e-08 | 0.0081434 | 0.0081433 | 0.0081434 | 0.99512 | -0.034142 | 0.99517 | -0.03377 | 3.0161
147 | -0.16309 | -0.041148 | 0.16341 | 0.04127 | 0.00031841 | 0.00012202 | 0.24429 | 0.24429 | 0.24429 | 0.99382 | -0.042754 | 0.99582 | -0.028866 | 45.2392
148 | 0.15931 | 0.040199 | -0.15877 | -0.039995 | 0.00053186 | 0.00020379 | 0.23862 | 0.23862 | 0.23862 | 0.99382 | -0.042754 | 0.99039 | -0.066623 | 44.1891
149 | -0.0065652 | -0.0016441 | 0.0065663 | 0.0016443 | 1.1395e-06 | 1.9198e-07 | 0.009816 | 0.0098159 | 0.009816 | 0.99517 | -0.03377 | 0.99535 | -0.032515 | 3.6356
150 | 0.0054658 | 0.0013643 | -0.0054646 | -0.0013641 | 1.1756e-06 | 1.0496e-07 | 0.0082824 | 0.0082825 | 0.0082825 | 0.98175 | -0.12783 | 0.98153 | -0.1294 | 3.0676
151 | -0.048138 | -0.01207 | 0.048182 | 0.012087 | 4.3838e-05 | 1.6693e-05 | 0.072851 | 0.072851 | 0.072851 | 0.98327 | -0.11694 | 0.9842 | -0.11038 | 26.9818
152 | 0.018688 | 0.0046875 | -0.018679 | -0.0046844 | 8.6762e-06 | 3.1188e-06 | 0.028352 | 0.028352 | 0.028352 | 0.98085 | -0.13423 | 0.98038 | -0.13758 | 10.5007
153 | 0.00096473 | 0.00024134 | -0.0009647 | -0.00024157 | 2.587e-08 | -2.3505e-07 | 0.0014624 | 0.0014625 | 0.0014625 | 0.98153 | -0.1294 | 0.9815 | -0.12959 | 0.54166
154 | 0.0044999 | 0.0011228 | -0.0044992 | -0.0011228 | 6.3807e-07 | -3.2398e-08 | 0.0068201 | 0.0068202 | 0.0068202 | 0.98153 | -0.1294 | 0.98138 | -0.13043 | 2.526
155 | -0.051494 | -0.012917 | 0.051542 | 0.012935 | 4.7358e-05 | 1.8055e-05 | 0.077859 | 0.077859 | 0.077859 | 0.9842 | -0.11038 | 0.98513 | -0.10375 | 28.8366
156 | 0.015381 | 0.0038577 | -0.015374 | -0.0038554 | 6.6463e-06 | 2.31e-06 | 0.023346 | 0.023346 | 0.023346 | 0.98038 | -0.13758 | 0.97994 | -0.1407 | 8.6466
157 | -0.16437 | -0.04151 | 0.1645 | 0.04156 | 0.00013016 | 4.9881e-05 | 0.24572 | 0.24572 | 0.24572 | 0.99582 | -0.028866 | 0.99663 | -0.023238 | 45.5043
158 | 0.096573 | 0.02435 | -0.096482 | -0.024315 | 9.1071e-05 | 3.4671e-05 | 0.14515 | 0.14515 | 0.14515 | 0.99039 | -0.066623 | 0.98943 | -0.07336 | 26.8792
159 | 0.062201 | 0.015646 | -0.062118 | -0.015614 | 8.3013e-05 | 3.1732e-05 | 0.093473 | 0.093473 | 0.093473 | 0.99039 | -0.066623 | 0.98903 | -0.076207 | 34.6198
160 | -0.16546 | -0.0418 | 0.16555 | 0.041836 | 9.278e-05 | 3.5558e-05 | 0.24715 | 0.24715 | 0.24715 | 0.99663 | -0.023238 | 0.99721 | -0.019254 | 45.7694
161 | 0.093764 | 0.023634 | -0.093669 | -0.023598 | 9.5424e-05 | 3.6307e-05 | 0.14106 | 0.14106 | 0.14106 | 0.98943 | -0.07336 | 0.98839 | -0.080635 | 26.1224
162 | 0.060486 | 0.015205 | -0.060486 | -0.015205 | 3.6524e-07 | 1.3957e-07 | 0.091019 | 0.091019 | 0.091019 | 0.98903 | -0.076207 | 0.98902 | -0.07625 | 33.7108
163 | 0.00048294 | 0.00012083 | -0.00048294 | -0.00012104 | 5.4943e-09 | -2.0549e-07 | 0.0007321 | 0.00073217 | 0.00073217 | 0.9815 | -0.12959 | 0.98149 | -0.12967 | 0.27117
164 | 0.0043293 | 0.0010803 | -0.0043291 | -0.0010803 | 2.2382e-07 | -1.9141e-08 | 0.0065626 | 0.0065627 | 0.0065627 | 0.98138 | -0.13043 | 0.98133 | -0.13081 | 2.4306
165 | -0.053173 | -0.013344 | 0.053241 | 0.01337 | 6.8028e-05 | 2.5949e-05 | 0.080323 | 0.080323 | 0.080323 | 0.98513 | -0.10375 | 0.98643 | -0.094548 | 29.7492
166 | 0.015374 | 0.0038554 | -0.015365 | -0.0038523 | 8.9568e-06 | 3.1133e-06 | 0.023346 | 0.023346 | 0.023346 | 0.97994 | -0.1407 | 0.97935 | -0.1449 | 8.6466
167 | 0.0043291 | 0.0010803 | -0.004329 | -0.0010803 | 1.136e-07 | -9.7099e-09 | 0.0065627 | 0.0065627 | 0.0065627 | 0.98133 | -0.13081 | 0.9813 | -0.131 | 2.4306
168 | -0.056317 | -0.014141 | 0.056348 | 0.014153 | 3.1687e-05 | 1.2098e-05 | 0.084962 | 0.084962 | 0.084962 | 0.98643 | -0.094548 | 0.987 | -0.090501 | 31.4676
169 | 0.015365 | 0.0038523 | -0.015358 | -0.0038498 | 7.3137e-06 | 2.5425e-06 | 0.023346 | 0.023346 | 0.023346 | 0.97935 | -0.1449 | 0.97887 | -0.14834 | 8.6467
170 | -0.057979 | -0.014562 | 0.058094 | 0.014606 | 0.0001151 | 4.396e-05 | 0.087421 | 0.08742 | 0.087421 | 0.987 | -0.090501 | 0.98902 | -0.07625 | 32.378
171 | 0.012944 | 0.0032449 | -0.012937 | -0.0032425 | 7.193e-06 | 2.3925e-06 | 0.019677 | 0.019677 | 0.019677 | 0.97887 | -0.14834 | 0.97831 | -0.15235 | 7.2878
172 | 0.01122 | 0.0028121 | -0.011217 | -0.0028112 | 3.0379e-06 | 9.5857e-07 | 0.017065 | 0.017066 | 0.017066 | 0.97831 | -0.15235 | 0.97803 | -0.15431 | 6.3206
173 | 0.011217 | 0.0028112 | -0.011209 | -0.0028086 | 8.1893e-06 | 2.5846e-06 | 0.017066 | 0.017066 | 0.017066 | 0.97803 | -0.15431 | 0.9773 | -0.15959 | 6.3206
174 | 0.0092643 | 0.0023213 | -0.0092604 | -0.0023202 | 3.8676e-06 | 1.0974e-06 | 0.014105 | 0.014106 | 0.014106 | 0.9773 | -0.15959 | 0.97688 | -0.1626 | 5.2243
175 | 0.0069081 | 0.0017307 | -0.0069064 | -0.0017303 | 1.6616e-06 | 3.3806e-07 | 0.010522 | 0.010522 | 0.010522 | 0.97688 | -0.1626 | 0.97663 | -0.16434 | 3.8972
176 | 0.0043747 | 0.0010958 | -0.0043737 | -0.0010959 | 1.0398e-06 | -6.932e-08 | 0.0066652 | 0.0066654 | 0.0066654 | 0.97663 | -0.16434 | 0.9764 | -0.16606 | 2.4687
177 | 0.001649 | 0.00041302 | -0.0016489 | -0.00041326 | 8.316e-08 | -2.3194e-07 | 0.002513 | 0.002513 | 0.002513 | 0.9764 | -0.16606 | 0.97634 | -0.16643 | 0.93076
178 | 0.092703 | 0.023356 | -0.092662 | -0.02334 | 4.0895e-05 | 1.5557e-05 | 0.13961 | 0.13961 | 0.13961 | 0.98839 | -0.080635 | 0.98794 | -0.083789 | 25.8532
179 | 0.091675 | 0.023093 | -0.091635 | -0.023077 | 4.0369e-05 | 1.5353e-05 | 0.13812 | 0.13812 | 0.13812 | 0.98794 | -0.083789 | 0.98749 | -0.08694 | 25.5779
180 | -0.16766 | -0.042363 | 0.1677 | 0.04238 | 4.2678e-05 | 1.6358e-05 | 0.2503 | 0.2503 | 0.2503 | 0.99721 | -0.019254 | 0.99747 | -0.017446 | 46.351
181 | 0.090658 | 0.022833 | -0.090657 | -0.022832 | 1.0154e-06 | 3.8609e-07 | 0.13665 | 0.13665 | 0.13665 | 0.98749 | -0.08694 | 0.98748 | -0.08702 | 25.3055
182 | 0.088857 | 0.022381 | -0.08882 | -0.022367 | 3.6937e-05 | 1.4038e-05 | 0.13394 | 0.13394 | 0.13394 | 0.98748 | -0.08702 | 0.98706 | -0.089994 | 24.8031
183 | 0.087831 | 0.022119 | -0.087794 | -0.022105 | 3.7e-05 | 1.4058e-05 | 0.13244 | 0.13244 | 0.13244 | 0.98706 | -0.089994 | 0.98663 | -0.093009 | 24.5268
184 | -0.038066 | -0.0095531 | 0.038108 | 0.0095689 | 4.1736e-05 | 1.5805e-05 | 0.058072 | 0.058071 | 0.058072 | 0.97547 | -0.17216 | 0.97658 | -0.16427 | 21.508
185 | 0.035573 | 0.0089283 | -0.035558 | -0.0089228 | 1.454e-05 | 5.4936e-06 | 0.054268 | 0.054268 | 0.054268 | 0.97547 | -0.17216 | 0.97506 | -0.1751 | 20.0994
186 | -0.04151 | -0.010422 | 0.041556 | 0.010439 | 4.6331e-05 | 1.7587e-05 | 0.063256 | 0.063256 | 0.063256 | 0.97658 | -0.16427 | 0.9777 | -0.15624 | 23.428
187 | 0.032741 | 0.0082167 | -0.03272 | -0.0082088 | 2.0968e-05 | 7.8969e-06 | 0.049969 | 0.049969 | 0.049969 | 0.97506 | -0.1751 | 0.97442 | -0.17972 | 18.5071
188 | -0.045275 | -0.011371 | 0.045313 | 0.011385 | 3.7901e-05 | 1.3935e-05 | 0.068914 | 0.068914 | 0.068914 | 0.9777 | -0.15624 | 0.97855 | -0.15022 | 12.7619
189 | 0.030366 | 0.0076188 | -0.030352 | -0.0076137 | 1.373e-05 | 5.1532e-06 | 0.046374 | 0.046374 | 0.046374 | 0.97442 | -0.17972 | 0.97396 | -0.18298 | 17.1757
190 | -0.048077 | -0.012078 | 0.048111 | 0.01209 | 3.338e-05 | 1.2335e-05 | 0.073119 | 0.073118 | 0.073119 | 0.97855 | -0.15022 | 0.97925 | -0.14524 | 13.5405
191 | 0.025774 | 0.0064662 | -0.025762 | -0.0064617 | 1.2294e-05 | 4.5705e-06 | 0.03938 | 0.03938 | 0.03938 | 0.97396 | -0.18298 | 0.97349 | -0.18642 | 14.5851
192 | 0.015745 | 0.0039472 | -0.015733 | -0.003943 | 1.214e-05 | 4.2421e-06 | 0.023926 | 0.023926 | 0.023926 | 0.97925 | -0.14524 | 0.97847 | -0.15081 | 8.8614
193 | -0.063856 | -0.016038 | 0.063949 | 0.016073 | 9.3696e-05 | 3.5233e-05 | 0.097044 | 0.097044 | 0.097044 | 0.97925 | -0.14524 | 0.98073 | -0.1347 | 17.9711
194 | 0.023864 | 0.0059859 | -0.023846 | -0.0059796 | 1.7236e-05 | 6.3714e-06 | 0.036478 | 0.036478 | 0.036478 | 0.97349 | -0.18642 | 0.97276 | -0.19163 | 13.5105
195 | 0.012055 | 0.0030213 | -0.012049 | -0.0030194 | 5.6966e-06 | 1.85e-06 | 0.018333 | 0.018333 | 0.018333 | 0.97847 | -0.15081 | 0.97799 | -0.15422 | 6.79
196 | -0.063949 | -0.016073 | 0.063991 | 0.016088 | 4.1239e-05 | 1.5507e-05 | 0.097044 | 0.097044 | 0.097044 | 0.98073 | -0.1347 | 0.98138 | -0.13007 | 17.971
197 | 0.02207 | 0.0055344 | -0.022062 | -0.0055315 | 7.8399e-06 | 2.8786e-06 | 0.033761 | 0.033761 | 0.033761 | 0.97276 | -0.19163 | 0.9724 | -0.19419 | 12.5041
198 | 0.0085289 | 0.0021371 | -0.0085266 | -0.0021365 | 2.3134e-06 | 6.1358e-07 | 0.012977 | 0.012977 | 0.012977 | 0.97799 | -0.15422 | 0.97772 | -0.15618 | 4.8062
199 | -0.067147 | -0.016879 | 0.067218 | 0.016906 | 7.0998e-05 | 2.6752e-05 | 0.10183 | 0.10183 | 0.10183 | 0.98138 | -0.13007 | 0.98245 | -0.12248 | 18.8573
200 | 0.0045721 | 0.0011454 | -0.0045714 | -0.0011454 | 6.5778e-07 | -2.0012e-08 | 0.0069582 | 0.0069583 | 0.0069583 | 0.97772 | -0.15618 | 0.97757 | -0.15722 | 2.5771
201 | -0.068507 | -0.017229 | 0.068507 | 0.017229 | 8.3777e-07 | 3.159e-07 | 0.10378 | 0.10378 | 0.10378 | 0.98245 | -0.12248 | 0.98246 | -0.1224 | 19.2187
202 | 0.014222 | 0.0035649 | -0.014217 | -0.0035632 | 4.702e-06 | 1.6119e-06 | 0.021782 | 0.021782 | 0.021782 | 0.97157 | -0.20023 | 0.97123 | -0.20262 | 8.0675
203 | -0.016406 | -0.0041122 | 0.016408 | 0.0041129 | 2.074e-06 | 7.325e-07 | 0.025127 | 0.025127 | 0.025127 | 0.97157 | -0.20023 | 0.97169 | -0.19932 | 9.3063
204 | 0.012582 | 0.0031535 | -0.012581 | -0.0031529 | 1.6347e-06 | 5.415e-07 | 0.019277 | 0.019277 | 0.019277 | 0.97123 | -0.20262 | 0.9711 | -0.20356 | 7.1398
205 | -0.018695 | -0.0046862 | 0.018703 | 0.0046888 | 7.3825e-06 | 2.6606e-06 | 0.02863 | 0.02863 | 0.02863 | 0.97169 | -0.19932 | 0.97209 | -0.19647 | 10.6036
206 | 0.010859 | 0.0027214 | -0.010857 | -0.0027209 | 1.5929e-06 | 4.986e-07 | 0.016639 | 0.016639 | 0.016639 | 0.9711 | -0.20356 | 0.97096 | -0.20462 | 6.1626
207 | -0.020445 | -0.0051255 | 0.020451 | 0.0051278 | 6.4386e-06 | 2.3457e-06 | 0.031296 | 0.031296 | 0.031296 | 0.97209 | -0.19647 | 0.9724 | -0.19419 | 11.5913
208 | 0.0071141 | 0.0017828 | -0.0071126 | -0.0017824 | 1.4601e-06 | 3.1816e-07 | 0.010902 | 0.010903 | 0.010903 | 0.97096 | -0.20462 | 0.97075 | -0.2061 | 4.038
209 | 0.0051149 | 0.0012818 | -0.0051142 | -0.0012817 | 7.0757e-07 | 4.4121e-08 | 0.0078403 | 0.0078404 | 0.0078404 | 0.97075 | -0.2061 | 0.97061 | -0.2071 | 2.9039
210 | 0.0028269 | 0.00070846 | -0.0028269 | -0.00070848 | 2.7182e-08 | -1.8211e-08 | 0.0043338 | 0.0043338 | 0.0043338 | 0.97061 | -0.2071 | 0.9706 | -0.20717 | 1.6051
211 | -0.0022858 | -0.00057289 | 0.002286 | 0.00057267 | 1.6637e-07 | -2.1207e-07 | 0.0034797 | 0.0034796 | 0.0034797 | 0.9775 | -0.15775 | 0.97757 | -0.15722 | 1.2888
212 | 0.029149 | 0.0073124 | -0.029124 | -0.0073032 | 2.4635e-05 | 9.2064e-06 | 0.043635 | 0.043635 | 0.043635 | 0.99407 | -0.041486 | 0.99321 | -0.047584 | 16.1611
213 | -0.030679 | -0.007696 | 0.030697 | 0.0077027 | 1.7895e-05 | 6.7064e-06 | 0.045926 | 0.045926 | 0.045926 | 0.99407 | -0.041486 | 0.99467 | -0.037283 | 17.0096
214 | 0.027899 | 0.0069963 | -0.027889 | -0.0069923 | 1.0644e-05 | 3.9677e-06 | 0.0418 | 0.0418 | 0.0418 | 0.99321 | -0.047584 | 0.99281 | -0.050338 | 15.4815
215 | -0.030697 | -0.0077027 | 0.030726 | 0.0077134 | 2.8435e-05 | 1.0656e-05 | 0.045926 | 0.045926 | 0.045926 | 0.99467 | -0.037283 | 0.99562 | -0.030614 | 17.0096
216 | 0.026866 | 0.0067359 | -0.026859 | -0.0067335 | 6.6647e-06 | 2.4782e-06 | 0.040267 | 0.040267 | 0.040267 | 0.99281 | -0.050338 | 0.99256 | -0.052129 | 14.9136
217 | -0.03891 | -0.0097632 | 0.038956 | 0.0097807 | 4.6277e-05 | 1.7513e-05 | 0.058157 | 0.058157 | 0.058157 | 0.99562 | -0.030614 | 0.99684 | -0.022053 | 21.5398
218 | 0.0081845 | 0.0020498 | -0.0081824 | -0.0020493 | 2.1504e-06 | 5.2763e-07 | 0.012232 | 0.012232 | 0.012232 | 0.99562 | -0.030614 | 0.99535 | -0.032515 | 4.5303
219 | 0.025823 | 0.0064739 | -0.02582 | -0.0064725 | 3.7551e-06 | 1.3924e-06 | 0.038714 | 0.038714 | 0.038714 | 0.99256 | -0.052129 | 0.99241 | -0.053179 | 14.3386
220 | -0.040044 | -0.010053 | 0.040065 | 0.010061 | 2.0702e-05 | 7.8413e-06 | 0.059781 | 0.059781 | 0.059781 | 0.99684 | -0.022053 | 0.99737 | -0.018334 | 22.1412
221 | -0.0047954 | -0.0012003 | 0.0047962 | 0.0012003 | 8.2653e-07 | -9.5675e-09 | 0.0072098 | 0.0072097 | 0.0072098 | 0.98963 | -0.072865 | 0.9898 | -0.071617 | 2.6703
222 | 0.0047954 | 0.0012003 | -0.0047947 | -0.0012003 | 6.2158e-07 | -7.1114e-09 | 0.0072098 | 0.0072099 | 0.0072099 | 0.98963 | -0.072865 | 0.9895 | -0.073804 | 2.6703
223 | 0.0042498 | 0.0010641 | -0.0042494 | -0.0010641 | 4.2032e-07 | -5.0444e-08 | 0.0063885 | 0.0063886 | 0.0063886 | 0.9898 | -0.071617 | 0.9897 | -0.072333 | 2.3661
224 | -0.009046 | -0.0022644 | 0.0090477 | 0.0022648 | 1.7751e-06 | 4.8496e-07 | 0.013598 | 0.013598 | 0.013598 | 0.9898 | -0.071617 | 0.99 | -0.070196 | 5.0364
225 | 0.0033568 | 0.00083992 | -0.0033568 | -0.00083992 | 3.0715e-09 | -1.3005e-09 | 0.0050475 | 0.0050475 | 0.0050475 | 0.9895 | -0.073804 | 0.98949 | -0.073811 | 1.8694
226 | 0.021542 | 0.0054004 | -0.021532 | -0.0053967 | 1.0251e-05 | 3.7394e-06 | 0.0323 | 0.0323 | 0.0323 | 0.99241 | -0.053179 | 0.99192 | -0.056616 | 11.9631
227 | -0.044297 | -0.011121 | 0.04432 | 0.01113 | 2.2636e-05 | 8.5978e-06 | 0.066096 | 0.066096 | 0.066096 | 0.99737 | -0.018334 | 0.9979 | -0.014657 | 24.4799
228 | 0.0042325 | 0.0010602 | -0.0042322 | -0.0010602 | 2.8058e-07 | -3.9246e-08 | 0.0063145 | 0.0063145 | 0.0063145 | 0.99737 | -0.018334 | 0.99731 | -0.018813 | 2.3387
229 | 0.0017015 | 0.00042555 | -0.0017015 | -0.00042562 | 2.4947e-08 | -6.8926e-08 | 0.0025579 | 0.0025579 | 0.0025579 | 0.9897 | -0.072333 | 0.98969 | -0.072439 | 0.94737
230 | -0.010694 | -0.0026775 | 0.010697 | 0.0026782 | 2.3036e-06 | 7.0221e-07 | 0.016073 | 0.016073 | 0.016073 | 0.99 | -0.070196 | 0.99022 | -0.068637 | 5.953
231 | 0.0021178 | 0.00052941 | -0.0021177 | -0.00052962 | 1.3079e-07 | -2.1519e-07 | 0.0031843 | 0.0031844 | 0.0031844 | 0.98949 | -0.073811 | 0.98943 | -0.074259 | 1.1794
232 | 0.019861 | 0.004978 | -0.019848 | -0.0049733 | 1.2964e-05 | 4.6842e-06 | 0.029794 | 0.029794 | 0.029794 | 0.99192 | -0.056616 | 0.99126 | -0.061333 | 11.035
233 | -0.045403 | -0.011402 | 0.045426 | 0.01141 | 2.2574e-05 | 8.5793e-06 | 0.067711 | 0.067711 | 0.067711 | 0.9979 | -0.014657 | 0.99841 | -0.011081 | 25.0781
234 | 0.0018602 | 0.00046575 | -0.0018601 | -0.00046593 | 7.8821e-08 | -1.8366e-07 | 0.0027753 | 0.0027754 | 0.0027754 | 0.99731 | -0.018813 | 0.99726 | -0.019119 | 1.0279
235 | 0.00020701 | 5.1071e-05 | -0.000207 | -5.1323e-05 | 1.1826e-09 | -2.5133e-07 | 0.00031095 | 0.00031104 | 0.00031104 | 0.98969 | -0.072439 | 0.98968 | -0.072481 | 0.1152
236 | -0.012379 | -0.0030998 | 0.012381 | 0.0031006 | 2.3224e-06 | 7.5483e-07 | 0.018601 | 0.018601 | 0.018601 | 0.99022 | -0.068637 | 0.99042 | -0.06728 | 6.8892
237 | 0.0019314 | 0.00048294 | -0.0019314 | -0.00048301 | 3.4266e-08 | -7.0434e-08 | 0.0029043 | 0.0029043 | 0.0029043 | 0.98943 | -0.074259 | 0.98941 | -0.074387 | 1.0757
238 | -0.000207 | -5.1879e-05 | 0.000207 | 5.1323e-05 | 2.6224e-09 | -5.5682e-07 | 0.00031124 | 0.00031104 | 0.00031124 | 0.98967 | -0.072574 | 0.98968 | -0.072481 | 0.11527
239 | -0.00025172 | -6.3086e-05 | 0.00025172 | 6.2703e-05 | 2.6727e-09 | -3.8287e-07 | 0.00037859 | 0.00037845 | 0.00037859 | 0.98936 | -0.074773 | 0.98937 | -0.074696 | 0.14022
240 | -0.00050727 | -0.00012675 | 0.00050728 | 0.0001264 | 1.0111e-08 | -3.5381e-07 | 0.0007628 | 0.00076268 | 0.0007628 | 0.98937 | -0.074696 | 0.98939 | -0.074551 | 0.28252
241 | -0.00069201 | -0.00017269 | 0.00069203 | 0.00017241 | 1.548e-08 | -2.8835e-07 | 0.0010405 | 0.0010404 | 0.0010405 | 0.98939 | -0.074551 | 0.98941 | -0.074387 | 0.38537
242 | 0.018051 | 0.004523 | -0.018045 | -0.0045206 | 6.7798e-06 | 2.417e-06 | 0.027097 | 0.027097 | 0.027097 | 0.99126 | -0.061333 | 0.99087 | -0.064048 | 10.0361
243 | 0.015829 | 0.0039654 | -0.015825 | -0.0039639 | 4.3706e-06 | 1.5214e-06 | 0.02377 | 0.023771 | 0.023771 | 0.99087 | -0.064048 | 0.99059 | -0.066045 | 8.8039
244 | 0.014035 | 0.0035152 | -0.014032 | -0.0035144 | 2.3961e-06 | 8.1036e-07 | 0.021082 | 0.021082 | 0.021082 | 0.99059 | -0.066045 | 0.99042 | -0.06728 | 7.808
245 | -0.046489 | -0.011677 | 0.04651 | 0.011684 | 2.0243e-05 | 7.6974e-06 | 0.069296 | 0.069296 | 0.069296 | 0.99841 | -0.011081 | 0.99886 | -0.0079511 | 25.6651
246 | 0.0011532 | 0.00028876 | -0.0011532 | -0.00028902 | 3.7725e-08 | -2.519e-07 | 0.0017206 | 0.0017207 | 0.0017207 | 0.99726 | -0.019119 | 0.99723 | -0.019356 | 0.63731
247 | -0.047567 | -0.011949 | 0.047588 | 0.011957 | 2.0888e-05 | 7.9466e-06 | 0.070871 | 0.070871 | 0.070871 | 0.99886 | -0.0079511 | 0.99931 | -0.0047953 | 26.2485
248 | -0.049622 | -0.012467 | 0.049631 | 0.012471 | 9.6106e-06 | 3.6594e-06 | 0.0739 | 0.0739 | 0.0739 | 0.99931 | -0.0047953 | 0.99951 | -0.0034034 | 27.3702
249 | -0.16869 | -0.042627 | 0.16883 | 0.042681 | 0.00013937 | 5.342e-05 | 0.25177 | 0.25177 | 0.25177 | 0.99747 | -0.017446 | 0.99832 | -0.011581 | 46.6243
250 | -0.16989 | -0.042946 | 0.17003 | 0.043 | 0.00013961 | 5.3512e-05 | 0.25335 | 0.25335 | 0.25335 | 0.99832 | -0.011581 | 0.99916 | -0.005752 | 46.9167
251 | -0.17107 | -0.043262 | 0.17121 | 0.043315 | 0.00013883 | 5.3216e-05 | 0.25491 | 0.25491 | 0.25491 | 0.99916 | -0.005752 | 1 | 0 | 47.2048
252 | 0.050675 | 0.012735 | -0.050651 | -0.012726 | 2.3996e-05 | 9.1404e-06 | 0.075417 | 0.075417 | 0.075417 | 1 | 0 | 0.99951 | -0.0034034 | 27.9322
253 | 0.086719 | 0.021836 | -0.086683 | -0.021822 | 3.5028e-05 | 1.3305e-05 | 0.13082 | 0.13082 | 0.13082 | 0.98663 | -0.093009 | 0.98622 | -0.095901 | 24.2266
254 | 0.085643 | 0.021562 | -0.085587 | -0.02154 | 5.6116e-05 | 2.1309e-05 | 0.12925 | 0.12925 | 0.12925 | 0.98622 | -0.095901 | 0.98555 | -0.10059 | 23.936
255 | 0.082768 | 0.020834 | -0.082706 | -0.02081 | 6.1667e-05 | 2.3396e-05 | 0.125 | 0.125 | 0.125 | 0.98555 | -0.10059 | 0.98479 | -0.10593 | 23.1477
256 | 0.079797 | 0.020081 | -0.079722 | -0.020053 | 7.5311e-05 | 2.8544e-05 | 0.1206 | 0.1206 | 0.1206 | 0.98479 | -0.10593 | 0.98384 | -0.1127 | 22.3337
257 | 0.075932 | 0.019103 | -0.075906 | -0.019093 | 2.5861e-05 | 9.7872e-06 | 0.11487 | 0.11487 | 0.11487 | 0.98384 | -0.1127 | 0.98349 | -0.11514 | 21.2722
258 | 0.072926 | 0.018346 | -0.072852 | -0.018318 | 7.3401e-05 | 2.7741e-05 | 0.11036 | 0.11036 | 0.11036 | 0.98349 | -0.11514 | 0.98247 | -0.12237 | 20.4373
259 | 0.071564 | 0.017995 | -0.071563 | -0.017995 | 2.9349e-07 | 1.1085e-07 | 0.10841 | 0.10841 | 0.10841 | 0.98247 | -0.12237 | 0.98246 | -0.1224 | 20.0758

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22371 | 0.056306

## res_load
| p_mw | q_mvar
0 | 0.00011366 | 2.8485e-05
1 | 0.00010329 | 2.5886e-05
2 | 9.4031e-05 | 2.3566e-05
3 | 0.00016795 | 4.2093e-05
4 | 0.00010018 | 2.5107e-05
5 | 0.00011053 | 2.7701e-05
6 | 0.00010409 | 2.6088e-05
7 | 0.00011407 | 2.8588e-05
8 | 8.7651e-05 | 2.1967e-05
9 | 8.9536e-05 | 2.244e-05
10 | 0.00015822 | 3.9653e-05
11 | 0.00034619 | 8.6764e-05
12 | 0.00016483 | 4.1309e-05
13 | 8.5614e-05 | 2.1457e-05
14 | 9.459e-05 | 2.3707e-05
15 | 8.2478e-05 | 2.0671e-05
16 | 9.5291e-05 | 2.3882e-05
17 | 9.5709e-05 | 2.3987e-05
18 | 8.3183e-05 | 2.0848e-05
19 | 0.00010495 | 2.6303e-05
20 | 8.8641e-05 | 2.2216e-05
21 | 8.3416e-05 | 2.0906e-05
22 | 9.4107e-05 | 2.3585e-05
23 | 0.00011041 | 2.7671e-05
24 | 0.00012344 | 3.0938e-05
25 | 0.00011051 | 2.7695e-05
26 | 0.00010824 | 2.7126e-05
27 | 9.9529e-05 | 2.4944e-05
28 | 8.6139e-05 | 2.1588e-05
29 | 0.0001774 | 4.4461e-05
30 | 9.7978e-05 | 2.4556e-05
31 | 0.00027034 | 6.7754e-05
32 | 0.00010313 | 2.5847e-05
33 | 8.8929e-05 | 2.2288e-05
34 | 0.0001122 | 2.812e-05
35 | 0.00012663 | 3.1736e-05
36 | 0.00019803 | 4.9631e-05
37 | 0.00023897 | 5.9891e-05
38 | 0.00015914 | 3.9883e-05
39 | 8.64e-05 | 2.1654e-05
40 | 0.00011696 | 2.9314e-05
41 | 0.0001345 | 3.3708e-05
42 | 0.00010773 | 2.7e-05
43 | 0.00011023 | 2.7627e-05
44 | 9.8768e-05 | 2.4754e-05
45 | 0.00010256 | 2.5705e-05
46 | 9.9778e-05 | 2.5007e-05
47 | 0.00011577 | 2.9014e-05
48 | 8.9472e-05 | 2.2424e-05
49 | 9.7725e-05 | 2.4492e-05
50 | 0.00024946 | 6.252e-05
51 | 9.4779e-05 | 2.3754e-05
52 | 0.00017802 | 4.4616e-05
53 | 0.00010318 | 2.5858e-05
54 | 0.00010614 | 2.66e-05
55 | 0.0001362 | 3.4134e-05
56 | 0.00010593 | 2.6549e-05
57 | 0.00010647 | 2.6684e-05
58 | 8.7326e-05 | 2.1886e-05
59 | 8.2668e-05 | 2.0719e-05
60 | 0.00067913 | 0.00017021
61 | 0.00041757 | 0.00010465
62 | 0.00044897 | 0.00011252
63 | 0.00011304 | 2.833e-05
64 | 0.0003673 | 9.2055e-05
65 | 0.00040174 | 0.00010069
66 | 0.00036188 | 9.0695e-05
67 | 0.00062632 | 0.00015697
68 | 0.00040652 | 0.00010188
69 | 0.00048257 | 0.00012094
70 | 0.00068895 | 0.00017267
71 | 0.0010681 | 0.0002677
72 | 8.2218e-05 | 2.0606e-05
73 | 0.00044752 | 0.00011216
74 | 0.00013017 | 3.2623e-05
75 | 0.00018419 | 4.6163e-05
76 | 0.00015017 | 3.7636e-05
77 | 0.00059217 | 0.00014841
78 | 0.00016038 | 4.0196e-05
79 | 0.00013428 | 3.3654e-05
80 | 0.00011738 | 2.9417e-05
81 | 0.00011249 | 2.8194e-05
82 | 0.00041593 | 0.00010424
83 | 0.00013407 | 3.3601e-05
84 | 0.00014053 | 3.5219e-05
85 | 0.00018656 | 4.6758e-05
86 | 0.00014727 | 3.691e-05
87 | 0.00014519 | 3.6388e-05
88 | 0.0001725 | 4.3233e-05
89 | 0.00014054 | 3.5223e-05
90 | 0.00014958 | 3.7488e-05
91 | 0.00014735 | 3.6929e-05
92 | 0.00037334 | 9.3567e-05
93 | 0.00038018 | 9.5283e-05
94 | 0.00019497 | 4.8863e-05
95 | 0.00014071 | 3.5265e-05
96 | 0.00014641 | 3.6694e-05
97 | 0.00052541 | 0.00013168
98 | 0.00025766 | 6.4575e-05
99 | 0.00050092 | 0.00012554
100 | 0.00039546 | 9.9113e-05
101 | 0.00039987 | 0.00010022
102 | 0.00039523 | 9.9054e-05
103 | 0.0001402 | 3.5136e-05
104 | 0.00047444 | 0.0001189
105 | 0.00044444 | 0.00011139
106 | 0.00017289 | 4.333e-05
107 | 0.00018402 | 4.612e-05
108 | 0.00033994 | 8.5196e-05
109 | 0.00014718 | 3.6888e-05
110 | 0.00012934 | 3.2415e-05
111 | 0.00037474 | 9.3919e-05
112 | 0.00016064 | 4.0261e-05
113 | 0.00041144 | 0.00010312
114 | 0.00069702 | 0.00017469
115 | 0.0010135 | 0.000254
116 | 0.00061175 | 0.00015332
117 | 0.00078139 | 0.00019583
118 | 0.0006495 | 0.00016278
119 | 0.0006167 | 0.00015456
120 | 0.00071156 | 0.00017833
121 | 0.00074052 | 0.00018559
122 | 0.0017118 | 0.00042901
123 | 0.0014097 | 0.00035331
124 | 0.0013351 | 0.0003346
125 | 0.0012764 | 0.00031991
126 | 0.0011187 | 0.00028037
127 | 0.00010755 | 2.6955e-05
128 | 0.00024825 | 6.2218e-05
129 | 0.00143 | 0.00035839
130 | 0.0033124 | 0.00083017
131 | 0.0032984 | 0.00082666
132 | 0.00095794 | 0.00024008
133 | 0.00095901 | 0.00024035
134 | 0.0027173 | 0.00068103
135 | 0.0016313 | 0.00040884
136 | 0.00048176 | 0.00012074
137 | 0.00016988 | 4.2575e-05
138 | 0.0016312 | 0.00040882
139 | 0.00048294 | 0.00012104
140 | 0.0030757 | 0.00077085
141 | 0.00011643 | 2.9179e-05
142 | 0.0016305 | 0.00040864
143 | 0.0023919 | 0.00059948
144 | 0.0024136 | 0.00060491
145 | 0.0017171 | 0.00043033
146 | 0.0019442 | 0.00048727
147 | 0.0023524 | 0.00058956
148 | 0.0025317 | 0.00063449
149 | 0.0027247 | 0.00068287
150 | 0.00096584 | 0.00024206
151 | 0.00098711 | 0.00024739
152 | 0.0021045 | 0.00052745
153 | 0.00097605 | 0.00024462
154 | 0.0018005 | 0.00045125
155 | 0.00098952 | 0.000248
156 | 0.0016489 | 0.00041326
157 | 0.0024932 | 0.00062486
158 | 0.0034024 | 0.00085272
159 | 0.0028173 | 0.00070608
160 | 0.0037182 | 0.00093186
161 | 0.002354 | 0.00058997
162 | 0.0027649 | 0.00069294
163 | 0.0045782 | 0.0011474
164 | 0.0018982 | 0.00047573
165 | 0.0036777 | 0.00092172
166 | 0.0017764 | 0.00044521
167 | 0.0035204 | 0.00088229
168 | 0.0031564 | 0.00079108
169 | 0.0039545 | 0.0009911
170 | 0.0012886 | 0.00032295
171 | 0.0021838 | 0.00054732
172 | 0.001635 | 0.00040977
173 | 0.0022873 | 0.00057325
174 | 0.0017218 | 0.00043153
175 | 0.0017422 | 0.00043663
176 | 0.0037432 | 0.00093814
177 | 0.0016107 | 0.00040369
178 | 0.0019977 | 0.00050068
179 | 0.0022873 | 0.00057326
180 | 0.0028269 | 0.00070848
181 | 0.0022858 | 0.00057289
182 | 0.0022854 | 0.00057277
183 | 0.0015306 | 0.0003836
184 | 0.0012247 | 0.00030694
185 | 0.001023 | 0.00025639
186 | 0.0010356 | 0.00025954
187 | 0.0010879 | 0.00027265
188 | 0.001616 | 0.00040502
189 | 0.001438 | 0.00036039
190 | 0.0042778 | 0.0010721
191 | 0.0025479 | 0.00063856
192 | 0.0016467 | 0.00041269
193 | 0.001239 | 0.00031052
194 | 0.0016705 | 0.00041867
195 | 0.0010833 | 0.00027149
196 | 0.002372 | 0.00059449
197 | 0.0014945 | 0.00037455
198 | 0.0016822 | 0.0004216
199 | 0.00018625 | 4.6679e-05
200 | 0.000207 | 5.1879e-05
201 | 0.00025172 | 6.3086e-05
202 | 0.00025555 | 6.4048e-05
203 | 0.00018473 | 4.6297e-05
204 | 0.0012393 | 0.00031061
205 | 0.0017967 | 0.0004503
206 | 0.0022154 | 0.00055523
207 | 0.0017901 | 0.00044864
208 | 0.0016511 | 0.00041381
209 | 0.0010634 | 0.0002665
210 | 0.0007069 | 0.00017717
211 | 0.0011532 | 0.00028902
212 | 0.0010573 | 0.00026499
213 | 0.0020341 | 0.00050979
214 | 0.00098939 | 0.00024796
215 | 0.0010594 | 0.0002655
216 | 0.0010447 | 0.00026182
217 | 0.0010212 | 0.00025594
218 | 0.0010192 | 0.00025545
219 | 0.001075 | 0.00026942
220 | 0.00104 | 0.00026065
221 | 0.0028197 | 0.00070669
222 | 0.0029089 | 0.00072905
223 | 0.0037901 | 0.00094989
224 | 0.0029801 | 0.00074688
225 | 0.0012886 | 0.00032295
226 | 0.003056 | 0.00076591

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1