## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2025-3_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2025-3_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2025-3_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2025-3_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2025-3_0_5_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_2025-3_0_5_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_2025-3_0_5_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2025-3_0_5_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_2025-3_0_5_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2025-3_0_5_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2025-3_0_5_node_111 | 0.4 | n |  | TRUE
11 | bus_LV_2025-3_0_5_node_110 | 0.4 | n |  | TRUE
12 | bus_LV_2025-3_0_5_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_2025-3_0_5_node_38 | 0.4 | n |  | TRUE
14 | bus_LV_2025-3_0_5_node_68 | 0.4 | n |  | TRUE
15 | bus_LV_2025-3_0_5_node_67 | 0.4 | n |  | TRUE
16 | bus_LV_2025-3_0_5_node_37 | 0.4 | n |  | TRUE
17 | bus_LV_2025-3_0_5_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_2025-3_0_5_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_2025-3_0_5_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_2025-3_0_5_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_2025-3_0_5_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_2025-3_0_5_node_73 | 0.4 | n |  | TRUE
23 | bus_LV_2025-3_0_5_node_71 | 0.4 | n |  | TRUE
24 | bus_LV_2025-3_0_5_node_74 | 0.4 | n |  | TRUE
25 | bus_LV_2025-3_0_5_node_72 | 0.4 | n |  | TRUE
26 | bus_LV_2025-3_0_5_node_69 | 0.4 | n |  | TRUE
27 | bus_LV_2025-3_0_5_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_2025-3_0_5_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_2025-3_0_5_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_2025-3_0_5_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_2025-3_0_5_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_2025-3_0_5_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_2025-3_0_5_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_2025-3_0_5_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_2025-3_0_5_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_2025-3_0_5_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_2025-3_0_5_node_78 | 0.4 | n |  | TRUE
38 | bus_LV_2025-3_0_5_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_2025-3_0_5_node_79 | 0.4 | n |  | TRUE
40 | bus_LV_2025-3_0_5_node_77 | 0.4 | n |  | TRUE
41 | bus_LV_2025-3_0_5_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_2025-3_0_5_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_2025-3_0_5_node_92 | 0.4 | n |  | TRUE
44 | bus_LV_2025-3_0_5_node_89 | 0.4 | n |  | TRUE
45 | bus_LV_2025-3_0_5_node_88 | 0.4 | n |  | TRUE
46 | bus_LV_2025-3_0_5_node_90 | 0.4 | n |  | TRUE
47 | bus_LV_2025-3_0_5_node_109 | 0.4 | n |  | TRUE
48 | bus_LV_2025-3_0_5_node_91 | 0.4 | n |  | TRUE
49 | bus_LV_2025-3_0_5_node_99 | 0.4 | n |  | TRUE
50 | bus_LV_2025-3_0_5_node_98 | 0.4 | n |  | TRUE
51 | bus_LV_2025-3_0_5_node_96 | 0.4 | n |  | TRUE
52 | bus_LV_2025-3_0_5_node_94 | 0.4 | n |  | TRUE
53 | bus_LV_2025-3_0_5_node_95 | 0.4 | n |  | TRUE
54 | bus_LV_2025-3_0_5_node_97 | 0.4 | n |  | TRUE
55 | bus_LV_2025-3_0_5_node_117 | 0.4 | n |  | TRUE
56 | bus_LV_2025-3_0_5_node_101 | 0.4 | n |  | TRUE
57 | bus_LV_2025-3_0_5_node_100 | 0.4 | n |  | TRUE
58 | bus_LV_2025-3_0_5_node_102 | 0.4 | n |  | TRUE
59 | bus_LV_2025-3_0_5_node_103 | 0.4 | n |  | TRUE
60 | bus_LV_2025-3_0_5_node_105 | 0.4 | n |  | TRUE
61 | bus_LV_2025-3_0_5_node_107 | 0.4 | n |  | TRUE
62 | bus_LV_2025-3_0_5_node_108 | 0.4 | n |  | TRUE
63 | bus_LV_2025-3_0_5_node_33 | 0.4 | n |  | TRUE
64 | bus_LV_2025-3_0_5_node_63 | 0.4 | n |  | TRUE
65 | bus_LV_2025-3_0_5_node_35 | 0.4 | n |  | TRUE
66 | bus_LV_2025-3_0_5_node_62 | 0.4 | n |  | TRUE
67 | bus_LV_2025-3_0_5_node_28 | 0.4 | n |  | TRUE
68 | bus_LV_2025-3_0_5_node_36 | 0.4 | n |  | TRUE
69 | bus_LV_2025-3_0_5_node_30 | 0.4 | n |  | TRUE
70 | bus_LV_2025-3_0_5_node_29 | 0.4 | n |  | TRUE
71 | bus_LV_2025-3_0_5_node_31 | 0.4 | n |  | TRUE
72 | bus_LV_2025-3_0_5_node_32 | 0.4 | n |  | TRUE
73 | bus_LV_2025-3_0_5_node_115 | 0.4 | n |  | TRUE
74 | bus_LV_2025-3_0_5_node_34 | 0.4 | n |  | TRUE
75 | bus_LV_2025-3_0_5_node_40 | 0.4 | n |  | TRUE
76 | bus_LV_2025-3_0_5_node_47 | 0.4 | n |  | TRUE
77 | bus_LV_2025-3_0_5_node_41 | 0.4 | n |  | TRUE
78 | bus_LV_2025-3_0_5_node_48 | 0.4 | n |  | TRUE
79 | bus_LV_2025-3_0_5_node_42 | 0.4 | n |  | TRUE
80 | bus_LV_2025-3_0_5_node_43 | 0.4 | n |  | TRUE
81 | bus_LV_2025-3_0_5_node_53 | 0.4 | n |  | TRUE
82 | bus_LV_2025-3_0_5_node_46 | 0.4 | n |  | TRUE
83 | bus_LV_2025-3_0_5_node_64 | 0.4 | n |  | TRUE
84 | bus_LV_2025-3_0_5_node_50 | 0.4 | n |  | TRUE
85 | bus_LV_2025-3_0_5_node_45 | 0.4 | n |  | TRUE
86 | bus_LV_2025-3_0_5_node_44 | 0.4 | n |  | TRUE
87 | bus_LV_2025-3_0_5_node_49 | 0.4 | n |  | TRUE
88 | bus_LV_2025-3_0_5_node_51 | 0.4 | n |  | TRUE
89 | bus_LV_2025-3_0_5_node_52 | 0.4 | n |  | TRUE
90 | bus_LV_2025-3_0_5_node_54 | 0.4 | n |  | TRUE
91 | bus_LV_2025-3_0_5_node_57 | 0.4 | n |  | TRUE
92 | bus_LV_2025-3_0_5_node_55 | 0.4 | n |  | TRUE
93 | bus_LV_2025-3_0_5_node_58 | 0.4 | n |  | TRUE
94 | bus_LV_2025-3_0_5_node_65 | 0.4 | n |  | TRUE
95 | bus_LV_2025-3_0_5_node_56 | 0.4 | n |  | TRUE
96 | bus_LV_2025-3_0_5_node_61 | 0.4 | n |  | TRUE
97 | bus_LV_2025-3_0_5_node_59 | 0.4 | n |  | TRUE
98 | bus_LV_2025-3_0_5_node_60 | 0.4 | n |  | TRUE
99 | bus_LV_2025-3_0_5_node_66 | 0.4 | n |  | TRUE
100 | bus_LV_2025-3_0_5_node_70 | 0.4 | n |  | TRUE
101 | bus_LV_2025-3_0_5_node_75 | 0.4 | n |  | TRUE
102 | bus_LV_2025-3_0_5_node_76 | 0.4 | n |  | TRUE
103 | bus_LV_2025-3_0_5_node_80 | 0.4 | n |  | TRUE
104 | bus_LV_2025-3_0_5_node_81 | 0.4 | n |  | TRUE
105 | bus_LV_2025-3_0_5_node_83 | 0.4 | n |  | TRUE
106 | bus_LV_2025-3_0_5_node_82 | 0.4 | n |  | TRUE
107 | bus_LV_2025-3_0_5_node_114 | 0.4 | n |  | TRUE
108 | bus_LV_2025-3_0_5_node_116 | 0.4 | n |  | TRUE
109 | bus_LV_2025-3_0_5_node_122 | 0.4 | n |  | TRUE
110 | bus_LV_2025-3_0_5_node_112 | 0.4 | n |  | TRUE
111 | bus_LV_2025-3_0_5_node_84 | 0.4 | n |  | TRUE
112 | bus_LV_2025-3_0_5_node_85 | 0.4 | n |  | TRUE
113 | bus_LV_2025-3_0_5_node_86 | 0.4 | n |  | TRUE
114 | bus_LV_2025-3_0_5_node_87 | 0.4 | n |  | TRUE
115 | bus_LV_2025-3_0_5_node_120 | 0.4 | n |  | TRUE
116 | bus_LV_2025-3_0_5_node_121 | 0.4 | n |  | TRUE
117 | bus_LV_2025-3_0_5_node_118 | 0.4 | n |  | TRUE
118 | bus_LV_2025-3_0_5_node_113 | 0.4 | n |  | TRUE
119 | bus_LV_2025-3_0_5_node_119 | 0.4 | n |  | TRUE
120 | bus_MV_454_1_node_273 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2025-3_0_5_load_0 | 0 | 0.0023312 | 0.00058425 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2025-3_0_5_load_1 | 1 | 0.0013349 | 0.00033456 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2025-3_0_5_load_2 | 2 | 0.0031281 | 0.00078398 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2025-3_0_5_load_3 | 3 | 0.001962 | 0.00049172 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2025-3_0_5_load_7 | 6 | 0.0012522 | 0.00031383 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2025-3_0_5_load_111 | 10 | 0.0029658 | 0.00074329 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2025-3_0_5_load_110 | 11 | 0.002311 | 0.0005792 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2025-3_0_5_load_38 | 13 | 0.0037044 | 0.00092842 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2025-3_0_5_load_68 | 14 | 0.0044856 | 0.0011242 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2025-3_0_5_load_67 | 15 | 0.0066132 | 0.0016574 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2025-3_0_5_load_37 | 16 | 0.0017951 | 0.00044988 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2025-3_0_5_load_10 | 17 | 0.0008474 | 0.00021238 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2025-3_0_5_load_11 | 18 | 0.0014763 | 0.00036998 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2025-3_0_5_load_12 | 19 | 0.002468 | 0.00061853 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2025-3_0_5_load_13 | 20 | 0.0013708 | 0.00034357 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2025-3_0_5_load_14 | 21 | 0.0010475 | 0.00026253 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2025-3_0_5_load_71 | 23 | 0.002714 | 0.00068018 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2025-3_0_5_load_74 | 24 | 0.0025502 | 0.00063914 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2025-3_0_5_load_72 | 25 | 0.0016798 | 0.000421 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2025-3_0_5_load_15 | 27 | 0.0023744 | 0.00059508 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2025-3_0_5_load_16 | 28 | 0.0019058 | 0.00047763 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2025-3_0_5_load_26 | 31 | 0.0055183 | 0.001383 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2025-3_0_5_load_21 | 32 | 0.0022406 | 0.00056155 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2025-3_0_5_load_22 | 33 | 0.012677 | 0.0031771 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2025-3_0_5_load_19 | 34 | 0.0062498 | 0.0015663 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2025-3_0_5_load_27 | 35 | 0.0035957 | 0.00090117 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2025-3_0_5_load_18 | 36 | 0.00099054 | 0.00024825 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2025-3_0_5_load_78 | 37 | 0.0015921 | 0.00039903 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2025-3_0_5_load_77 | 40 | 0.0017142 | 0.00042962 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2025-3_0_5_load_24 | 41 | 0.0021192 | 0.00053111 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2025-3_0_5_load_89 | 44 | 0.00078554 | 0.00019687 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2025-3_0_5_load_109 | 47 | 0.00066891 | 0.00016764 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2025-3_0_5_load_99 | 49 | 0.00038129 | 9.5559e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2025-3_0_5_load_98 | 50 | 0.0016404 | 0.00041112 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2025-3_0_5_load_96 | 51 | 0.00038194 | 9.5724e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2025-3_0_5_load_94 | 52 | 0.00090822 | 0.00022762 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2025-3_0_5_load_117 | 55 | 0.00038155 | 9.5626e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2025-3_0_5_load_101 | 56 | 0.0030592 | 0.00076671 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2025-3_0_5_load_100 | 57 | 0.0081502 | 0.0020426 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2025-3_0_5_load_102 | 58 | 0.001329 | 0.00033307 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2025-3_0_5_load_103 | 59 | 0.0036296 | 0.00090967 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2025-3_0_5_load_107 | 61 | 0.0053641 | 0.0013444 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2025-3_0_5_load_108 | 62 | 0.00053237 | 0.00013342 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2025-3_0_5_load_63 | 64 | 0.0127 | 0.0031828 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2025-3_0_5_load_35 | 65 | 0.0016603 | 0.0004161 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2025-3_0_5_load_36 | 68 | 0.0015538 | 0.00038942 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2025-3_0_5_load_30 | 69 | 0.0018344 | 0.00045976 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2025-3_0_5_load_29 | 70 | 0.0013412 | 0.00033613 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2025-3_0_5_load_31 | 71 | 0.0018346 | 0.0004598 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2025-3_0_5_load_32 | 72 | 0.0021615 | 0.00054173 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2025-3_0_5_load_115 | 73 | 0.0015841 | 0.00039702 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2025-3_0_5_load_34 | 74 | 0.0036382 | 0.00091182 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2025-3_0_5_load_40 | 75 | 0.0096316 | 0.0024139 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2025-3_0_5_load_47 | 76 | 0.0012028 | 0.00030146 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2025-3_0_5_load_48 | 78 | 0.0025628 | 0.00064231 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2025-3_0_5_load_42 | 79 | 0.0015383 | 0.00038554 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2025-3_0_5_load_43 | 80 | 0.0017675 | 0.00044298 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2025-3_0_5_load_64 | 83 | 0.0014635 | 0.00036679 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2025-3_0_5_load_44 | 86 | 0.0019509 | 0.00048894 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2025-3_0_5_load_49 | 87 | 0.0011627 | 0.00029139 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2025-3_0_5_load_52 | 89 | 0.0020477 | 0.00051319 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2025-3_0_5_load_54 | 90 | 0.0015816 | 0.00039639 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2025-3_0_5_load_57 | 91 | 0.0025723 | 0.00064467 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2025-3_0_5_load_55 | 92 | 0.002253 | 0.00056465 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2025-3_0_5_load_58 | 93 | 0.00099851 | 0.00025025 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2025-3_0_5_load_65 | 94 | 0.0015633 | 0.0003918 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2025-3_0_5_load_56 | 95 | 0.0020592 | 0.00051609 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2025-3_0_5_load_59 | 97 | 0.0027193 | 0.00068153 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2025-3_0_5_load_60 | 98 | 0.0029528 | 0.00074005 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2025-3_0_5_load_66 | 99 | 0.0046502 | 0.0011655 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2025-3_0_5_load_70 | 100 | 0.005549 | 0.0013907 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2025-3_0_5_load_75 | 101 | 0.0017904 | 0.00044873 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2025-3_0_5_load_76 | 102 | 0.0022193 | 0.00055621 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2025-3_0_5_load_80 | 103 | 0.0013869 | 0.00034759 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2025-3_0_5_load_82 | 106 | 0.0020438 | 0.00051222 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2025-3_0_5_load_116 | 108 | 0.0031168 | 0.00078114 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2025-3_0_5_load_122 | 109 | 0.0016066 | 0.00040266 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2025-3_0_5_load_84 | 111 | 0.0018557 | 0.00046508 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2025-3_0_5_load_86 | 113 | 0.0022506 | 0.00056404 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2025-3_0_5_load_120 | 115 | 0.0025084 | 0.00062868 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2025-3_0_5_load_121 | 116 | 0.0024279 | 0.00060849 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2025-3_0_5_load_113 | 118 | 0.0022839 | 0.00057241 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2025-3_0_5_load_119 | 119 | 0.0079214 | 0.0019853 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2025-3_0_5_line_0 | NAYY 4x150 SE | 0 | 1 | 0.039054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2025-3_0_5_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0095033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2025-3_0_5_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0033542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2025-3_0_5_line_3 | NAYY 4x150 SE | 3 | 7 | 0.017057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2025-3_0_5_line_4 | NAYY 4x150 SE | 4 | 5 | 0.017424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2025-3_0_5_line_5 | NAYY 4x150 SE | 4 | 6 | 0.15442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2025-3_0_5_line_6 | NAYY 4x150 SE | 5 | 12 | 0.039293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_2025-3_0_5_line_7 | NAYY 4x150 SE | 5 | 13 | 0.024096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_2025-3_0_5_line_8 | NAYY 4x150 SE | 6 | 8 | 0.020949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2025-3_0_5_line_9 | NAYY 4x150 SE | 7 | 8 | 0.021837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2025-3_0_5_line_10 | NAYY 4x150 SE | 7 | 9 | 0.08036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2025-3_0_5_line_11 | NAYY 4x150 SE | 9 | 10 | 0.021893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2025-3_0_5_line_12 | NAYY 4x150 SE | 10 | 11 | 0.045892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2025-3_0_5_line_13 | NAYY 4x150 SE | 12 | 14 | 0.021558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_2025-3_0_5_line_14 | NAYY 4x150 SE | 12 | 15 | 0.019564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2025-3_0_5_line_15 | NAYY 4x150 SE | 13 | 16 | 0.023023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_2025-3_0_5_line_16 | NAYY 4x150 SE | 14 | 26 | 0.029353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_2025-3_0_5_line_17 | NAYY 4x150 SE | 16 | 68 | 0.024747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_2025-3_0_5_line_18 | NAYY 4x150 SE | 17 | 18 | 0.026942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_2025-3_0_5_line_19 | NAYY 4x150 SE | 17 | 19 | 0.029557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_2025-3_0_5_line_20 | NAYY 4x150 SE | 18 | 20 | 0.024915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_2025-3_0_5_line_21 | NAYY 4x150 SE | 19 | 21 | 0.015353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_2025-3_0_5_line_22 | NAYY 4x150 SE | 20 | 22 | 0.00025022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_2025-3_0_5_line_23 | NAYY 4x150 SE | 21 | 23 | 0.015116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
24 | LV_2025-3_0_5_line_24 | NAYY 4x150 SE | 22 | 24 | 0.028944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_2025-3_0_5_line_25 | NAYY 4x150 SE | 22 | 25 | 0.021599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2025-3_0_5_line_26 | NAYY 4x150 SE | 23 | 26 | 0.032129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_2025-3_0_5_line_27 | NAYY 4x150 SE | 24 | 40 | 0.029185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_2025-3_0_5_line_28 | NAYY 4x150 SE | 24 | 101 | 0.0241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2025-3_0_5_line_29 | NAYY 4x150 SE | 26 | 100 | 0.052832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2025-3_0_5_line_30 | NAYY 4x150 SE | 27 | 28 | 0.03569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2025-3_0_5_line_31 | NAYY 4x150 SE | 28 | 29 | 0.021728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2025-3_0_5_line_32 | NAYY 4x150 SE | 29 | 30 | 0.016469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2025-3_0_5_line_33 | NAYY 4x150 SE | 29 | 31 | 0.026359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_2025-3_0_5_line_34 | NAYY 4x150 SE | 30 | 32 | 0.048918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2025-3_0_5_line_35 | NAYY 4x150 SE | 30 | 33 | 0.038047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2025-3_0_5_line_36 | NAYY 4x150 SE | 30 | 34 | 0.022624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2025-3_0_5_line_37 | NAYY 4x150 SE | 31 | 35 | 0.0017387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_2025-3_0_5_line_38 | NAYY 4x150 SE | 32 | 63 | 0.010146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_2025-3_0_5_line_39 | NAYY 4x150 SE | 33 | 64 | 0.037595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_2025-3_0_5_line_40 | NAYY 4x150 SE | 35 | 67 | 0.022426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_2025-3_0_5_line_41 | NAYY 4x150 SE | 36 | 37 | 0.052375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_2025-3_0_5_line_42 | NAYY 4x150 SE | 36 | 38 | 0.097922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_2025-3_0_5_line_43 | NAYY 4x150 SE | 37 | 39 | 0.01545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_2025-3_0_5_line_44 | NAYY 4x150 SE | 37 | 40 | 0.048014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_2025-3_0_5_line_45 | NAYY 4x150 SE | 38 | 41 | 0.055248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_2025-3_0_5_line_46 | NAYY 4x150 SE | 38 | 42 | 0.052514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_2025-3_0_5_line_47 | NAYY 4x150 SE | 39 | 103 | 0.019557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_2025-3_0_5_line_48 | NAYY 4x150 SE | 39 | 104 | 0.004776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_2025-3_0_5_line_49 | NAYY 4x150 SE | 42 | 43 | 0.052775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_2025-3_0_5_line_50 | NAYY 4x150 SE | 42 | 44 | 0.056408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_2025-3_0_5_line_51 | NAYY 4x150 SE | 43 | 51 | 0.051094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_2025-3_0_5_line_52 | NAYY 4x150 SE | 43 | 52 | 0.029394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_2025-3_0_5_line_53 | NAYY 4x150 SE | 44 | 45 | 0.036625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
54 | LV_2025-3_0_5_line_54 | NAYY 4x150 SE | 45 | 46 | 0.045325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_2025-3_0_5_line_55 | NAYY 4x150 SE | 46 | 47 | 0.062169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
56 | LV_2025-3_0_5_line_56 | NAYY 4x150 SE | 47 | 62 | 0.025758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_2025-3_0_5_line_57 | NAYY 4x150 SE | 48 | 49 | 0.028218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_2025-3_0_5_line_58 | NAYY 4x150 SE | 48 | 50 | 0.015978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_2025-3_0_5_line_59 | NAYY 4x150 SE | 49 | 55 | 0.0088671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_2025-3_0_5_line_60 | NAYY 4x150 SE | 51 | 55 | 0.0090989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_2025-3_0_5_line_61 | NAYY 4x150 SE | 52 | 53 | 0.053247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_2025-3_0_5_line_62 | NAYY 4x150 SE | 53 | 54 | 0.014584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_2025-3_0_5_line_63 | NAYY 4x150 SE | 54 | 56 | 0.013371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_2025-3_0_5_line_64 | NAYY 4x150 SE | 54 | 57 | 0.0084213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_2025-3_0_5_line_65 | NAYY 4x150 SE | 58 | 59 | 0.059098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_2025-3_0_5_line_66 | NAYY 4x150 SE | 59 | 60 | 0.0082376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_2025-3_0_5_line_67 | NAYY 4x150 SE | 60 | 61 | 0.0021618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_2025-3_0_5_line_68 | NAYY 4x150 SE | 61 | 62 | 0.042185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_2025-3_0_5_line_69 | NAYY 4x150 SE | 63 | 65 | 0.028434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_2025-3_0_5_line_70 | NAYY 4x150 SE | 64 | 66 | 0.0038403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_2025-3_0_5_line_71 | NAYY 4x150 SE | 65 | 76 | 0.0094406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_2025-3_0_5_line_72 | NAYY 4x150 SE | 66 | 96 | 0.018267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_2025-3_0_5_line_73 | NAYY 4x150 SE | 67 | 68 | 0.05346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_2025-3_0_5_line_74 | NAYY 4x150 SE | 67 | 69 | 0.021281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_2025-3_0_5_line_75 | NAYY 4x150 SE | 69 | 70 | 0.0062674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_2025-3_0_5_line_76 | NAYY 4x150 SE | 70 | 71 | 0.01962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_2025-3_0_5_line_77 | NAYY 4x150 SE | 71 | 72 | 0.031571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_2025-3_0_5_line_78 | NAYY 4x150 SE | 72 | 73 | 0.024178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_2025-3_0_5_line_79 | NAYY 4x150 SE | 74 | 75 | 0.0012491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_2025-3_0_5_line_80 | NAYY 4x150 SE | 75 | 77 | 0.0402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_2025-3_0_5_line_81 | NAYY 4x150 SE | 76 | 78 | 0.010652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_2025-3_0_5_line_82 | NAYY 4x150 SE | 77 | 79 | 0.026131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_2025-3_0_5_line_83 | NAYY 4x150 SE | 77 | 80 | 0.026972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_2025-3_0_5_line_84 | NAYY 4x150 SE | 79 | 81 | 0.018145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_2025-3_0_5_line_85 | NAYY 4x150 SE | 80 | 82 | 0.024287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_2025-3_0_5_line_86 | NAYY 4x150 SE | 81 | 83 | 0.013139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_2025-3_0_5_line_87 | NAYY 4x150 SE | 81 | 84 | 0.019747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_2025-3_0_5_line_88 | NAYY 4x150 SE | 82 | 85 | 0.02105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_2025-3_0_5_line_89 | NAYY 4x150 SE | 83 | 94 | 0.022187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_2025-3_0_5_line_90 | NAYY 4x150 SE | 84 | 89 | 0.011724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_2025-3_0_5_line_91 | NAYY 4x150 SE | 84 | 87 | 0.015319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_2025-3_0_5_line_92 | NAYY 4x150 SE | 85 | 86 | 0.081329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_2025-3_0_5_line_93 | NAYY 4x150 SE | 87 | 88 | 0.0029488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_2025-3_0_5_line_94 | NAYY 4x150 SE | 88 | 90 | 0.0098395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_2025-3_0_5_line_95 | NAYY 4x150 SE | 89 | 91 | 0.0063452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_2025-3_0_5_line_96 | NAYY 4x150 SE | 90 | 92 | 0.03063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_2025-3_0_5_line_97 | NAYY 4x150 SE | 91 | 93 | 0.012984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_2025-3_0_5_line_98 | NAYY 4x150 SE | 92 | 95 | 0.015828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_2025-3_0_5_line_99 | NAYY 4x150 SE | 93 | 97 | 0.017319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_2025-3_0_5_line_100 | NAYY 4x150 SE | 94 | 99 | 0.014495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_2025-3_0_5_line_101 | NAYY 4x150 SE | 95 | 96 | 0.015931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_2025-3_0_5_line_102 | NAYY 4x150 SE | 97 | 98 | 0.023571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_2025-3_0_5_line_103 | NAYY 4x150 SE | 101 | 102 | 0.0011872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_2025-3_0_5_line_104 | NAYY 4x150 SE | 104 | 105 | 0.031203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_2025-3_0_5_line_105 | NAYY 4x150 SE | 104 | 106 | 0.030227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_2025-3_0_5_line_106 | NAYY 4x150 SE | 105 | 107 | 0.036879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_2025-3_0_5_line_107 | NAYY 4x150 SE | 105 | 108 | 0.021695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_2025-3_0_5_line_108 | NAYY 4x150 SE | 107 | 109 | 0.031592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_2025-3_0_5_line_109 | NAYY 4x150 SE | 107 | 110 | 0.031706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_2025-3_0_5_line_110 | NAYY 4x150 SE | 110 | 118 | 0.02785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_2025-3_0_5_line_111 | NAYY 4x150 SE | 110 | 113 | 0.026555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_2025-3_0_5_line_112 | NAYY 4x150 SE | 111 | 112 | 0.026899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_2025-3_0_5_line_113 | NAYY 4x150 SE | 112 | 113 | 0.009432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_2025-3_0_5_line_114 | NAYY 4x150 SE | 112 | 114 | 0.02727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_2025-3_0_5_line_115 | NAYY 4x150 SE | 114 | 115 | 0.006854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_2025-3_0_5_line_116 | NAYY 4x150 SE | 114 | 116 | 0.029189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_2025-3_0_5_line_117 | NAYY 4x150 SE | 114 | 117 | 0.019605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_2025-3_0_5_line_118 | NAYY 4x150 SE | 117 | 119 | 0.006838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2025-3_0_5_trafo_17 | 0.25 MVA 20/0.4 kV | 120 | 29 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2552933.2292 | 1185242.5693 | 2552963.4991 | 1185241.1546 | 2552972.0843 | 1185242.8484
1 | 2552923.7363 | 1185243.013 | 2552933.2292 | 1185242.5693
2 | 2552972.0843 | 1185242.8484 | 2552975.3751 | 1185243.4976
3 | 2552992.1097 | 1185246.7992 | 2552975.3751 | 1185243.4976
4 | 2553149.5937 | 1185319.7916 | 2553164.4258 | 1185329.0026
5 | 2553149.5937 | 1185319.7916 | 2553021.8163 | 1185233.0822
6 | 2553164.4258 | 1185329.0026 | 2553158.243 | 1185343.4701 | 2553158.8691 | 1185356.161 | 2553165.7122 | 1185364.6009
7 | 2553164.4258 | 1185329.0026 | 2553182.0192 | 1185339.993 | 2553184.7818 | 1185341.892
8 | 2553001.7165 | 1185227.1796 | 2553021.8163 | 1185233.0822
9 | 2553001.7165 | 1185227.1796 | 2552992.1097 | 1185246.7992
10 | 2552946.2358 | 1185310.9286 | 2552967.5389 | 1185293.8293 | 2552978.6257 | 1185275.1208 | 2552992.1097 | 1185246.7992
11 | 2552946.2358 | 1185310.9286 | 2552948.8979 | 1185322.3805 | 2552956.5823 | 1185328.9891
12 | 2552993.4822 | 1185356.166 | 2552968.0229 | 1185338.8279 | 2552956.5823 | 1185328.9891
13 | 2553165.7122 | 1185364.6009 | 2553179.711 | 1185380.9959
14 | 2553165.7122 | 1185364.6009 | 2553170.5273 | 1185363.5515 | 2553182.4985 | 1185371.9723
15 | 2553203.4908 | 1185355.2707 | 2553200.872 | 1185352.9524 | 2553184.7818 | 1185341.892
16 | 2553198.771 | 1185403.3186 | 2553179.711 | 1185380.9959
17 | 2553222.0986 | 1185371.5839 | 2553217.7022 | 1185367.8511 | 2553203.4908 | 1185355.2707
18 | 2553270.3834 | 1185458.9242 | 2553294.7698 | 1185470.3782
19 | 2553270.3834 | 1185458.9242 | 2553246.1665 | 1185447.5497 | 2553243.7608 | 1185446.1126
20 | 2553294.7698 | 1185470.3782 | 2553317.3211 | 1185480.9704
21 | 2553243.7608 | 1185446.1126 | 2553233.3081 | 1185439.8683 | 2553230.8872 | 1185437.8104
22 | 2553317.3211 | 1185480.9704 | 2553317.5476 | 1185481.0767
23 | 2553219.671 | 1185427.7085 | 2553221.9299 | 1185430.1965 | 2553230.8872 | 1185437.8104
24 | 2553343.8425 | 1185493.3337 | 2553317.5476 | 1185481.0767
25 | 2553317.5476 | 1185481.0767 | 2553308.5494 | 1185500.7119
26 | 2553198.771 | 1185403.3186 | 2553210.8755 | 1185418.0208 | 2553219.671 | 1185427.7085
27 | 2553343.8425 | 1185493.3337 | 2553370.2072 | 1185505.8511
28 | 2553343.8425 | 1185493.3337 | 2553333.6629 | 1185515.1782
29 | 2553198.771 | 1185403.3186 | 2553173.4779 | 1185410.8987 | 2553166.7778 | 1185412.9078 | 2553162.5911 | 1185413.2964 | 2553148.3808 | 1185407.449
30 | 2553358.1099 | 1185429.9923 | 2553339.042 | 1185415.1395 | 2553333.1709 | 1185405.228
31 | 2553322.0975 | 1185386.534 | 2553333.1709 | 1185405.228
32 | 2553332.7141 | 1185373.9442 | 2553327.4246 | 1185380.6892 | 2553324.8917 | 1185383.7217 | 2553322.0975 | 1185386.534
33 | 2553322.0975 | 1185386.534 | 2553317.8417 | 1185388.824 | 2553312.9953 | 1185389.7735 | 2553308.8691 | 1185390.0948 | 2553304.7145 | 1185389.7159 | 2553297.2769 | 1185388.1843 | 2553296.6042 | 1185388.0613
34 | 2553332.7141 | 1185373.9442 | 2553327.4806 | 1185368.3264 | 2553317.2731 | 1185356.0995 | 2553303.0804 | 1185335.1398
35 | 2553332.7141 | 1185373.9442 | 2553353.1885 | 1185341.8756
36 | 2553332.7141 | 1185373.9442 | 2553348.4568 | 1185389.3853 | 2553348.8871 | 1185389.7634
37 | 2553294.8938 | 1185387.7483 | 2553296.6042 | 1185388.0613
38 | 2553297.3918 | 1185326.7387 | 2553303.0804 | 1185335.1398
39 | 2553373.4194 | 1185310.1884 | 2553353.1885 | 1185341.8756
40 | 2553272.6689 | 1185384.8304 | 2553284.1411 | 1185386.0191 | 2553290.7501 | 1185386.9902 | 2553294.8938 | 1185387.7483
41 | 2553391.4235 | 1185541.5471 | 2553436.8996 | 1185515.5646
42 | 2553436.8996 | 1185515.5646 | 2553533.8343 | 1185501.6915
43 | 2553380.5281 | 1185552.0907 | 2553385.8587 | 1185548.6694 | 2553390.2027 | 1185543.9885 | 2553391.4235 | 1185541.5471
44 | 2553391.4235 | 1185541.5471 | 2553393.0656 | 1185538.2631 | 2553394.0236 | 1185531.9299 | 2553393.0794 | 1185525.3559 | 2553390.5137 | 1185519.2949 | 2553386.3473 | 1185514.458 | 2553381.1618 | 1185511.0522 | 2553370.2072 | 1185505.8511
45 | 2553533.8343 | 1185501.6915 | 2553550.4395 | 1185509.4111 | 2553566.6596 | 1185516.678 | 2553583.0457 | 1185523.7101 | 2553584.2724 | 1185524.2282
46 | 2553533.8343 | 1185501.6915 | 2553542.0917 | 1185493.8453 | 2553549.4315 | 1185489.6971 | 2553557.4136 | 1185489.635 | 2553572.9567 | 1185496.1956 | 2553580.0344 | 1185499.5647
47 | 2553380.5281 | 1185552.0907 | 2553390.8428 | 1185568.7063
48 | 2553375.9526 | 1185553.5049 | 2553380.5281 | 1185552.0907
49 | 2553580.0344 | 1185499.5647 | 2553591.2254 | 1185494.0748 | 2553631.5228 | 1185490.4934
50 | 2553580.0344 | 1185499.5647 | 2553631.6922 | 1185522.2227
51 | 2553631.5228 | 1185490.4934 | 2553671.9674 | 1185521.7165
52 | 2553631.5228 | 1185490.4934 | 2553609.0748 | 1185473.3249 | 2553608.1134 | 1185472.7241
53 | 2553648.7137 | 1185553.0498 | 2553639.1766 | 1185527.7767 | 2553636.4941 | 1185524.3289 | 2553631.6922 | 1185522.2227
54 | 2553648.7137 | 1185553.0498 | 2553659.165 | 1185558.4606 | 2553664.6282 | 1185561.2865 | 2553680.384 | 1185569.7356 | 2553688.7303 | 1185574.329
55 | 2553688.7303 | 1185574.329 | 2553711.5463 | 1185586.8702 | 2553743.1363 | 1185604.4119
56 | 2553765.6551 | 1185616.9165 | 2553743.1363 | 1185604.4119
57 | 2553709.583 | 1185548.2088 | 2553701.127 | 1185544.2277 | 2553686.1886 | 1185532.6953
58 | 2553709.583 | 1185548.2088 | 2553717.3573 | 1185551.8617 | 2553724.1967 | 1185549.0676
59 | 2553679.1697 | 1185527.2767 | 2553686.1886 | 1185532.6953
60 | 2553671.9674 | 1185521.7165 | 2553679.1697 | 1185527.2767
61 | 2553585.9723 | 1185433.816 | 2553581.8275 | 1185443.5424 | 2553582.0973 | 1185452.7231 | 2553585.217 | 1185458.4131 | 2553608.1134 | 1185472.7241
62 | 2553574.5759 | 1185424.6773 | 2553585.9723 | 1185433.816
63 | 2553574.5759 | 1185424.6773 | 2553562.9738 | 1185431.3242
64 | 2553574.5759 | 1185424.6773 | 2553581.4978 | 1185419.8809
65 | 2553861.721 | 1185673.6184 | 2553860.7098 | 1185672.7527 | 2553853.8088 | 1185667.5253 | 2553846.4897 | 1185662.5013 | 2553836.1377 | 1185656.0666 | 2553825.2761 | 1185649.8583 | 2553811.6793 | 1185642.3503
66 | 2553804.4681 | 1185638.3683 | 2553811.6793 | 1185642.3503
67 | 2553804.4681 | 1185638.3683 | 2553802.5754 | 1185637.3237
68 | 2553802.5754 | 1185637.3237 | 2553774.6317 | 1185621.9011 | 2553765.6551 | 1185616.9165
69 | 2553297.3918 | 1185326.7387 | 2553297.8849 | 1185325.3786 | 2553307.0999 | 1185300.0132
70 | 2553375.486 | 1185306.9516 | 2553373.4194 | 1185310.1884
71 | 2553307.0999 | 1185300.0132 | 2553310.3234 | 1185291.1401
72 | 2553375.486 | 1185306.9516 | 2553384.0756 | 1185290.8202
73 | 2553272.6689 | 1185384.8304 | 2553265.9331 | 1185384.2383 | 2553244.574 | 1185381.5705 | 2553237.4292 | 1185380.4035 | 2553232.8698 | 1185379.0051 | 2553227.7052 | 1185376.3441 | 2553222.0986 | 1185371.5839
74 | 2553272.6689 | 1185384.8304 | 2553274.5668 | 1185366.9613 | 2553273.7238 | 1185363.7585
75 | 2553273.7238 | 1185363.7585 | 2553272.1285 | 1185357.6975 | 2553272.1285 | 1185357.6975
76 | 2553256.354 | 1185346.0306 | 2553272.1285 | 1185357.6975
77 | 2553230.9714 | 1185327.2575 | 2553256.354 | 1185346.0306
78 | 2553211.5326 | 1185312.8804 | 2553230.9714 | 1185327.2575
79 | 2553269.5808 | 1185263.3199 | 2553269.964 | 1185264.5088
80 | 2553257.1326 | 1185225.0979 | 2553258.3261 | 1185228.4015 | 2553269.5808 | 1185263.3199
81 | 2553310.3234 | 1185291.1401 | 2553313.9605 | 1185281.1287
82 | 2553257.1326 | 1185225.0979 | 2553260.3817 | 1185224.8279 | 2553265.3239 | 1185224.4113 | 2553282.9984 | 1185227.3104
83 | 2553257.1326 | 1185225.0979 | 2553250.1319 | 1185199.0506
84 | 2553300.9037 | 1185230.2475 | 2553282.9984 | 1185227.3104
85 | 2553244.228 | 1185175.494 | 2553248.2263 | 1185191.9606 | 2553250.1319 | 1185199.0506
86 | 2553300.9037 | 1185230.2475 | 2553295.5855 | 1185218.2328
87 | 2553300.9037 | 1185230.2475 | 2553318.7679 | 1185238.7681
88 | 2553244.228 | 1185175.494 | 2553240.8992 | 1185176.2982 | 2553232.8321 | 1185178.2402 | 2553223.8163 | 1185180.8455
89 | 2553295.5855 | 1185218.2328 | 2553286.605 | 1185197.9442
90 | 2553318.7679 | 1185238.7681 | 2553330.3501 | 1185236.9527
91 | 2553318.7679 | 1185238.7681 | 2553321.1645 | 1185253.8988
92 | 2553223.8163 | 1185180.8455 | 2553220.4772 | 1185182.2946 | 2553216.611 | 1185184.6595 | 2553211.7919 | 1185190.078 | 2553208.4772 | 1185195.618 | 2553207.4152 | 1185200.34 | 2553205.967 | 1185213.2473 | 2553203.423 | 1185237.2693 | 2553200.2147 | 1185254.4371
93 | 2553321.6258 | 1185256.8112 | 2553321.1645 | 1185253.8988
94 | 2553321.6258 | 1185256.8112 | 2553330.8442 | 1185260.2518
95 | 2553330.3501 | 1185236.9527 | 2553335.3393 | 1185236.1707 | 2553336.5527 | 1185236.6234
96 | 2553330.8442 | 1185260.2518 | 2553359.5404 | 1185270.962
97 | 2553348.7181 | 1185241.1623 | 2553336.5527 | 1185236.6234
98 | 2553359.5404 | 1185270.962 | 2553362.7057 | 1185272.1434 | 2553372.0799 | 1185280.3363
99 | 2553348.7181 | 1185241.1623 | 2553364.9444 | 1185247.2163
100 | 2553283.0111 | 1185183.9398 | 2553285.6917 | 1185195.8809 | 2553286.605 | 1185197.9442
101 | 2553384.0756 | 1185290.8202 | 2553372.0799 | 1185280.3363
102 | 2553364.9444 | 1185247.2163 | 2553387.028 | 1185255.4557
103 | 2553333.6629 | 1185515.1782 | 2553333.1614 | 1185516.2543
104 | 2553346.8827 | 1185543.5263 | 2553362.6739 | 1185551.5519 | 2553369.344 | 1185553.5342 | 2553375.9526 | 1185553.5049
105 | 2553375.9526 | 1185553.5049 | 2553392.1233 | 1185579.0425
106 | 2553313.9288 | 1185526.7855 | 2553346.8827 | 1185543.5263
107 | 2553346.8827 | 1185543.5263 | 2553344.9272 | 1185553.069 | 2553345.4596 | 1185555.7663 | 2553353.6089 | 1185560.0456
108 | 2553326.4642 | 1185551.7791 | 2553327.4534 | 1185548.4807 | 2553312.9537 | 1185534.8309 | 2553312.5143 | 1185532.3107 | 2553313.9288 | 1185526.7855
109 | 2553285.5949 | 1185512.3991 | 2553313.9288 | 1185526.7855
110 | 2553285.5949 | 1185512.3991 | 2553284.0333 | 1185516.6692 | 2553284.5683 | 1185519.7 | 2553288.3966 | 1185522.2826 | 2553294.4392 | 1185526.9601 | 2553295.816 | 1185529.3173 | 2553296.4221 | 1185531.6694 | 2553295.1751 | 1185534.2139
111 | 2553285.5949 | 1185512.3991 | 2553261.9166 | 1185500.3775
112 | 2553253.5065 | 1185496.1077 | 2553251.9841 | 1185499.5326 | 2553252.0105 | 1185502.912 | 2553253.7258 | 1185505.6001 | 2553267.8041 | 1185514.3624
113 | 2553253.5065 | 1185496.1077 | 2553261.9166 | 1185500.3775
114 | 2553229.1412 | 1185483.7249 | 2553253.5065 | 1185496.1077
115 | 2553229.1412 | 1185483.7249 | 2553232.2835 | 1185477.6303
116 | 2553229.1412 | 1185483.7249 | 2553232.5813 | 1185493.2587 | 2553237.0586 | 1185498.7934 | 2553238.5889 | 1185502.2277 | 2553235.0139 | 1185509.5931
117 | 2553229.1412 | 1185483.7249 | 2553211.6181 | 1185474.8349
118 | 2553208.6442 | 1185480.9949 | 2553211.6181 | 1185474.8349

## bus_geodata
| x | y | coords
0 | 2552933.2292 | 1185242.5693
1 | 2552972.0843 | 1185242.8484
2 | 2552923.7363 | 1185243.013
3 | 2552975.3751 | 1185243.4976
4 | 2553149.5937 | 1185319.7916
5 | 2553164.4258 | 1185329.0026
6 | 2553021.8163 | 1185233.0822
7 | 2552992.1097 | 1185246.7992
8 | 2553001.7165 | 1185227.1796
9 | 2552946.2358 | 1185310.9286
10 | 2552956.5823 | 1185328.9891
11 | 2552993.4822 | 1185356.166
12 | 2553165.7122 | 1185364.6009
13 | 2553184.7818 | 1185341.892
14 | 2553179.711 | 1185380.9959
15 | 2553182.4985 | 1185371.9723
16 | 2553203.4908 | 1185355.2707
17 | 2553270.3834 | 1185458.9242
18 | 2553294.7698 | 1185470.3782
19 | 2553243.7608 | 1185446.1126
20 | 2553317.3211 | 1185480.9704
21 | 2553230.8872 | 1185437.8104
22 | 2553317.5476 | 1185481.0767
23 | 2553219.671 | 1185427.7085
24 | 2553343.8425 | 1185493.3337
25 | 2553308.5494 | 1185500.7119
26 | 2553198.771 | 1185403.3186
27 | 2553358.1099 | 1185429.9923
28 | 2553333.1709 | 1185405.228
29 | 2553322.0975 | 1185386.534
30 | 2553332.7141 | 1185373.9442
31 | 2553296.6042 | 1185388.0613
32 | 2553303.0804 | 1185335.1398
33 | 2553353.1885 | 1185341.8756
34 | 2553348.8871 | 1185389.7634
35 | 2553294.8938 | 1185387.7483
36 | 2553436.8996 | 1185515.5646
37 | 2553391.4235 | 1185541.5471
38 | 2553533.8343 | 1185501.6915
39 | 2553380.5281 | 1185552.0907
40 | 2553370.2072 | 1185505.8511
41 | 2553584.2724 | 1185524.2282
42 | 2553580.0344 | 1185499.5647
43 | 2553631.5228 | 1185490.4934
44 | 2553631.6922 | 1185522.2227
45 | 2553648.7137 | 1185553.0498
46 | 2553688.7303 | 1185574.329
47 | 2553743.1363 | 1185604.4119
48 | 2553709.583 | 1185548.2088
49 | 2553686.1886 | 1185532.6953
50 | 2553724.1967 | 1185549.0676
51 | 2553671.9674 | 1185521.7165
52 | 2553608.1134 | 1185472.7241
53 | 2553585.9723 | 1185433.816
54 | 2553574.5759 | 1185424.6773
55 | 2553679.1697 | 1185527.2767
56 | 2553562.9738 | 1185431.3242
57 | 2553581.4978 | 1185419.881
58 | 2553861.721 | 1185673.6184
59 | 2553811.6793 | 1185642.3503
60 | 2553804.4681 | 1185638.3683
61 | 2553802.5754 | 1185637.3237
62 | 2553765.6551 | 1185616.9165
63 | 2553297.3918 | 1185326.7387
64 | 2553373.4194 | 1185310.1884
65 | 2553307.0999 | 1185300.0132
66 | 2553375.486 | 1185306.9516
67 | 2553272.6689 | 1185384.8304
68 | 2553222.0986 | 1185371.5839
69 | 2553273.7238 | 1185363.7585
70 | 2553272.1285 | 1185357.6976
71 | 2553256.354 | 1185346.0306
72 | 2553230.9714 | 1185327.2575
73 | 2553211.5326 | 1185312.8804
74 | 2553269.964 | 1185264.5088
75 | 2553269.5808 | 1185263.3199
76 | 2553310.3234 | 1185291.1401
77 | 2553257.1326 | 1185225.0979
78 | 2553313.9605 | 1185281.1287
79 | 2553282.9984 | 1185227.3104
80 | 2553250.1319 | 1185199.0506
81 | 2553300.9037 | 1185230.2475
82 | 2553244.228 | 1185175.494
83 | 2553295.5855 | 1185218.2328
84 | 2553318.7679 | 1185238.7681
85 | 2553223.8163 | 1185180.8455
86 | 2553200.2147 | 1185254.4371
87 | 2553321.1645 | 1185253.8988
88 | 2553321.6258 | 1185256.8112
89 | 2553330.3501 | 1185236.9527
90 | 2553330.8442 | 1185260.2518
91 | 2553336.5527 | 1185236.6234
92 | 2553359.5404 | 1185270.962
93 | 2553348.7181 | 1185241.1623
94 | 2553286.605 | 1185197.9442
95 | 2553372.0799 | 1185280.3363
96 | 2553384.0756 | 1185290.8202
97 | 2553364.9444 | 1185247.2163
98 | 2553387.028 | 1185255.4557
99 | 2553283.0111 | 1185183.9398
100 | 2553148.3808 | 1185407.449
101 | 2553333.6629 | 1185515.1782
102 | 2553333.1614 | 1185516.2543
103 | 2553390.8428 | 1185568.7063
104 | 2553375.9526 | 1185553.5049
105 | 2553346.8827 | 1185543.5263
106 | 2553392.1233 | 1185579.0425
107 | 2553313.9288 | 1185526.7855
108 | 2553353.6089 | 1185560.0456
109 | 2553326.4642 | 1185551.7791
110 | 2553285.5949 | 1185512.3991
111 | 2553267.8041 | 1185514.3624
112 | 2553253.5065 | 1185496.1077
113 | 2553261.9166 | 1185500.3775
114 | 2553229.1412 | 1185483.7249
115 | 2553232.2835 | 1185477.6303
116 | 2553235.0139 | 1185509.5931
117 | 2553211.6181 | 1185474.8349
118 | 2553295.1751 | 1185534.2139
119 | 2553208.6442 | 1185480.9949
120 | 2553332.7141 | 1185373.9442

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98449 | -0.1085 | 0.0023312 | 0.00058425
1 | 0.9848 | -0.1063 | 0.0013349 | 0.00033456
2 | 0.98445 | -0.1088 | 0.0031281 | 0.00078398
3 | 0.98483 | -0.10607 | 0.001962 | 0.00049172
4 | 0.98933 | -0.074149 | 0 | 0
5 | 0.98972 | -0.071427 | 0 | 0
6 | 0.98592 | -0.09835 | 0.0012522 | 0.00031383
7 | 0.98505 | -0.10453 | 0 | 0
8 | 0.98549 | -0.10138 | 0 | 0
9 | 0.98443 | -0.1089 | 0 | 0
10 | 0.98427 | -0.11009 | 0.0029658 | 0.00074329
11 | 0.98411 | -0.11119 | 0.002311 | 0.0005792
12 | 0.98789 | -0.08428 | 0 | 0
13 | 0.99102 | -0.062317 | 0.0037044 | 0.00092842
14 | 0.98695 | -0.090864 | 0.0044856 | 0.0011242
15 | 0.9877 | -0.085603 | 0.0066132 | 0.0016574
16 | 0.9923 | -0.053346 | 0.0017951 | 0.00044988
17 | 0.98232 | -0.12358 | 0.0008474 | 0.00021238
18 | 0.98137 | -0.13031 | 0.0014763 | 0.00036998
19 | 0.98337 | -0.11613 | 0.002468 | 0.00061853
20 | 0.98052 | -0.13641 | 0.0013708 | 0.00034357
21 | 0.98394 | -0.11213 | 0.0010475 | 0.00026253
22 | 0.98051 | -0.13647 | 0 | 0
23 | 0.9845 | -0.10815 | 0.002714 | 0.00068018
24 | 0.97955 | -0.14327 | 0.0025502 | 0.00063914
25 | 0.98045 | -0.13685 | 0.0016798 | 0.000421
26 | 0.98574 | -0.099397 | 0 | 0
27 | 0.99975 | -0.001776 | 0.0023744 | 0.00059508
28 | 0.99987 | -0.00092926 | 0.0019058 | 0.00047763
29 | 1 | 0 | -0.22845 | -0.057455
30 | 0.99801 | -0.01382 | 0 | 0
31 | 0.99826 | -0.011986 | 0.0055183 | 0.001383
32 | 0.99747 | -0.017584 | 0.0022406 | 0.00056155
33 | 0.99417 | -0.040602 | 0.012677 | 0.0031771
34 | 0.99781 | -0.015237 | 0.0062498 | 0.0015663
35 | 0.99815 | -0.012746 | 0.0035957 | 0.00090117
36 | 0.97652 | -0.16497 | 0.00099054 | 0.00024825
37 | 0.97729 | -0.15941 | 0.0015921 | 0.00039903
38 | 0.97511 | -0.17505 | 0 | 0
39 | 0.97667 | -0.16384 | 0 | 0
40 | 0.97868 | -0.14947 | 0.0017142 | 0.00042962
41 | 0.97494 | -0.17628 | 0.0021192 | 0.00053111
42 | 0.97441 | -0.18007 | 0 | 0
43 | 0.97326 | -0.18836 | 0 | 0
44 | 0.97407 | -0.18251 | 0.00078554 | 0.00019687
45 | 0.97387 | -0.184 | 0 | 0
46 | 0.97361 | -0.18584 | 0 | 0
47 | 0.97309 | -0.18962 | 0.00066891 | 0.00016764
48 | 0.97293 | -0.19077 | 0 | 0
49 | 0.97299 | -0.19028 | 0.00038129 | 9.5559e-05
50 | 0.97289 | -0.19105 | 0.0016404 | 0.00041112
51 | 0.97305 | -0.18986 | 0.00038194 | 9.5724e-05
52 | 0.97274 | -0.19212 | 0.00090822 | 0.00022762
53 | 0.97186 | -0.19842 | 0 | 0
54 | 0.97162 | -0.20015 | 0 | 0
55 | 0.97302 | -0.19009 | 0.00038155 | 9.5626e-05
56 | 0.97156 | -0.20058 | 0.0030592 | 0.00076671
57 | 0.97152 | -0.20087 | 0.0081502 | 0.0020426
58 | 0.97185 | -0.19854 | 0.001329 | 0.00033307
59 | 0.97196 | -0.19771 | 0.0036296 | 0.00090967
60 | 0.97202 | -0.19728 | 0 | 0
61 | 0.97204 | -0.19717 | 0.0053641 | 0.0013444
62 | 0.97268 | -0.19257 | 0.00053237 | 0.00013342
63 | 0.99739 | -0.018136 | 0 | 0
64 | 0.99105 | -0.062422 | 0.0127 | 0.0031828
65 | 0.99717 | -0.019685 | 0.0016603 | 0.0004161
66 | 0.9908 | -0.064163 | 0 | 0
67 | 0.99677 | -0.022293 | 0 | 0
68 | 0.99371 | -0.043579 | 0.0015538 | 0.00038942
69 | 0.99651 | -0.024168 | 0.0018344 | 0.00045976
70 | 0.99644 | -0.024604 | 0.0013412 | 0.00033613
71 | 0.99629 | -0.025706 | 0.0018346 | 0.0004598
72 | 0.99612 | -0.026897 | 0.0021615 | 0.00054173
73 | 0.99606 | -0.027282 | 0.0015841 | 0.00039702
74 | 0.98162 | -0.12921 | 0.0036382 | 0.00091182
75 | 0.98162 | -0.12916 | 0.0096316 | 0.0024139
76 | 0.99712 | -0.020042 | 0.0012028 | 0.00030146
77 | 0.9824 | -0.12364 | 0 | 0
78 | 0.99708 | -0.020316 | 0.0025628 | 0.00064231
79 | 0.98304 | -0.11905 | 0.0015383 | 0.00038554
80 | 0.98225 | -0.12468 | 0.0017675 | 0.00044298
81 | 0.98353 | -0.11557 | 0 | 0
82 | 0.98218 | -0.12517 | 0 | 0
83 | 0.98339 | -0.11662 | 0.0014635 | 0.00036679
84 | 0.98428 | -0.11023 | 0 | 0
85 | 0.98213 | -0.1256 | 0 | 0
86 | 0.98189 | -0.12725 | 0.0019509 | 0.00048894
87 | 0.98512 | -0.10432 | 0.0011627 | 0.00029139
88 | 0.98528 | -0.10314 | 0 | 0
89 | 0.98409 | -0.1116 | 0.0020477 | 0.00051319
90 | 0.98583 | -0.099231 | 0.0015816 | 0.00039639
91 | 0.98401 | -0.1122 | 0.0025723 | 0.00064467
92 | 0.98762 | -0.086584 | 0.002253 | 0.00056465
93 | 0.98388 | -0.1131 | 0.00099851 | 0.00025025
94 | 0.98319 | -0.11804 | 0.0015633 | 0.0003918
95 | 0.98859 | -0.079702 | 0.0020592 | 0.00051609
96 | 0.98962 | -0.072455 | 0 | 0
97 | 0.98374 | -0.11411 | 0.0027193 | 0.00068153
98 | 0.98364 | -0.11483 | 0.0029528 | 0.00074005
99 | 0.98309 | -0.11874 | 0.0046502 | 0.0011655
100 | 0.98532 | -0.10241 | 0.005549 | 0.0013907
101 | 0.97941 | -0.14427 | 0.0017904 | 0.00044873
102 | 0.97941 | -0.1443 | 0.0022193 | 0.00055621
103 | 0.97663 | -0.16412 | 0.0013869 | 0.00034759
104 | 0.97649 | -0.16514 | 0 | 0
105 | 0.97539 | -0.17299 | 0 | 0
106 | 0.9764 | -0.16579 | 0.0020438 | 0.00051222
107 | 0.97427 | -0.18108 | 0 | 0
108 | 0.97529 | -0.1737 | 0.0031168 | 0.00078114
109 | 0.97419 | -0.18161 | 0.0016066 | 0.00040266
110 | 0.97337 | -0.18751 | 0 | 0
111 | 0.97243 | -0.19425 | 0.0018557 | 0.00046508
112 | 0.97251 | -0.19372 | 0 | 0
113 | 0.97271 | -0.19226 | 0.0022506 | 0.00056404
114 | 0.97199 | -0.19743 | 0 | 0
115 | 0.97197 | -0.19761 | 0.0025084 | 0.00062868
116 | 0.97189 | -0.19818 | 0.0024279 | 0.00060849
117 | 0.97177 | -0.19907 | 0 | 0
118 | 0.97328 | -0.18818 | 0.0022839 | 0.00057241
119 | 0.97169 | -0.19964 | 0.0079214 | 0.0019853
120 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0054594 | -0.0013682 | 0.0054611 | 0.0013683 | 1.6593e-06 | 1.4144e-07 | 0.0082517 | 0.0082515 | 0.0082517 | 0.98449 | -0.1085 | 0.9848 | -0.1063 | 3.0562
1 | 0.0031282 | 0.00078391 | -0.0031281 | -0.00078398 | 1.3257e-07 | -6.9845e-08 | 0.0047282 | 0.0047282 | 0.0047282 | 0.98449 | -0.1085 | 0.98445 | -0.1088 | 1.7512
2 | -0.006796 | -0.0017029 | 0.0067962 | 0.0017029 | 2.207e-07 | 4.2204e-08 | 0.010269 | 0.010269 | 0.010269 | 0.9848 | -0.1063 | 0.98483 | -0.10607 | 3.8032
3 | -0.0087582 | -0.0021946 | 0.0087601 | 0.0021951 | 1.8638e-06 | 4.9976e-07 | 0.013233 | 0.013233 | 0.013233 | 0.98483 | -0.10607 | 0.98505 | -0.10453 | 4.9011
4 | -0.015357 | -0.0038531 | 0.015363 | 0.0038551 | 5.8013e-06 | 2.0074e-06 | 0.023099 | 0.023099 | 0.023099 | 0.98933 | -0.074149 | 0.98972 | -0.071427 | 8.5553
5 | 0.015357 | 0.0038531 | -0.015305 | -0.0038353 | 5.1416e-05 | 1.7799e-05 | 0.023099 | 0.0231 | 0.0231 | 0.98933 | -0.074149 | 0.98592 | -0.09835 | 8.5555
6 | 0.097054 | 0.024447 | -0.09688 | -0.024381 | 0.00017412 | 6.5458e-05 | 0.14596 | 0.14596 | 0.14596 | 0.98972 | -0.071427 | 0.98789 | -0.08428 | 18.02
7 | -0.11242 | -0.028302 | 0.11256 | 0.028356 | 0.00014325 | 5.4167e-05 | 0.16906 | 0.16906 | 0.16906 | 0.98972 | -0.071427 | 0.99102 | -0.062317 | 20.8717
8 | 0.014053 | 0.0035215 | -0.014047 | -0.0035195 | 5.8806e-06 | 1.9947e-06 | 0.02121 | 0.02121 | 0.02121 | 0.98592 | -0.09835 | 0.98549 | -0.10138 | 7.8556
9 | -0.014041 | -0.0035174 | 0.014047 | 0.0035195 | 6.1301e-06 | 2.0796e-06 | 0.02121 | 0.02121 | 0.02121 | 0.98505 | -0.10453 | 0.98549 | -0.10138 | 7.8556
10 | 0.0052812 | 0.0013223 | -0.005278 | -0.0013221 | 3.1913e-06 | 2.0507e-07 | 0.0079774 | 0.0079777 | 0.0079777 | 0.98505 | -0.10453 | 0.98443 | -0.1089 | 2.9547
11 | 0.005278 | 0.0013221 | -0.0052772 | -0.001322 | 8.6945e-07 | 5.6107e-08 | 0.0079777 | 0.0079778 | 0.0079778 | 0.98443 | -0.1089 | 0.98427 | -0.11009 | 2.9547
12 | 0.0023114 | 0.00057875 | -0.002311 | -0.0005792 | 3.4965e-07 | -4.487e-07 | 0.0034941 | 0.0034944 | 0.0034944 | 0.98427 | -0.11009 | 0.98411 | -0.11119 | 1.2942
13 | 0.090265 | 0.022724 | -0.090183 | -0.022693 | 8.2938e-05 | 3.1072e-05 | 0.136 | 0.136 | 0.136 | 0.98789 | -0.08428 | 0.98695 | -0.090864 | 16.79
14 | 0.0066145 | 0.0016577 | -0.0066132 | -0.0016574 | 1.2118e-06 | 2.1564e-07 | 0.009963 | 0.0099631 | 0.0099631 | 0.98789 | -0.08428 | 0.9877 | -0.085603 | 3.6901
15 | -0.11626 | -0.029284 | 0.11641 | 0.02934 | 0.00014602 | 5.5271e-05 | 0.17462 | 0.17462 | 0.17462 | 0.99102 | -0.062317 | 0.9923 | -0.053346 | 21.5583
16 | 0.085697 | 0.021568 | -0.085595 | -0.02153 | 0.00010197 | 3.8096e-05 | 0.12924 | 0.12924 | 0.12924 | 0.98695 | -0.090864 | 0.98574 | -0.099397 | 15.9552
17 | -0.11821 | -0.02979 | 0.11837 | 0.029851 | 0.00016184 | 6.1284e-05 | 0.17731 | 0.17731 | 0.17731 | 0.9923 | -0.053346 | 0.99371 | -0.043579 | 21.8906
18 | 0.072708 | 0.01827 | -0.07264 | -0.018244 | 6.7999e-05 | 2.5131e-05 | 0.11015 | 0.11015 | 0.11015 | 0.98232 | -0.12358 | 0.98137 | -0.13031 | 13.5993
19 | -0.073555 | -0.018482 | 0.073631 | 0.01851 | 7.6347e-05 | 2.824e-05 | 0.11144 | 0.11144 | 0.11144 | 0.98232 | -0.12358 | 0.98337 | -0.11613 | 13.7577
20 | 0.071163 | 0.017874 | -0.071103 | -0.017852 | 6.0353e-05 | 2.2269e-05 | 0.10792 | 0.10792 | 0.10792 | 0.98137 | -0.13031 | 0.98052 | -0.13641 | 13.323
21 | -0.076099 | -0.019129 | 0.076142 | 0.019144 | 4.236e-05 | 1.5708e-05 | 0.11517 | 0.11517 | 0.11517 | 0.98337 | -0.11613 | 0.98394 | -0.11213 | 14.2187
22 | 0.069732 | 0.017509 | -0.069732 | -0.017508 | 5.8298e-07 | 2.1476e-07 | 0.10584 | 0.10584 | 0.10584 | 0.98052 | -0.13641 | 0.98051 | -0.13647 | 13.0662
23 | -0.077189 | -0.019407 | 0.077232 | 0.019423 | 4.2862e-05 | 1.5909e-05 | 0.11676 | 0.11676 | 0.11676 | 0.98394 | -0.11213 | 0.9845 | -0.10815 | 14.4143
24 | 0.068052 | 0.017088 | -0.067987 | -0.017064 | 6.4226e-05 | 2.3608e-05 | 0.10329 | 0.10329 | 0.10329 | 0.98051 | -0.13647 | 0.97955 | -0.14327 | 12.7515
25 | 0.0016799 | 0.00042076 | -0.0016798 | -0.000421 | 8.7596e-08 | -2.3872e-07 | 0.0025493 | 0.0025494 | 0.0025494 | 0.98051 | -0.13647 | 0.98045 | -0.13685 | 0.94423
26 | -0.079946 | -0.020103 | 0.080044 | 0.020139 | 9.7612e-05 | 3.6316e-05 | 0.12086 | 0.12086 | 0.12086 | 0.9845 | -0.10815 | 0.98574 | -0.099397 | 14.9207
27 | 0.061427 | 0.01542 | -0.061374 | -0.015401 | 5.2868e-05 | 1.9233e-05 | 0.093321 | 0.093322 | 0.093322 | 0.97955 | -0.14327 | 0.97868 | -0.14947 | 11.5212
28 | 0.0040103 | 0.0010048 | -0.0040098 | -0.0010049 | 5.5811e-07 | -8.8677e-08 | 0.0060919 | 0.006092 | 0.006092 | 0.97955 | -0.14327 | 0.97941 | -0.14427 | 2.2563
29 | 0.0055513 | 0.0013909 | -0.005549 | -0.0013907 | 2.3151e-06 | 2.1721e-07 | 0.0083798 | 0.0083801 | 0.0083801 | 0.98574 | -0.099397 | 0.98532 | -0.10241 | 3.1037
30 | -0.0023744 | -0.00059508 | 0.0023747 | 0.00059472 | 2.7814e-07 | -3.6107e-07 | 0.0035341 | 0.0035339 | 0.0035341 | 0.99975 | -0.001776 | 0.99987 | -0.00092926 | 1.3089
31 | -0.0042805 | -0.0010724 | 0.004281 | 0.0010723 | 5.5015e-07 | -7.3416e-08 | 0.0063701 | 0.00637 | 0.0063701 | 0.99987 | -0.00092926 | 1 | 0 | 2.3593
32 | 0.084789 | 0.021368 | -0.084626 | -0.021305 | 0.0001637 | 6.2744e-05 | 0.12621 | 0.12621 | 0.12621 | 1 | 0 | 0.99801 | -0.01382 | 46.7443
33 | 0.13857 | 0.035015 | -0.13834 | -0.034926 | 0.00023335 | 8.8714e-05 | 0.2063 | 0.2063 | 0.2063 | 1 | 0 | 0.99826 | -0.011986 | 25.4694
34 | 0.0076724 | 0.0019223 | -0.0076684 | -0.0019214 | 3.9944e-06 | 8.9745e-07 | 0.011439 | 0.011439 | 0.011439 | 0.99801 | -0.01382 | 0.99747 | -0.017584 | 4.2368
35 | 0.070702 | 0.017816 | -0.070438 | -0.017715 | 0.000264 | 0.00010104 | 0.10545 | 0.10545 | 0.10545 | 0.99801 | -0.01382 | 0.99417 | -0.040602 | 39.0557
36 | 0.006251 | 0.0015665 | -0.0062498 | -0.0015663 | 1.2263e-06 | 1.7609e-07 | 0.0093201 | 0.0093202 | 0.0093202 | 0.99801 | -0.01382 | 0.99781 | -0.015237 | 3.4519
37 | 0.13282 | 0.033543 | -0.13281 | -0.033538 | 1.4189e-05 | 5.3892e-06 | 0.19808 | 0.19808 | 0.19808 | 0.99826 | -0.011986 | 0.99815 | -0.012746 | 24.4539
38 | 0.0054278 | 0.0013598 | -0.0054274 | -0.0013598 | 4.1506e-07 | 2.7216e-08 | 0.0080969 | 0.008097 | 0.008097 | 0.99747 | -0.017584 | 0.99739 | -0.018136 | 2.9989
39 | 0.057762 | 0.014538 | -0.057586 | -0.014471 | 0.00017543 | 6.6988e-05 | 0.086476 | 0.086477 | 0.086477 | 0.99417 | -0.040602 | 0.99105 | -0.062422 | 32.0283
40 | 0.12921 | 0.032637 | -0.12904 | -0.032571 | 0.00017324 | 6.5754e-05 | 0.19272 | 0.19272 | 0.19272 | 0.99815 | -0.012746 | 0.99677 | -0.022293 | 23.7922
41 | -0.030447 | -0.0076293 | 0.030471 | 0.0076363 | 2.3449e-05 | 7.0516e-06 | 0.046395 | 0.046394 | 0.046395 | 0.97652 | -0.16497 | 0.97729 | -0.15941 | 5.7278
42 | 0.029457 | 0.007381 | -0.029416 | -0.0073689 | 4.1037e-05 | 1.2113e-05 | 0.044886 | 0.044887 | 0.044887 | 0.97652 | -0.16497 | 0.97511 | -0.17505 | 5.5416
43 | 0.027515 | 0.006906 | -0.027498 | -0.0068997 | 1.6923e-05 | 6.3155e-06 | 0.041898 | 0.041898 | 0.041898 | 0.97729 | -0.15941 | 0.97667 | -0.16384 | 15.5176
44 | -0.059578 | -0.014941 | 0.05966 | 0.014971 | 8.2186e-05 | 2.9803e-05 | 0.090716 | 0.090715 | 0.090716 | 0.97729 | -0.15941 | 0.97868 | -0.14947 | 11.1995
45 | 0.0021195 | 0.00053056 | -0.0021192 | -0.00053111 | 3.6062e-07 | -5.5037e-07 | 0.0032341 | 0.0032344 | 0.0032344 | 0.97511 | -0.17505 | 0.97494 | -0.17628 | 1.1979
46 | 0.027296 | 0.0068384 | -0.027277 | -0.006833 | 1.8951e-05 | 5.325e-06 | 0.041653 | 0.041653 | 0.041653 | 0.97511 | -0.17505 | 0.97441 | -0.18007 | 5.1424
47 | 0.001387 | 0.00034737 | -0.0013869 | -0.00034759 | 5.4489e-08 | -2.2377e-07 | 0.002113 | 0.0021131 | 0.0021131 | 0.97667 | -0.16384 | 0.97663 | -0.16412 | 0.78263
48 | 0.026111 | 0.0065523 | -0.026106 | -0.0065506 | 4.7171e-06 | 1.7545e-06 | 0.039785 | 0.039785 | 0.039785 | 0.97667 | -0.16384 | 0.97649 | -0.16514 | 14.735
49 | 0.014941 | 0.003746 | -0.014923 | -0.0037401 | 1.7144e-05 | 5.9371e-06 | 0.022816 | 0.022816 | 0.022816 | 0.97441 | -0.18007 | 0.97326 | -0.18836 | 8.4505
50 | 0.012337 | 0.003087 | -0.012332 | -0.0030875 | 4.1635e-06 | -5.0587e-07 | 0.018837 | 0.018838 | 0.018838 | 0.97441 | -0.18007 | 0.97407 | -0.18251 | 2.3257
51 | 0.002786 | 0.00069696 | -0.0027855 | -0.00069737 | 5.7839e-07 | -4.1236e-07 | 0.0042591 | 0.0042593 | 0.0042593 | 0.97326 | -0.18836 | 0.97305 | -0.18986 | 1.5775
52 | 0.012137 | 0.0030431 | -0.012131 | -0.003041 | 6.3166e-06 | 2.0644e-06 | 0.018557 | 0.018557 | 0.018557 | 0.97326 | -0.18836 | 0.97274 | -0.19212 | 6.8731
53 | 0.011547 | 0.0028907 | -0.011544 | -0.0028911 | 2.37e-06 | -4.5587e-07 | 0.017638 | 0.017639 | 0.017639 | 0.97407 | -0.18251 | 0.97387 | -0.184 | 2.1776
54 | 0.011544 | 0.0028911 | -0.011542 | -0.0028917 | 2.9332e-06 | -5.6329e-07 | 0.017639 | 0.017639 | 0.017639 | 0.97387 | -0.184 | 0.97361 | -0.18584 | 2.1777
55 | 0.011542 | 0.0028917 | -0.011536 | -0.0028909 | 6.0353e-06 | 7.7582e-07 | 0.017639 | 0.01764 | 0.01764 | 0.97361 | -0.18584 | 0.97309 | -0.18962 | 3.2666
56 | 0.010867 | 0.0027233 | -0.010862 | -0.0027219 | 4.438e-06 | 1.3871e-06 | 0.016617 | 0.016617 | 0.016617 | 0.97309 | -0.18962 | 0.97268 | -0.19257 | 6.1544
57 | -0.0016404 | -0.00041094 | 0.0016406 | 0.00041064 | 1.1083e-07 | -3.0783e-07 | 0.0025089 | 0.0025087 | 0.0025089 | 0.97293 | -0.19077 | 0.97299 | -0.19028 | 0.92921
58 | 0.0016404 | 0.00041094 | -0.0016404 | -0.00041112 | 6.2758e-08 | -1.7428e-07 | 0.0025089 | 0.0025089 | 0.0025089 | 0.97293 | -0.19077 | 0.97289 | -0.19105 | 0.92924
59 | -0.0020218 | -0.0005062 | 0.0020219 | 0.00050611 | 5.2893e-08 | -8.9791e-08 | 0.0030918 | 0.0030918 | 0.0030918 | 0.97299 | -0.19028 | 0.97302 | -0.19009 | 1.1451
60 | 0.0024035 | 0.00060165 | -0.0024034 | -0.00060173 | 7.6693e-08 | -8.3523e-08 | 0.0036753 | 0.0036753 | 0.0036753 | 0.97305 | -0.18986 | 0.97302 | -0.19009 | 1.3612
61 | 0.011223 | 0.0028134 | -0.011213 | -0.0028103 | 9.7934e-06 | 3.1063e-06 | 0.017168 | 0.017168 | 0.017168 | 0.97274 | -0.19212 | 0.97186 | -0.19842 | 6.3586
62 | 0.011213 | 0.0028103 | -0.01121 | -0.0028095 | 2.6824e-06 | 8.5101e-07 | 0.017168 | 0.017168 | 0.017168 | 0.97186 | -0.19842 | 0.97162 | -0.20015 | 6.3587
63 | 0.0030594 | 0.00076661 | -0.0030592 | -0.00076671 | 1.8316e-07 | -9.5149e-08 | 0.0046853 | 0.0046854 | 0.0046854 | 0.97162 | -0.20015 | 0.97156 | -0.20058 | 1.7353
64 | 0.008151 | 0.0020428 | -0.0081502 | -0.0020426 | 8.1886e-07 | 2.1066e-07 | 0.012483 | 0.012483 | 0.012483 | 0.97162 | -0.20015 | 0.97152 | -0.20087 | 4.6234
65 | -0.001329 | -0.00033307 | 0.0013291 | 0.0003324 | 1.5267e-07 | -6.7365e-07 | 0.0020348 | 0.0020346 | 0.0020348 | 0.97185 | -0.19854 | 0.97196 | -0.19771 | 0.75364
66 | -0.0049587 | -0.0012421 | 0.004959 | 0.0012421 | 2.9622e-07 | 1.1827e-08 | 0.0075913 | 0.0075912 | 0.0075913 | 0.97196 | -0.19771 | 0.97202 | -0.19728 | 2.8116
67 | -0.004959 | -0.0012421 | 0.0049591 | 0.0012421 | 7.7737e-08 | 3.1016e-09 | 0.0075912 | 0.0075912 | 0.0075912 | 0.97202 | -0.19728 | 0.97204 | -0.19717 | 2.8116
68 | -0.010323 | -0.0025865 | 0.01033 | 0.0025885 | 6.5735e-06 | 2.005e-06 | 0.015803 | 0.015803 | 0.015803 | 0.97204 | -0.19717 | 0.97268 | -0.19257 | 5.8528
69 | 0.0054274 | 0.0013598 | -0.0054262 | -0.0013597 | 1.1633e-06 | 7.6395e-08 | 0.008097 | 0.0080971 | 0.0080971 | 0.99739 | -0.018136 | 0.99717 | -0.019685 | 2.9989
70 | 0.044887 | 0.011288 | -0.044876 | -0.011284 | 1.0889e-05 | 4.1386e-06 | 0.067409 | 0.067409 | 0.067409 | 0.99105 | -0.062422 | 0.9908 | -0.064163 | 24.9662
71 | 0.003766 | 0.00094361 | -0.0037658 | -0.00094366 | 1.8604e-07 | -5.1596e-08 | 0.0056196 | 0.0056196 | 0.0056196 | 0.99717 | -0.019685 | 0.99712 | -0.020042 | 2.0814
72 | 0.044876 | 0.011284 | -0.044824 | -0.011265 | 5.1795e-05 | 1.9686e-05 | 0.067409 | 0.067409 | 0.067409 | 0.9908 | -0.064163 | 0.98962 | -0.072455 | 24.9663
73 | 0.12028 | 0.030376 | -0.11992 | -0.03024 | 0.00035884 | 0.00013593 | 0.17964 | 0.17964 | 0.17964 | 0.99677 | -0.022293 | 0.99371 | -0.043579 | 22.1778
74 | 0.0087601 | 0.0021947 | -0.0087579 | -0.0021941 | 2.271e-06 | 5.9614e-07 | 0.013077 | 0.013077 | 0.013077 | 0.99677 | -0.022293 | 0.99651 | -0.024168 | 4.8434
75 | 0.0069234 | 0.0017344 | -0.006923 | -0.0017343 | 4.1797e-07 | 7.9113e-08 | 0.010338 | 0.010338 | 0.010338 | 0.99651 | -0.024168 | 0.99644 | -0.024604 | 3.8289
76 | 0.0055818 | 0.0013982 | -0.005581 | -0.0013981 | 8.5061e-07 | 7.162e-08 | 0.0083352 | 0.0083353 | 0.0083353 | 0.99644 | -0.024604 | 0.99629 | -0.025706 | 3.0872
77 | 0.0037464 | 0.00093829 | -0.0037457 | -0.00093847 | 6.1675e-07 | -1.7383e-07 | 0.0055952 | 0.0055953 | 0.0055953 | 0.99629 | -0.025706 | 0.99612 | -0.026897 | 2.0723
78 | 0.0015842 | 0.00039674 | -0.0015841 | -0.00039702 | 8.4489e-08 | -2.8223e-07 | 0.0023664 | 0.0023665 | 0.0023665 | 0.99612 | -0.026897 | 0.99606 | -0.027282 | 0.87649
79 | -0.0036382 | -0.00091182 | 0.0036382 | 0.00091181 | 2.3708e-08 | -6.6724e-09 | 0.0055151 | 0.0055151 | 0.0055151 | 0.98162 | -0.12921 | 0.98162 | -0.12916 | 2.0426
80 | -0.01327 | -0.0033257 | 0.01328 | 0.0033291 | 1.015e-05 | 3.3952e-06 | 0.020115 | 0.020115 | 0.020115 | 0.98162 | -0.12916 | 0.9824 | -0.12364 | 7.4501
81 | 0.0025629 | 0.00064221 | -0.0025628 | -0.00064231 | 9.7228e-08 | -1.0154e-07 | 0.0038247 | 0.0038247 | 0.0038247 | 0.99712 | -0.020042 | 0.99708 | -0.020316 | 1.4166
82 | -0.017 | -0.0042596 | 0.01701 | 0.0042634 | 1.081e-05 | 3.8267e-06 | 0.025749 | 0.025748 | 0.025749 | 0.9824 | -0.12364 | 0.98304 | -0.11905 | 9.5365
83 | 0.0037196 | 0.00093044 | -0.0037191 | -0.00093058 | 5.3412e-07 | -1.3602e-07 | 0.0056334 | 0.0056335 | 0.0056335 | 0.9824 | -0.12364 | 0.98225 | -0.12468 | 2.0865
84 | -0.018549 | -0.0046489 | 0.018558 | 0.0046521 | 8.9254e-06 | 3.2027e-06 | 0.028077 | 0.028077 | 0.028077 | 0.98304 | -0.11905 | 0.98353 | -0.11557 | 10.3989
85 | 0.0019516 | 0.0004876 | -0.0019514 | -0.00048786 | 1.3242e-07 | -2.5646e-07 | 0.0029559 | 0.002956 | 0.002956 | 0.98225 | -0.12468 | 0.98218 | -0.12517 | 1.0948
86 | 0.0076798 | 0.0019245 | -0.0076787 | -0.0019242 | 1.1069e-06 | 2.5899e-07 | 0.011619 | 0.011619 | 0.011619 | 0.98353 | -0.11557 | 0.98339 | -0.11662 | 4.3034
87 | -0.026237 | -0.0065766 | 0.026257 | 0.0065838 | 1.9417e-05 | 7.2172e-06 | 0.039696 | 0.039696 | 0.039696 | 0.98353 | -0.11557 | 0.98428 | -0.11023 | 14.7022
88 | 0.0019514 | 0.00048786 | -0.0019513 | -0.00048808 | 1.1478e-07 | -2.2225e-07 | 0.002956 | 0.0029561 | 0.0029561 | 0.98218 | -0.12517 | 0.98213 | -0.1256 | 1.0949
89 | 0.0062152 | 0.0015574 | -0.006214 | -0.0015573 | 1.2245e-06 | 1.8954e-07 | 0.0094045 | 0.0094046 | 0.0094046 | 0.98339 | -0.11662 | 0.98319 | -0.11804 | 3.4832
90 | 0.011295 | 0.0028306 | -0.011293 | -0.00283 | 2.1332e-06 | 6.7147e-07 | 0.017076 | 0.017076 | 0.017076 | 0.98428 | -0.11023 | 0.98409 | -0.1116 | 6.3245
91 | -0.037552 | -0.0094145 | 0.037583 | 0.0094261 | 3.081e-05 | 1.1655e-05 | 0.056772 | 0.056772 | 0.056772 | 0.98428 | -0.11023 | 0.98512 | -0.10432 | 21.0266
92 | 0.0019513 | 0.00048808 | -0.0019509 | -0.00048894 | 4.4353e-07 | -8.5835e-07 | 0.0029561 | 0.0029565 | 0.0029565 | 0.98213 | -0.1256 | 0.98189 | -0.12725 | 1.095
93 | -0.038746 | -0.0097175 | 0.038752 | 0.0097199 | 6.3031e-06 | 2.3867e-06 | 0.058528 | 0.058528 | 0.058528 | 0.98512 | -0.10432 | 0.98528 | -0.10314 | 21.677
94 | -0.038752 | -0.0097199 | 0.038773 | 0.0097279 | 2.1032e-05 | 7.9639e-06 | 0.058528 | 0.058528 | 0.058528 | 0.98528 | -0.10314 | 0.98583 | -0.099231 | 21.677
95 | 0.0092456 | 0.0023168 | -0.0092449 | -0.0023166 | 7.7382e-07 | 2.1701e-07 | 0.01398 | 0.01398 | 0.01398 | 0.98409 | -0.1116 | 0.98401 | -0.1122 | 5.1778
96 | -0.040355 | -0.010124 | 0.040426 | 0.010151 | 7.0921e-05 | 2.6886e-05 | 0.060915 | 0.060915 | 0.060915 | 0.98583 | -0.099231 | 0.98762 | -0.086584 | 22.5612
97 | 0.0066726 | 0.0016719 | -0.0066718 | -0.0016717 | 8.2491e-07 | 1.5235e-07 | 0.01009 | 0.01009 | 0.01009 | 0.98401 | -0.1122 | 0.98388 | -0.1131 | 3.7371
98 | -0.042679 | -0.010716 | 0.042719 | 0.010731 | 4.0848e-05 | 1.5508e-05 | 0.06431 | 0.064309 | 0.06431 | 0.98762 | -0.086584 | 0.98859 | -0.079702 | 23.8183
99 | 0.0056733 | 0.0014215 | -0.0056725 | -0.0014214 | 7.956e-07 | 8.6084e-08 | 0.0085801 | 0.0085802 | 0.0085802 | 0.98388 | -0.1131 | 0.98374 | -0.11411 | 3.1778
100 | 0.0046507 | 0.0011654 | -0.0046502 | -0.0011655 | 4.481e-07 | -1.1456e-08 | 0.0070386 | 0.0070387 | 0.0070387 | 0.98319 | -0.11804 | 0.98309 | -0.11874 | 2.6069
101 | -0.044779 | -0.011247 | 0.044824 | 0.011265 | 4.5173e-05 | 1.717e-05 | 0.067409 | 0.067409 | 0.067409 | 0.98859 | -0.079702 | 0.98962 | -0.072455 | 24.9663
102 | 0.0029531 | 0.00073987 | -0.0029528 | -0.00074005 | 2.9347e-07 | -1.8635e-07 | 0.0044669 | 0.004467 | 0.004467 | 0.98374 | -0.11411 | 0.98364 | -0.11483 | 1.6544
103 | 0.0022193 | 0.0005562 | -0.0022193 | -0.00055621 | 8.4224e-09 | -1.1701e-08 | 0.0033718 | 0.0033718 | 0.0033718 | 0.97941 | -0.14427 | 0.97941 | -0.1443 | 1.2488
104 | 0.024062 | 0.0060386 | -0.024036 | -0.006029 | 2.6182e-05 | 9.6802e-06 | 0.03667 | 0.03667 | 0.03667 | 0.97649 | -0.16514 | 0.97539 | -0.17299 | 13.5816
105 | 0.002044 | 0.00051191 | -0.0020438 | -0.00051222 | 1.8297e-07 | -3.0772e-07 | 0.0031145 | 0.0031147 | 0.0031147 | 0.97649 | -0.16514 | 0.9764 | -0.16579 | 1.1536
106 | 0.020919 | 0.005248 | -0.020896 | -0.0052394 | 2.344e-05 | 8.5556e-06 | 0.031915 | 0.031915 | 0.031915 | 0.97539 | -0.17299 | 0.97427 | -0.18108 | 11.8204
107 | 0.0031171 | 0.00078098 | -0.0031168 | -0.00078114 | 3.0612e-07 | -1.5302e-07 | 0.0047552 | 0.0047553 | 0.0047553 | 0.97539 | -0.17299 | 0.97529 | -0.1737 | 1.7612
108 | 0.0016067 | 0.00040231 | -0.0016066 | -0.00040266 | 1.1871e-07 | -3.4772e-07 | 0.0024539 | 0.002454 | 0.002454 | 0.97427 | -0.18108 | 0.97419 | -0.18161 | 0.90889
109 | 0.019289 | 0.0048371 | -0.019272 | -0.0048309 | 1.7172e-05 | 6.2103e-06 | 0.029461 | 0.029461 | 0.029461 | 0.97427 | -0.18108 | 0.97337 | -0.18751 | 10.9117
110 | 0.0022842 | 0.00057215 | -0.0022839 | -0.00057241 | 2.1189e-07 | -2.6464e-07 | 0.0034917 | 0.0034919 | 0.0034919 | 0.97337 | -0.18751 | 0.97328 | -0.18818 | 1.2933
111 | 0.016988 | 0.0042588 | -0.016976 | -0.0042548 | 1.1176e-05 | 3.9685e-06 | 0.02597 | 0.02597 | 0.02597 | 0.97337 | -0.18751 | 0.97271 | -0.19226 | 9.6185
112 | -0.0018557 | -0.00046508 | 0.0018558 | 0.00046479 | 1.3533e-07 | -2.8168e-07 | 0.0028395 | 0.0028394 | 0.0028395 | 0.97243 | -0.19425 | 0.97251 | -0.19372 | 1.0517
113 | -0.014723 | -0.0036897 | 0.014726 | 0.0036907 | 2.9867e-06 | 1.0317e-06 | 0.022527 | 0.022527 | 0.022527 | 0.97251 | -0.19372 | 0.97271 | -0.19226 | 8.3434
114 | 0.012867 | 0.0032249 | -0.01286 | -0.0032227 | 6.5957e-06 | 2.1986e-06 | 0.019688 | 0.019688 | 0.019688 | 0.97251 | -0.19372 | 0.97199 | -0.19743 | 7.2918
115 | 0.0025085 | 0.00062862 | -0.0025084 | -0.00062868 | 6.3073e-08 | -6.0692e-08 | 0.0038402 | 0.0038403 | 0.0038403 | 0.97199 | -0.19743 | 0.97197 | -0.19761 | 1.4223
116 | 0.0024281 | 0.00060822 | -0.0024279 | -0.00060849 | 2.5167e-07 | -2.6496e-07 | 0.0037171 | 0.0037172 | 0.0037172 | 0.97199 | -0.19743 | 0.97189 | -0.19818 | 1.3768
117 | 0.0079238 | 0.0019859 | -0.007922 | -0.0019854 | 1.8001e-06 | 4.4942e-07 | 0.01213 | 0.012131 | 0.012131 | 0.97199 | -0.19743 | 0.97177 | -0.19907 | 4.4928
118 | 0.007922 | 0.0019854 | -0.0079214 | -0.0019853 | 6.2788e-07 | 1.5678e-07 | 0.012131 | 0.012131 | 0.012131 | 0.97177 | -0.19907 | 0.97169 | -0.19964 | 4.4928

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22845 | 0.057455

## res_load
| p_mw | q_mvar
0 | 0.0023312 | 0.00058425
1 | 0.0013349 | 0.00033456
2 | 0.0031281 | 0.00078398
3 | 0.001962 | 0.00049172
4 | 0.0012522 | 0.00031383
5 | 0.0029658 | 0.00074329
6 | 0.002311 | 0.0005792
7 | 0.0037044 | 0.00092842
8 | 0.0044856 | 0.0011242
9 | 0.0066132 | 0.0016574
10 | 0.0017951 | 0.00044988
11 | 0.0008474 | 0.00021238
12 | 0.0014763 | 0.00036998
13 | 0.002468 | 0.00061853
14 | 0.0013708 | 0.00034357
15 | 0.0010475 | 0.00026253
16 | 0.002714 | 0.00068018
17 | 0.0025502 | 0.00063914
18 | 0.0016798 | 0.000421
19 | 0.0023744 | 0.00059508
20 | 0.0019058 | 0.00047763
21 | 0.0055183 | 0.001383
22 | 0.0022406 | 0.00056155
23 | 0.012677 | 0.0031771
24 | 0.0062498 | 0.0015663
25 | 0.0035957 | 0.00090117
26 | 0.00099054 | 0.00024825
27 | 0.0015921 | 0.00039903
28 | 0.0017142 | 0.00042962
29 | 0.0021192 | 0.00053111
30 | 0.00078554 | 0.00019687
31 | 0.00066891 | 0.00016764
32 | 0.00038129 | 9.5559e-05
33 | 0.0016404 | 0.00041112
34 | 0.00038194 | 9.5724e-05
35 | 0.00090822 | 0.00022762
36 | 0.00038155 | 9.5626e-05
37 | 0.0030592 | 0.00076671
38 | 0.0081502 | 0.0020426
39 | 0.001329 | 0.00033307
40 | 0.0036296 | 0.00090967
41 | 0.0053641 | 0.0013444
42 | 0.00053237 | 0.00013342
43 | 0.0127 | 0.0031828
44 | 0.0016603 | 0.0004161
45 | 0.0015538 | 0.00038942
46 | 0.0018344 | 0.00045976
47 | 0.0013412 | 0.00033613
48 | 0.0018346 | 0.0004598
49 | 0.0021615 | 0.00054173
50 | 0.0015841 | 0.00039702
51 | 0.0036382 | 0.00091182
52 | 0.0096316 | 0.0024139
53 | 0.0012028 | 0.00030146
54 | 0.0025628 | 0.00064231
55 | 0.0015383 | 0.00038554
56 | 0.0017675 | 0.00044298
57 | 0.0014635 | 0.00036679
58 | 0.0019509 | 0.00048894
59 | 0.0011627 | 0.00029139
60 | 0.0020477 | 0.00051319
61 | 0.0015816 | 0.00039639
62 | 0.0025723 | 0.00064467
63 | 0.002253 | 0.00056465
64 | 0.00099851 | 0.00025025
65 | 0.0015633 | 0.0003918
66 | 0.0020592 | 0.00051609
67 | 0.0027193 | 0.00068153
68 | 0.0029528 | 0.00074005
69 | 0.0046502 | 0.0011655
70 | 0.005549 | 0.0013907
71 | 0.0017904 | 0.00044873
72 | 0.0022193 | 0.00055621
73 | 0.0013869 | 0.00034759
74 | 0.0020438 | 0.00051222
75 | 0.0031168 | 0.00078114
76 | 0.0016066 | 0.00040266
77 | 0.0018557 | 0.00046508
78 | 0.0022506 | 0.00056404
79 | 0.0025084 | 0.00062868
80 | 0.0024279 | 0.00060849
81 | 0.0022839 | 0.00057241
82 | 0.0079214 | 0.0019853

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1