## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2025-6_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2025-6_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2025-6_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2025-6_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2025-6_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2025-6_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2025-6_0_3_node_38 | 0.4 | n |  | TRUE
7 | bus_LV_2025-6_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2025-6_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_2025-6_0_3_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_2025-6_0_3_node_28 | 0.4 | n |  | TRUE
11 | bus_LV_2025-6_0_3_node_29 | 0.4 | n |  | TRUE
12 | bus_LV_2025-6_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2025-6_0_3_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_2025-6_0_3_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_2025-6_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2025-6_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2025-6_0_3_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_2025-6_0_3_node_37 | 0.4 | n |  | TRUE
19 | bus_LV_2025-6_0_3_node_36 | 0.4 | n |  | TRUE
20 | bus_LV_2025-6_0_3_node_33 | 0.4 | n |  | TRUE
21 | bus_LV_2025-6_0_3_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2025-6_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2025-6_0_3_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_2025-6_0_3_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_2025-6_0_3_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_2025-6_0_3_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_2025-6_0_3_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_2025-6_0_3_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_2025-6_0_3_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_2025-6_0_3_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_2025-6_0_3_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_2025-6_0_3_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_2025-6_0_3_node_40 | 0.4 | n |  | TRUE
34 | bus_LV_2025-6_0_3_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_2025-6_0_3_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_2025-6_0_3_node_39 | 0.4 | n |  | TRUE
37 | bus_LV_2025-6_0_3_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_2025-6_0_3_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_2025-6_0_3_node_34 | 0.4 | n |  | TRUE
40 | bus_MV_454_1_node_272 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2025-6_0_3_load_0 | 0 | 0.031658 | 0.0079344 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2025-6_0_3_load_3 | 3 | 0.036129 | 0.0090548 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2025-6_0_3_load_38 | 6 | 0.002521 | 0.00063181 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2025-6_0_3_load_6 | 7 | 0.00897 | 0.0022481 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2025-6_0_3_load_8 | 9 | 0.020656 | 0.005177 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2025-6_0_3_load_28 | 10 | 0.016954 | 0.004249 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2025-6_0_3_load_29 | 11 | 0.0082859 | 0.0020767 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2025-6_0_3_load_9 | 12 | 0.0072711 | 0.0018223 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2025-6_0_3_load_22 | 13 | 0.0094076 | 0.0023578 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2025-6_0_3_load_25 | 14 | 0.0039947 | 0.0010012 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2025-6_0_3_load_37 | 18 | 0.0039042 | 0.00097847 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2025-6_0_3_load_36 | 19 | 0.0059582 | 0.0014933 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2025-6_0_3_load_33 | 20 | 0.0023164 | 0.00058053 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2025-6_0_3_load_12 | 21 | 0.0037174 | 0.00093167 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2025-6_0_3_load_13 | 22 | 0.0089522 | 0.0022436 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2025-6_0_3_load_14 | 23 | 0.0026079 | 0.0006536 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2025-6_0_3_load_27 | 26 | 0.0061882 | 0.0015509 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2025-6_0_3_load_23 | 27 | 0.0048242 | 0.0012091 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2025-6_0_3_load_15 | 28 | 0.0022846 | 0.00057257 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2025-6_0_3_load_17 | 30 | 0.0038495 | 0.00096478 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2025-6_0_3_load_19 | 31 | 0.0033012 | 0.00082736 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2025-6_0_3_load_40 | 33 | 0.0031607 | 0.00079215 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2025-6_0_3_load_24 | 34 | 0.004458 | 0.0011173 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2025-6_0_3_load_39 | 36 | 0.0017337 | 0.00043452 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2025-6_0_3_load_30 | 37 | 0.0041182 | 0.0010321 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2025-6_0_3_load_32 | 38 | 0.00073517 | 0.00018425 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2025-6_0_3_load_34 | 39 | 0.001848 | 0.00046315 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2025-6_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.022717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_2025-6_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.023563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_2025-6_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.05097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_2025-6_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.008906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_2025-6_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.048154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_2025-6_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.011588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_2025-6_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.039214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_2025-6_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.028375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_2025-6_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.0036829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_2025-6_0_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.02118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_2025-6_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.0040845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_2025-6_0_3_line_11 | NAYY 4x150 SE | 9 | 12 | 0.026216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_2025-6_0_3_line_12 | NAYY 4x150 SE | 10 | 13 | 0.036966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_2025-6_0_3_line_13 | NAYY 4x150 SE | 11 | 14 | 0.016494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_2025-6_0_3_line_14 | NAYY 4x150 SE | 12 | 15 | 0.035819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_2025-6_0_3_line_15 | NAYY 4x150 SE | 13 | 32 | 0.018174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_2025-6_0_3_line_16 | NAYY 4x150 SE | 14 | 34 | 0.014868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_2025-6_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.029185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_2025-6_0_3_line_18 | NAYY 4x150 SE | 16 | 17 | 0.0467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_2025-6_0_3_line_19 | NAYY 4x150 SE | 16 | 18 | 0.021849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_2025-6_0_3_line_20 | NAYY 4x150 SE | 17 | 19 | 0.007111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_2025-6_0_3_line_21 | NAYY 4x150 SE | 17 | 20 | 0.013119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_2025-6_0_3_line_22 | NAYY 4x150 SE | 20 | 39 | 0.011101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_2025-6_0_3_line_23 | NAYY 4x150 SE | 21 | 22 | 0.035799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_2025-6_0_3_line_24 | NAYY 4x150 SE | 22 | 23 | 0.051102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_2025-6_0_3_line_25 | NAYY 4x150 SE | 23 | 24 | 0.019638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_2025-6_0_3_line_26 | NAYY 4x150 SE | 24 | 25 | 0.006745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_2025-6_0_3_line_27 | NAYY 4x150 SE | 24 | 26 | 0.037415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_2025-6_0_3_line_28 | NAYY 4x150 SE | 24 | 27 | 0.019305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_2025-6_0_3_line_29 | NAYY 4x150 SE | 25 | 33 | 0.015809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_2025-6_0_3_line_30 | NAYY 4x150 SE | 27 | 34 | 0.017059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_2025-6_0_3_line_31 | NAYY 4x150 SE | 28 | 29 | 0.021569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_2025-6_0_3_line_32 | NAYY 4x150 SE | 29 | 30 | 0.0088352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_2025-6_0_3_line_33 | NAYY 4x150 SE | 30 | 31 | 0.028836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_2025-6_0_3_line_34 | NAYY 4x150 SE | 31 | 32 | 0.021374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_2025-6_0_3_line_35 | NAYY 4x150 SE | 32 | 35 | 0.005307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_2025-6_0_3_line_36 | NAYY 4x150 SE | 35 | 36 | 0.038204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_2025-6_0_3_line_37 | NAYY 4x150 SE | 37 | 38 | 0.00732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_2025-6_0_3_line_38 | NAYY 4x150 SE | 38 | 39 | 0.020773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2025-6_0_3_trafo_5 | 0.25 MVA 20/0.4 kV | 40 | 5 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2554888.4117 | 1187111.3367 | 2554868.9108 | 1187099.6837
1 | 2554848.4326 | 1187088.037 | 2554859.9167 | 1187094.3093 | 2554868.9108 | 1187099.6837
2 | 2554888.4117 | 1187111.3367 | 2554860.878 | 1187154.2302
3 | 2554843.844 | 1187095.6759 | 2554848.4326 | 1187088.037
4 | 2554834.8657 | 1187194.7535 | 2554860.878 | 1187154.2302
5 | 2554843.844 | 1187095.6759 | 2554833.5776 | 1187090.3024
6 | 2554834.8657 | 1187194.7535 | 2554804.3681 | 1187170.1028
7 | 2554855.5664 | 1187214.2188 | 2554834.8657 | 1187194.7535
8 | 2554801.5039 | 1187167.7877 | 2554804.3681 | 1187170.1028
9 | 2554855.5664 | 1187214.2188 | 2554843.8346 | 1187231.8532
10 | 2554855.5664 | 1187214.2188 | 2554858.6976 | 1187216.8414
11 | 2554801.5039 | 1187167.7877 | 2554781.1152 | 1187151.308
12 | 2554823.3591 | 1187262.6304 | 2554843.8346 | 1187231.8532
13 | 2554871.342 | 1187227.4322 | 2554858.6976 | 1187216.8414
14 | 2554750.2545 | 1187133.1266 | 2554781.0545 | 1187151.2589 | 2554781.1152 | 1187151.308
15 | 2554813.2924 | 1187277.762 | 2554823.3591 | 1187262.6304
16 | 2554871.342 | 1187227.4322 | 2554882.7398 | 1187236.9788
17 | 2554750.2545 | 1187133.1266 | 2554735.1162 | 1187158.0994
18 | 2554732.896 | 1187188.2883 | 2554718.5088 | 1187185.5069 | 2554735.1162 | 1187158.0994
19 | 2554735.1162 | 1187158.0994 | 2554752.5034 | 1187171.3305
20 | 2554732.896 | 1187188.2883 | 2554737.1558 | 1187182.5862
21 | 2554732.896 | 1187188.2883 | 2554745.7753 | 1187190.786
22 | 2554756.6736 | 1187192.8996 | 2554745.7753 | 1187190.786
23 | 2554912.8559 | 1187356.1794 | 2554929.1165 | 1187325.8357 | 2554929.6464 | 1187324.5685
24 | 2554920.9006 | 1187277.0567 | 2554931.3787 | 1187295.0351 | 2554933.1591 | 1187304.4935 | 2554932.5262 | 1187317.6833 | 2554929.6464 | 1187324.5685
25 | 2554910.6169 | 1187260.3283 | 2554918.6253 | 1187273.1527 | 2554920.9006 | 1187277.0567
26 | 2554910.6169 | 1187260.3283 | 2554917.378 | 1187260.533
27 | 2554946.2292 | 1187249.0424 | 2554934.3904 | 1187254.3457 | 2554920.8023 | 1187258.3393 | 2554910.6169 | 1187260.3283
28 | 2554910.6169 | 1187260.3283 | 2554895.8172 | 1187247.9323
29 | 2554917.378 | 1187260.533 | 2554924.7674 | 1187261.0997 | 2554933.0793 | 1187262.5823
30 | 2554895.8172 | 1187247.9323 | 2554882.7398 | 1187236.9788
31 | 2554859.7025 | 1187314.2645 | 2554876.6568 | 1187327.5973
32 | 2554859.7025 | 1187314.2645 | 2554852.7579 | 1187308.8024
33 | 2554852.7579 | 1187308.8024 | 2554830.0923 | 1187290.9754
34 | 2554813.2924 | 1187277.762 | 2554830.0923 | 1187290.9754
35 | 2554813.2924 | 1187277.762 | 2554810.0743 | 1187281.9886
36 | 2554810.0743 | 1187281.9886 | 2554792.4169 | 1187267.4476 | 2554792.3006 | 1187252.0845
37 | 2554773.3536 | 1187205.2801 | 2554769.7061 | 1187211.6266
38 | 2554756.6736 | 1187192.8996 | 2554773.3536 | 1187205.2801

## bus_geodata
| x | y | coords
0 | 2554868.9108 | 1187099.6837
1 | 2554888.4117 | 1187111.3367
2 | 2554848.4326 | 1187088.037
3 | 2554860.878 | 1187154.2302
4 | 2554843.844 | 1187095.6759
5 | 2554834.8657 | 1187194.7535
6 | 2554833.5776 | 1187090.3024
7 | 2554804.3681 | 1187170.1028
8 | 2554855.5664 | 1187214.2188
9 | 2554801.5039 | 1187167.7877
10 | 2554843.8346 | 1187231.8532
11 | 2554858.6976 | 1187216.8414
12 | 2554781.1152 | 1187151.308
13 | 2554823.3591 | 1187262.6304
14 | 2554871.342 | 1187227.4322
15 | 2554750.2545 | 1187133.1266
16 | 2554735.1162 | 1187158.0994
17 | 2554732.896 | 1187188.2883
18 | 2554752.5034 | 1187171.3305
19 | 2554737.1558 | 1187182.5862
20 | 2554745.7753 | 1187190.786
21 | 2554912.8559 | 1187356.1794
22 | 2554929.6464 | 1187324.5685
23 | 2554920.9006 | 1187277.0567
24 | 2554910.6169 | 1187260.3283
25 | 2554917.378 | 1187260.533
26 | 2554946.2292 | 1187249.0424
27 | 2554895.8172 | 1187247.9323
28 | 2554876.6568 | 1187327.5973
29 | 2554859.7025 | 1187314.2645
30 | 2554852.7579 | 1187308.8024
31 | 2554830.0923 | 1187290.9754
32 | 2554813.2924 | 1187277.762
33 | 2554933.0793 | 1187262.5823
34 | 2554882.7398 | 1187236.9788
35 | 2554810.0743 | 1187281.9886
36 | 2554792.3006 | 1187252.0845
37 | 2554769.7061 | 1187211.6266
38 | 2554773.3536 | 1187205.2801
39 | 2554756.6736 | 1187192.8996
40 | 2554855.5664 | 1187214.2188

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99152 | -0.059442 | 0.031658 | 0.0079344
1 | 0.99264 | -0.051567 | 0 | 0
2 | 0.99144 | -0.060046 | 0 | 0
3 | 0.99514 | -0.033961 | 0.036129 | 0.0090548
4 | 0.9914 | -0.060274 | 0 | 0
5 | 1 | 0 | -0.21179 | -0.053028
6 | 0.99136 | -0.060571 | 0.002521 | 0.00063181
7 | 0.99687 | -0.021908 | 0.00897 | 0.0022481
8 | 0.99659 | -0.023802 | 0 | 0
9 | 0.99662 | -0.02364 | 0.020656 | 0.005177
10 | 0.99545 | -0.031803 | 0.016954 | 0.004249
11 | 0.99632 | -0.025699 | 0.0082859 | 0.0020767
12 | 0.99564 | -0.030541 | 0.0072711 | 0.0018223
13 | 0.99436 | -0.039478 | 0.0094076 | 0.0023578
14 | 0.99543 | -0.031994 | 0.0039947 | 0.0010012
15 | 0.99467 | -0.037362 | 0 | 0
16 | 0.99388 | -0.042929 | 0 | 0
17 | 0.99287 | -0.050006 | 0 | 0
18 | 0.99375 | -0.043791 | 0.0039042 | 0.00097847
19 | 0.99281 | -0.050435 | 0.0059582 | 0.0014933
20 | 0.9927 | -0.051205 | 0.0023164 | 0.00058053
21 | 0.99175 | -0.057915 | 0.0037174 | 0.00093167
22 | 0.99194 | -0.056564 | 0.0089522 | 0.0022436
23 | 0.99287 | -0.05 | 0.0026079 | 0.0006536
24 | 0.9933 | -0.046962 | 0 | 0
25 | 0.99327 | -0.047178 | 0 | 0
26 | 0.99297 | -0.049306 | 0.0061882 | 0.0015509
27 | 0.99398 | -0.042153 | 0.0048242 | 0.0012091
28 | 0.99343 | -0.046061 | 0.0022846 | 0.00057257
29 | 0.9935 | -0.045562 | 0 | 0
30 | 0.99353 | -0.045358 | 0.0038495 | 0.00096478
31 | 0.99378 | -0.043569 | 0.0033012 | 0.00082736
32 | 0.99407 | -0.04153 | 0 | 0
33 | 0.9932 | -0.047684 | 0.0031607 | 0.00079215
34 | 0.9947 | -0.037079 | 0.004458 | 0.0011173
35 | 0.99406 | -0.041623 | 0 | 0
36 | 0.99396 | -0.042293 | 0.0017337 | 0.00043452
37 | 0.99241 | -0.053286 | 0.0041182 | 0.0010321
38 | 0.99245 | -0.052981 | 0.00073517 | 0.00018425
39 | 0.99259 | -0.051959 | 0.001848 | 0.00046315
40 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.03418 | -0.0085658 | 0.034217 | 0.0085798 | 3.7298e-05 | 1.4052e-05 | 0.051295 | 0.051295 | 0.051295 | 0.99152 | -0.059442 | 0.99264 | -0.051567 | 18.9981
1 | 0.0025214 | 0.0006314 | -0.0025212 | -0.00063162 | 2.1051e-07 | -2.2292e-07 | 0.0037837 | 0.0037838 | 0.0037838 | 0.99152 | -0.059442 | 0.99144 | -0.060046 | 1.4014
2 | -0.034217 | -0.0085798 | 0.034301 | 0.0086113 | 8.3685e-05 | 3.1526e-05 | 0.051295 | 0.051295 | 0.051295 | 0.99264 | -0.051567 | 0.99514 | -0.033961 | 18.9981
3 | 0.0025212 | 0.00063162 | -0.0025211 | -0.0006317 | 7.9568e-08 | -8.4241e-08 | 0.0037838 | 0.0037839 | 0.0037839 | 0.99144 | -0.060046 | 0.9914 | -0.060274 | 1.4014
4 | -0.07043 | -0.017666 | 0.070763 | 0.017794 | 0.00033328 | 0.00012756 | 0.10532 | 0.10532 | 0.10532 | 0.99514 | -0.033961 | 1 | 0 | 39.0065
5 | 0.0025211 | 0.0006317 | -0.002521 | -0.00063181 | 1.0353e-07 | -1.0959e-07 | 0.0037839 | 0.0037839 | 0.0037839 | 0.9914 | -0.060274 | 0.99136 | -0.060571 | 1.4015
6 | 0.056035 | 0.014075 | -0.055865 | -0.01401 | 0.00017017 | 6.4937e-05 | 0.083392 | 0.083392 | 0.083392 | 1 | 0 | 0.99687 | -0.021908 | 30.886
7 | 0.084197 | 0.021159 | -0.083919 | -0.021053 | 0.00027801 | 0.00010656 | 0.12531 | 0.12531 | 0.12531 | 1 | 0 | 0.99659 | -0.023802 | 46.4098
8 | 0.046895 | 0.011762 | -0.046884 | -0.011758 | 1.1262e-05 | 4.2834e-06 | 0.070003 | 0.070003 | 0.070003 | 0.99687 | -0.021908 | 0.99662 | -0.02364 | 25.927
9 | 0.037602 | 0.0094308 | -0.03756 | -0.0094151 | 4.1663e-05 | 1.5749e-05 | 0.056146 | 0.056146 | 0.056146 | 0.99659 | -0.023802 | 0.99545 | -0.031803 | 20.7947
10 | 0.046317 | 0.011622 | -0.046305 | -0.011617 | 1.2191e-05 | 4.6356e-06 | 0.069161 | 0.069161 | 0.069161 | 0.99659 | -0.023802 | 0.99632 | -0.025699 | 25.6151
11 | 0.026227 | 0.0065805 | -0.026202 | -0.0065712 | 2.5088e-05 | 9.3081e-06 | 0.039162 | 0.039162 | 0.039162 | 0.99662 | -0.02364 | 0.99564 | -0.030541 | 14.5043
12 | 0.020606 | 0.0051661 | -0.020584 | -0.0051581 | 2.1887e-05 | 7.9379e-06 | 0.030803 | 0.030803 | 0.030803 | 0.99545 | -0.031803 | 0.99436 | -0.039478 | 11.4086
13 | 0.038019 | 0.0095408 | -0.037985 | -0.0095282 | 3.3188e-05 | 1.255e-05 | 0.056786 | 0.056786 | 0.056786 | 0.99632 | -0.025699 | 0.99543 | -0.031994 | 21.0317
14 | 0.018931 | 0.0047489 | -0.018913 | -0.0047425 | 1.7894e-05 | 6.417e-06 | 0.028295 | 0.028295 | 0.028295 | 0.99564 | -0.030541 | 0.99467 | -0.037362 | 10.4796
15 | 0.011177 | 0.0028004 | -0.011174 | -0.0027994 | 3.1724e-06 | 9.8446e-07 | 0.016725 | 0.016725 | 0.016725 | 0.99436 | -0.039478 | 0.99407 | -0.04153 | 6.1946
16 | 0.033991 | 0.0085271 | -0.033967 | -0.008518 | 2.3955e-05 | 9.0203e-06 | 0.050814 | 0.050814 | 0.050814 | 0.99543 | -0.031994 | 0.9947 | -0.037079 | 18.82
17 | 0.018913 | 0.0047425 | -0.018899 | -0.0047373 | 1.458e-05 | 5.2293e-06 | 0.028295 | 0.028295 | 0.028295 | 0.99467 | -0.037362 | 0.99388 | -0.042929 | 10.4797
18 | 0.014994 | 0.0037589 | -0.014979 | -0.0037539 | 1.4686e-05 | 5.0439e-06 | 0.022449 | 0.022449 | 0.022449 | 0.99388 | -0.042929 | 0.99287 | -0.050006 | 8.3146
19 | 0.0039046 | 0.00097837 | -0.0039042 | -0.00097847 | 4.6593e-07 | -1.039e-07 | 0.0058459 | 0.005846 | 0.005846 | 0.99388 | -0.042929 | 0.99375 | -0.043791 | 2.1652
20 | 0.0059585 | 0.0014933 | -0.0059582 | -0.0014933 | 3.5385e-07 | 4.4137e-08 | 0.00893 | 0.0089301 | 0.0089301 | 0.99287 | -0.050006 | 0.99281 | -0.050435 | 3.3074
21 | 0.0090208 | 0.0022606 | -0.0090193 | -0.0022602 | 1.4963e-06 | 4.0585e-07 | 0.013519 | 0.013519 | 0.013519 | 0.99287 | -0.050006 | 0.9927 | -0.051205 | 5.0072
22 | 0.006703 | 0.0016796 | -0.0067023 | -0.0016795 | 6.993e-07 | 1.2545e-07 | 0.010047 | 0.010047 | 0.010047 | 0.9927 | -0.051205 | 0.99259 | -0.051959 | 3.7213
23 | -0.0037174 | -0.00093167 | 0.0037181 | 0.00093148 | 6.9493e-07 | -1.9475e-07 | 0.0055776 | 0.0055774 | 0.0055776 | 0.99175 | -0.057915 | 0.99194 | -0.056564 | 2.0658
24 | -0.01267 | -0.0031751 | 0.012682 | 0.0031789 | 1.1519e-05 | 3.7703e-06 | 0.019007 | 0.019006 | 0.019007 | 0.99194 | -0.056564 | 0.99287 | -0.05 | 7.0395
25 | -0.01529 | -0.0038325 | 0.015296 | 0.0038347 | 6.4346e-06 | 2.2208e-06 | 0.022915 | 0.022915 | 0.022915 | 0.99287 | -0.05 | 0.9933 | -0.046962 | 8.487
26 | 0.003161 | 0.00079198 | -0.0031609 | -0.00079203 | 9.4377e-08 | -5.1006e-08 | 0.0047353 | 0.0047353 | 0.0047353 | 0.9933 | -0.046962 | 0.99327 | -0.047178 | 1.7538
27 | 0.0061902 | 0.0015512 | -0.0061882 | -0.0015509 | 2.0077e-06 | 2.8806e-07 | 0.0092732 | 0.0092734 | 0.0092734 | 0.9933 | -0.046962 | 0.99297 | -0.049306 | 3.4346
28 | -0.024647 | -0.0061779 | 0.024664 | 0.006184 | 1.6423e-05 | 6.0666e-06 | 0.036923 | 0.036923 | 0.036923 | 0.9933 | -0.046962 | 0.99398 | -0.042153 | 13.6753
29 | 0.0031609 | 0.00079203 | -0.0031607 | -0.00079215 | 2.2121e-07 | -1.1953e-07 | 0.0047353 | 0.0047354 | 0.0047354 | 0.99327 | -0.047178 | 0.9932 | -0.047684 | 1.7539
30 | -0.029488 | -0.007393 | 0.029509 | 0.0074008 | 2.0744e-05 | 7.7573e-06 | 0.044145 | 0.044145 | 0.044145 | 0.99398 | -0.042153 | 0.9947 | -0.037079 | 16.3501
31 | -0.0022846 | -0.00057257 | 0.0022847 | 0.00057235 | 1.576e-07 | -2.1867e-07 | 0.003422 | 0.0034219 | 0.003422 | 0.99343 | -0.046061 | 0.9935 | -0.045562 | 1.2674
32 | -0.0022847 | -0.00057235 | 0.0022848 | 0.00057226 | 6.4555e-08 | -8.9585e-08 | 0.0034219 | 0.0034218 | 0.0034219 | 0.9935 | -0.045562 | 0.99353 | -0.045358 | 1.2674
33 | -0.0061343 | -0.001537 | 0.0061358 | 0.0015372 | 1.5188e-06 | 2.1061e-07 | 0.0091873 | 0.0091871 | 0.0091873 | 0.99353 | -0.045358 | 0.99378 | -0.043569 | 3.4027
34 | -0.009437 | -0.0023646 | 0.0094397 | 0.0023654 | 2.6629e-06 | 7.4717e-07 | 0.01413 | 0.01413 | 0.01413 | 0.99378 | -0.043569 | 0.99407 | -0.04153 | 5.2334
35 | 0.0017339 | 0.00043402 | -0.0017339 | -0.00043408 | 2.2306e-08 | -6.0221e-08 | 0.0025953 | 0.0025953 | 0.0025953 | 0.99407 | -0.04153 | 0.99406 | -0.041623 | 0.96123
36 | 0.0017339 | 0.00043408 | -0.0017337 | -0.00043452 | 1.6059e-07 | -4.3346e-07 | 0.0025953 | 0.0025955 | 0.0025955 | 0.99406 | -0.041623 | 0.99396 | -0.042293 | 0.9613
37 | -0.0041182 | -0.0010321 | 0.0041184 | 0.0010321 | 1.7416e-07 | -2.7599e-08 | 0.0061749 | 0.0061749 | 0.0061749 | 0.99241 | -0.053286 | 0.99245 | -0.052981 | 2.287
38 | -0.0048536 | -0.0012164 | 0.0048543 | 0.0012163 | 6.8642e-07 | -4.4521e-09 | 0.0072771 | 0.0072771 | 0.0072771 | 0.99245 | -0.052981 | 0.99259 | -0.051959 | 2.6952

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21179 | 0.053028

## res_load
| p_mw | q_mvar
0 | 0.031658 | 0.0079344
1 | 0.036129 | 0.0090548
2 | 0.002521 | 0.00063181
3 | 0.00897 | 0.0022481
4 | 0.020656 | 0.005177
5 | 0.016954 | 0.004249
6 | 0.0082859 | 0.0020767
7 | 0.0072711 | 0.0018223
8 | 0.0094076 | 0.0023578
9 | 0.0039947 | 0.0010012
10 | 0.0039042 | 0.00097847
11 | 0.0059582 | 0.0014933
12 | 0.0023164 | 0.00058053
13 | 0.0037174 | 0.00093167
14 | 0.0089522 | 0.0022436
15 | 0.0026079 | 0.0006536
16 | 0.0061882 | 0.0015509
17 | 0.0048242 | 0.0012091
18 | 0.0022846 | 0.00057257
19 | 0.0038495 | 0.00096478
20 | 0.0033012 | 0.00082736
21 | 0.0031607 | 0.00079215
22 | 0.004458 | 0.0011173
23 | 0.0017337 | 0.00043452
24 | 0.0041182 | 0.0010321
25 | 0.00073517 | 0.00018425
26 | 0.001848 | 0.00046315

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1